## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1372-21_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1372-21_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1372-21_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1372-21_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1372-21_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1372-21_0_5_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1372-21_0_5_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_1372-21_0_5_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1372-21_0_5_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1372-21_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1372-21_0_5_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1372-21_0_5_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_1372-21_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1372-21_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1372-21_0_5_node_36 | 0.4 | n |  | TRUE
15 | bus_LV_1372-21_0_5_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_1372-21_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1372-21_0_5_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1372-21_0_5_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1372-21_0_5_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1372-21_0_5_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_1372-21_0_5_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1372-21_0_5_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1372-21_0_5_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1372-21_0_5_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1372-21_0_5_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1372-21_0_5_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_1372-21_0_5_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1372-21_0_5_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_1372-21_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1372-21_0_5_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_1372-21_0_5_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_1372-21_0_5_node_32 | 0.4 | n |  | TRUE
33 | bus_MV_22_1_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1372-21_0_5_load_0 | 0 | 0.057241 | 0.014346 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1372-21_0_5_load_1 | 1 | 0.0049597 | 0.001243 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1372-21_0_5_load_8 | 8 | 0.0043457 | 0.0010891 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1372-21_0_5_load_6 | 9 | 0.084558 | 0.021192 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1372-21_0_5_load_27 | 10 | 0.022003 | 0.0055146 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1372-21_0_5_load_25 | 11 | 0.022005 | 0.0055151 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1372-21_0_5_load_11 | 12 | 0.0066461 | 0.0016657 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1372-21_0_5_load_10 | 13 | 0.051588 | 0.012929 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1372-21_0_5_load_36 | 14 | 0.0072421 | 0.001815 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1372-21_0_5_load_26 | 15 | 0.0050972 | 0.0012775 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1372-21_0_5_load_12 | 16 | 0.027413 | 0.0068704 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1372-21_0_5_load_13 | 17 | 0.03499 | 0.0087692 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1372-21_0_5_load_14 | 18 | 0.01557 | 0.0039023 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1372-21_0_5_load_15 | 19 | 0.0085506 | 0.002143 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1372-21_0_5_load_34 | 20 | 0.0042248 | 0.0010588 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1372-21_0_5_load_16 | 21 | 0.043403 | 0.010878 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1372-21_0_5_load_21 | 25 | 0.0081093 | 0.0020324 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1372-21_0_5_load_29 | 26 | 0.063756 | 0.015979 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1372-21_0_5_load_22 | 27 | 0.022007 | 0.0055155 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1372-21_0_5_load_23 | 29 | 0.022007 | 0.0055154 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1372-21_0_5_load_33 | 31 | 0.017402 | 0.0043613 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1372-21_0_5_load_32 | 32 | 0.02206 | 0.0055288 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1372-21_0_5_line_0 |  | 0 | 1 | 0.032363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1372-21_0_5_line_1 |  | 0 | 2 | 0.031781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1372-21_0_5_line_2 |  | 1 | 3 | 0.056577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1372-21_0_5_line_3 |  | 2 | 4 | 0.06197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1372-21_0_5_line_4 |  | 3 | 5 | 0.02642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1372-21_0_5_line_5 |  | 3 | 6 | 0.092558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1372-21_0_5_line_6 |  | 4 | 7 | 0.037455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1372-21_0_5_line_7 |  | 5 | 8 | 0.025931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1372-21_0_5_line_8 |  | 5 | 9 | 0.057364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1372-21_0_5_line_9 |  | 6 | 10 | 0.035106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1372-21_0_5_line_10 |  | 6 | 11 | 0.018402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1372-21_0_5_line_11 |  | 7 | 12 | 0.007349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1372-21_0_5_line_12 |  | 7 | 13 | 0.023497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1372-21_0_5_line_13 |  | 8 | 14 | 0.023216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1372-21_0_5_line_14 |  | 10 | 29 | 0.02394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1372-21_0_5_line_15 |  | 11 | 19 | 0.033037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1372-21_0_5_line_16 |  | 14 | 15 | 0.2881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1372-21_0_5_line_17 |  | 16 | 17 | 0.02644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1372-21_0_5_line_18 |  | 16 | 18 | 0.026158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1372-21_0_5_line_19 |  | 18 | 19 | 0.025648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1372-21_0_5_line_20 |  | 18 | 20 | 0.045038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1372-21_0_5_line_21 |  | 21 | 22 | 0.030761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1372-21_0_5_line_22 |  | 22 | 23 | 0.078881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1372-21_0_5_line_23 |  | 23 | 26 | 0.031319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1372-21_0_5_line_24 |  | 23 | 24 | 0.050966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_1372-21_0_5_line_25 |  | 24 | 25 | 0.010361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1372-21_0_5_line_26 |  | 25 | 27 | 0.026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_1372-21_0_5_line_27 |  | 26 | 28 | 0.037983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1372-21_0_5_line_28 |  | 27 | 29 | 0.024749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1372-21_0_5_line_29 |  | 28 | 32 | 0.031504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1372-21_0_5_line_30 |  | 28 | 30 | 0.020179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1372-21_0_5_line_31 |  | 30 | 31 | 0.0082997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1372-21_0_5_trafo_25 | 0.63 MVA 20/0.4 kV | 33 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2691713.3055 | 1208062.361 | 2691723.1716 | 1208072.3165 | 2691735.4307 | 1208085.9666
1 | 2691686.7617 | 1208045.695 | 2691705.56 | 1208054.5452 | 2691713.3055 | 1208062.361
2 | 2691774.8598 | 1208126.4805 | 2691753.973 | 1208106.6128 | 2691735.4307 | 1208085.9666
3 | 2691686.7617 | 1208045.695 | 2691680.4748 | 1208041.6291 | 2691661.6744 | 1208067.0573 | 2691651.1353 | 1208087.3423
4 | 2691774.8598 | 1208126.4805 | 2691757.7298 | 1208146.6306
5 | 2691774.8598 | 1208126.4805 | 2691809.4003 | 1208086.7629 | 2691812.1895 | 1208087.3506 | 2691818.2356 | 1208091.7465 | 2691823.4676 | 1208087.7688 | 2691828.8389 | 1208084.1268 | 2691820.4493 | 1208076.3703 | 2691824.7203 | 1208073.5675
6 | 2691624.5416 | 1208111.25 | 2691628.2187 | 1208111.4621 | 2691630.8882 | 1208110.9361 | 2691633.2355 | 1208108.615 | 2691650.0668 | 1208088.5823 | 2691651.1353 | 1208087.3423
7 | 2691757.7298 | 1208146.6306 | 2691740.9368 | 1208166.389
8 | 2691757.7298 | 1208146.6306 | 2691719.2413 | 1208118.2423 | 2691710.5544 | 1208114.301
9 | 2691824.7203 | 1208073.5675 | 2691854.4158 | 1208054.8421
10 | 2691824.7203 | 1208073.5675 | 2691814.7627 | 1208058.0929
11 | 2691624.5416 | 1208111.25 | 2691628.8985 | 1208105.324
12 | 2691624.5416 | 1208111.25 | 2691622.2979 | 1208113.2614 | 2691620.2115 | 1208114.4412 | 2691612.2872 | 1208115.9873 | 2691602.2761 | 1208116.1942
13 | 2691740.9368 | 1208166.389 | 2691725.9018 | 1208184.079
14 | 2691854.4158 | 1208054.8421 | 2691874.6663 | 1208042.0725
15 | 2691814.7627 | 1208058.0929 | 2691808.3821 | 1208048.177 | 2691804.2479 | 1208039.6189 | 2691813.9204 | 1208032.9633
16 | 2691725.9018 | 1208184.079 | 2691621.9755 | 1208452.7794
17 | 2691856.5989 | 1208003.597 | 2691878.381 | 1207988.6091
18 | 2691856.5989 | 1208003.597 | 2691835.0493 | 1208018.4249
19 | 2691813.9204 | 1208032.9633 | 2691835.0493 | 1208018.4249
20 | 2691835.0493 | 1208018.4249 | 2691814.4066 | 1207978.3961
21 | 2691925.7835 | 1207944.4702 | 2691895.8677 | 1207946.4887 | 2691895.693 | 1207945.7319
22 | 2691925.7835 | 1207944.4702 | 2691928.7894 | 1207949.2641 | 2691933.8732 | 1207957.3812 | 2691938.5711 | 1207964.8807 | 2691948.0751 | 1207978.7808 | 2691952.4924 | 1207985.2421 | 2691961.5719 | 1207995.6 | 2691958.0008 | 1207997.8798 | 2691964.2894 | 1208008.2392
23 | 2691964.2894 | 1208008.2392 | 2691961.3771 | 1208010.2067 | 2691938.3602 | 1208025.8057
24 | 2691925.247 | 1208018.7671 | 2691953.416 | 1208000.8 | 2691958.0008 | 1207997.8798 | 2691964.2894 | 1208008.2392
25 | 2691925.247 | 1208018.7671 | 2691916.4496 | 1208013.2946
26 | 2691895.304 | 1208028.416 | 2691901.0296 | 1208024.5647 | 2691916.4496 | 1208013.2946 | 2691916.4496 | 1208013.2946
27 | 2691906.9176 | 1208047.1148 | 2691938.3602 | 1208025.8057
28 | 2691874.6663 | 1208042.0725 | 2691880.0222 | 1208038.6952 | 2691895.304 | 1208028.416
29 | 2691906.9176 | 1208047.1148 | 2691880.7846 | 1208064.7094
30 | 2691906.9176 | 1208047.1148 | 2691913.1546 | 1208056.8841 | 2691913.8548 | 1208060.7863 | 2691913.2305 | 1208064.2902 | 2691912.4137 | 1208064.9892
31 | 2691912.4137 | 1208064.9892 | 2691910.626 | 1208066.5182 | 2691905.7249 | 1208069.887

## bus_geodata
| x | y | coords
0 | 2691713.3055 | 1208062.361
1 | 2691735.4307 | 1208085.9666
2 | 2691686.7617 | 1208045.695
3 | 2691774.8598 | 1208126.4805
4 | 2691651.1353 | 1208087.3423
5 | 2691757.7298 | 1208146.6306
6 | 2691824.7203 | 1208073.5675
7 | 2691624.5416 | 1208111.25
8 | 2691740.9368 | 1208166.389
9 | 2691710.5544 | 1208114.301
10 | 2691854.4158 | 1208054.8421
11 | 2691814.7627 | 1208058.0929
12 | 2691628.8985 | 1208105.324
13 | 2691602.2761 | 1208116.1942
14 | 2691725.9018 | 1208184.079
15 | 2691621.9755 | 1208452.7794
16 | 2691856.5989 | 1208003.597
17 | 2691878.381 | 1207988.6091
18 | 2691835.0493 | 1208018.4249
19 | 2691813.9204 | 1208032.9633
20 | 2691814.4066 | 1207978.3961
21 | 2691895.693 | 1207945.7319
22 | 2691925.7835 | 1207944.4702
23 | 2691964.2894 | 1208008.2392
24 | 2691925.247 | 1208018.7671
25 | 2691916.4496 | 1208013.2946
26 | 2691938.3602 | 1208025.8057
27 | 2691895.304 | 1208028.416
28 | 2691906.9176 | 1208047.1148
29 | 2691874.6663 | 1208042.0725
30 | 2691912.4137 | 1208064.9892
31 | 2691905.7249 | 1208069.887
32 | 2691880.7846 | 1208064.7094
33 | 2691824.7203 | 1208073.5675

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97878 | -0.40684 | 0.057241 | 0.014346
1 | 0.98225 | -0.33909 | 0.0049597 | 0.001243
2 | 0.97705 | -0.44057 | 0 | 0
3 | 0.9886 | -0.21678 | 0 | 0
4 | 0.97367 | -0.50669 | 0 | 0
5 | 0.98613 | -0.26461 | 0 | 0
6 | 0.99812 | -0.035546 | 0 | 0
7 | 0.97164 | -0.54688 | 0 | 0
8 | 0.98573 | -0.27237 | 0.0043457 | 0.0010891
9 | 0.98165 | -0.35194 | 0.084558 | 0.021192
10 | 0.99634 | -0.069506 | 0.022003 | 0.0055146
11 | 1 | 0 | -0.54211 | -0.13827
12 | 0.97159 | -0.54778 | 0.0066461 | 0.0016657
13 | 0.9705 | -0.56928 | 0.051588 | 0.012929
14 | 0.98547 | -0.27751 | 0.0072421 | 0.001815
15 | 0.98411 | -0.30393 | 0.0050972 | 0.0012775
16 | 0.99385 | -0.11818 | 0.027413 | 0.0068704
17 | 0.99301 | -0.13452 | 0.03499 | 0.0087692
18 | 0.99534 | -0.08942 | 0.01557 | 0.0039023
19 | 0.99726 | -0.0524 | 0.0085506 | 0.002143
20 | 0.99517 | -0.092768 | 0.0042248 | 0.0010588
21 | 0.98515 | -0.28551 | 0.043403 | 0.010878
22 | 0.98638 | -0.26156 | 0 | 0
23 | 0.98953 | -0.20042 | 0 | 0
24 | 0.99297 | -0.13414 | 0 | 0
25 | 0.99332 | -0.12743 | 0.0081093 | 0.0020324
26 | 0.98656 | -0.25814 | 0.063756 | 0.015979
27 | 0.99424 | -0.10968 | 0.022007 | 0.0055155
28 | 0.98518 | -0.28502 | 0 | 0
29 | 0.99525 | -0.090416 | 0.022007 | 0.0055154
30 | 0.98485 | -0.29133 | 0 | 0
31 | 0.98472 | -0.29393 | 0.017402 | 0.0043613
32 | 0.98454 | -0.29751 | 0.02206 | 0.0055288
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.11592 | -0.029225 | 0.1163 | 0.029466 | 0.0003772 | 0.000241 | 0.1763 | 0.1763 | 0.1763 | 0.97878 | -0.40684 | 0.98225 | -0.33909 | 48.433
1 | 0.058681 | 0.014879 | -0.058586 | -0.014819 | 9.4984e-05 | 6.0391e-05 | 0.089274 | 0.089274 | 0.089274 | 0.97878 | -0.40684 | 0.97705 | -0.44057 | 24.526
2 | -0.12126 | -0.030709 | 0.12198 | 0.031167 | 0.00071681 | 0.00045804 | 0.18381 | 0.18381 | 0.18381 | 0.98225 | -0.33909 | 0.9886 | -0.21678 | 50.4971
3 | 0.058586 | 0.014819 | -0.058401 | -0.014701 | 0.00018521 | 0.00011776 | 0.089274 | 0.089275 | 0.089275 | 0.97705 | -0.44057 | 0.97367 | -0.50669 | 24.526
4 | 0.10185 | 0.025754 | -0.10161 | -0.025605 | 0.00023307 | 0.00014883 | 0.15338 | 0.15338 | 0.15338 | 0.9886 | -0.21678 | 0.98613 | -0.26461 | 42.1365
5 | -0.22382 | -0.056921 | 0.22579 | 0.058181 | 0.0019731 | 0.0012604 | 0.33719 | 0.33718 | 0.33719 | 0.9886 | -0.21678 | 0.99812 | -0.035546 | 46.3167
6 | 0.058401 | 0.014701 | -0.058289 | -0.01463 | 0.00011194 | 7.1179e-05 | 0.089275 | 0.089275 | 0.089275 | 0.97367 | -0.50669 | 0.97164 | -0.54688 | 24.5261
7 | 0.016701 | 0.0041874 | -0.016694 | -0.0041837 | 6.1757e-06 | 3.6218e-06 | 0.025201 | 0.025201 | 0.025201 | 0.98613 | -0.26461 | 0.98573 | -0.27237 | 6.9234
8 | 0.084911 | 0.021418 | -0.084558 | -0.021192 | 0.00035342 | 0.00022546 | 0.12818 | 0.12818 | 0.12818 | 0.98613 | -0.26461 | 0.98165 | -0.35194 | 35.2132
9 | 0.22266 | 0.056537 | -0.2223 | -0.056306 | 0.00036322 | 0.00023063 | 0.3322 | 0.3322 | 0.3322 | 0.99812 | -0.035546 | 0.99634 | -0.069506 | 22.8163
10 | -0.44845 | -0.11472 | 0.44923 | 0.11521 | 0.000773 | 0.00049376 | 0.66939 | 0.66939 | 0.66939 | 0.99812 | -0.035546 | 1 | 0 | 45.9744
11 | 0.0066464 | 0.0016658 | -0.0066461 | -0.0016657 | 2.8552e-07 | 9.1718e-08 | 0.010179 | 0.010179 | 0.010179 | 0.97164 | -0.54688 | 0.97159 | -0.54778 | 2.7963
12 | 0.051643 | 0.012964 | -0.051588 | -0.012929 | 5.5126e-05 | 3.499e-05 | 0.079096 | 0.079096 | 0.079096 | 0.97164 | -0.54688 | 0.9705 | -0.56928 | 21.7298
13 | 0.012349 | 0.0030946 | -0.012346 | -0.003093 | 3.0253e-06 | 1.6403e-06 | 0.018641 | 0.018641 | 0.018641 | 0.98573 | -0.27237 | 0.98547 | -0.27751 | 5.1212
14 | 0.20029 | 0.050792 | -0.20009 | -0.050664 | 0.00020111 | 0.00012747 | 0.29934 | 0.29934 | 0.29934 | 0.99634 | -0.069506 | 0.99525 | -0.090416 | 20.5593
15 | 0.091236 | 0.023054 | -0.091008 | -0.022908 | 0.00022856 | 0.00014585 | 0.13583 | 0.13583 | 0.13583 | 1 | 0 | 0.99726 | -0.0524 | 37.3153
16 | 0.0051036 | 0.0012779 | -0.0050972 | -0.0012775 | 6.4164e-06 | 4.4095e-07 | 0.0077059 | 0.0077072 | 0.0077072 | 0.98547 | -0.27751 | 0.98411 | -0.30393 | 2.1174
17 | 0.035017 | 0.0087863 | -0.03499 | -0.0087692 | 2.7258e-05 | 1.7102e-05 | 0.052432 | 0.052432 | 0.052432 | 0.99385 | -0.11818 | 0.99301 | -0.13452 | 14.4043
18 | -0.06243 | -0.015657 | 0.062516 | 0.015711 | 8.571e-05 | 5.4515e-05 | 0.093475 | 0.093475 | 0.093475 | 0.99385 | -0.11818 | 0.99534 | -0.08942 | 25.68
19 | -0.082312 | -0.020672 | 0.082457 | 0.020765 | 0.00014567 | 9.2896e-05 | 0.12307 | 0.12307 | 0.12307 | 0.99534 | -0.08942 | 0.99726 | -0.0524 | 33.8103
20 | 0.0042255 | 0.0010587 | -0.0042248 | -0.0010588 | 6.7397e-07 | -1.5393e-07 | 0.0063169 | 0.0063171 | 0.0063171 | 0.99534 | -0.08942 | 0.99517 | -0.092768 | 1.7355
21 | -0.043403 | -0.010878 | 0.043453 | 0.010909 | 4.9577e-05 | 3.1337e-05 | 0.065559 | 0.065558 | 0.065559 | 0.98515 | -0.28551 | 0.98638 | -0.26156 | 18.0106
22 | -0.043453 | -0.010909 | 0.04358 | 0.01099 | 0.00012713 | 8.0355e-05 | 0.065558 | 0.065558 | 0.065558 | 0.98638 | -0.26156 | 0.98953 | -0.20042 | 18.0106
23 | 0.10357 | 0.026095 | -0.10329 | -0.025913 | 0.00028509 | 0.00018206 | 0.1558 | 0.1558 | 0.1558 | 0.98953 | -0.20042 | 0.98656 | -0.25814 | 42.8023
24 | -0.14716 | -0.037085 | 0.14762 | 0.037383 | 0.00046824 | 0.00029836 | 0.22136 | 0.22136 | 0.22136 | 0.98953 | -0.20042 | 0.99297 | -0.13414 | 30.4064
25 | -0.14762 | -0.037383 | 0.14767 | 0.037413 | 4.7593e-05 | 2.9923e-05 | 0.22136 | 0.22136 | 0.22136 | 0.99297 | -0.13414 | 0.99332 | -0.12743 | 15.2032
26 | -0.15578 | -0.039446 | 0.15591 | 0.039529 | 0.0001329 | 8.3711e-05 | 0.23351 | 0.23351 | 0.23351 | 0.99332 | -0.12743 | 0.99424 | -0.10968 | 16.0375
27 | 0.039533 | 0.0099344 | -0.039483 | -0.0099025 | 5.0659e-05 | 3.1937e-05 | 0.059637 | 0.059637 | 0.059637 | 0.98656 | -0.25814 | 0.98518 | -0.28502 | 16.3839
28 | -0.17792 | -0.045045 | 0.17809 | 0.045149 | 0.00016472 | 0.00010413 | 0.26644 | 0.26644 | 0.26644 | 0.99424 | -0.10968 | 0.99525 | -0.090416 | 18.2996
29 | 0.022073 | 0.0055368 | -0.02206 | -0.0055288 | 1.3133e-05 | 8.0043e-06 | 0.033342 | 0.033342 | 0.033342 | 0.98518 | -0.28502 | 0.98454 | -0.29751 | 9.1598
30 | 0.017409 | 0.0043657 | -0.017404 | -0.0043626 | 5.2325e-06 | 3.0919e-06 | 0.026296 | 0.026296 | 0.026296 | 0.98518 | -0.28502 | 0.98485 | -0.29133 | 7.2242
31 | 0.017404 | 0.0043626 | -0.017402 | -0.0043613 | 2.1521e-06 | 1.2718e-06 | 0.026296 | 0.026296 | 0.026296 | 0.98485 | -0.29133 | 0.98472 | -0.29393 | 7.2242

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56412 | 0.14378

## res_load
| p_mw | q_mvar
0 | 0.057241 | 0.014346
1 | 0.0049597 | 0.001243
2 | 0.0043457 | 0.0010891
3 | 0.084558 | 0.021192
4 | 0.022003 | 0.0055146
5 | 0.022005 | 0.0055151
6 | 0.0066461 | 0.0016657
7 | 0.051588 | 0.012929
8 | 0.0072421 | 0.001815
9 | 0.0050972 | 0.0012775
10 | 0.027413 | 0.0068704
11 | 0.03499 | 0.0087692
12 | 0.01557 | 0.0039023
13 | 0.0085506 | 0.002143
14 | 0.0042248 | 0.0010588
15 | 0.043403 | 0.010878
16 | 0.0081093 | 0.0020324
17 | 0.063756 | 0.015979
18 | 0.022007 | 0.0055155
19 | 0.022007 | 0.0055154
20 | 0.017402 | 0.0043613
21 | 0.02206 | 0.0055288

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1