## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1372-25_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1372-25_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1372-25_0_4_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_1372-25_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1372-25_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_1372-25_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1372-25_0_4_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_1372-25_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1372-25_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1372-25_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1372-25_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1372-25_0_4_node_43 | 0.4 | n |  | TRUE
12 | bus_LV_1372-25_0_4_node_40 | 0.4 | n |  | TRUE
13 | bus_LV_1372-25_0_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1372-25_0_4_node_41 | 0.4 | n |  | TRUE
15 | bus_LV_1372-25_0_4_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_1372-25_0_4_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_1372-25_0_4_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_1372-25_0_4_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_1372-25_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1372-25_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1372-25_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1372-25_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1372-25_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1372-25_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1372-25_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1372-25_0_4_node_50 | 0.4 | n |  | TRUE
27 | bus_LV_1372-25_0_4_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_1372-25_0_4_node_55 | 0.4 | n |  | TRUE
29 | bus_LV_1372-25_0_4_node_39 | 0.4 | n |  | TRUE
30 | bus_LV_1372-25_0_4_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_1372-25_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1372-25_0_4_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_1372-25_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_1372-25_0_4_node_53 | 0.4 | n |  | TRUE
35 | bus_LV_1372-25_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1372-25_0_4_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_1372-25_0_4_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_1372-25_0_4_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_1372-25_0_4_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_1372-25_0_4_node_48 | 0.4 | n |  | TRUE
41 | bus_LV_1372-25_0_4_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1372-25_0_4_node_47 | 0.4 | n |  | TRUE
43 | bus_LV_1372-25_0_4_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_1372-25_0_4_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_1372-25_0_4_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_1372-25_0_4_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_1372-25_0_4_node_63 | 0.4 | n |  | TRUE
48 | bus_LV_1372-25_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_1372-25_0_4_node_62 | 0.4 | n |  | TRUE
50 | bus_LV_1372-25_0_4_node_61 | 0.4 | n |  | TRUE
51 | bus_LV_1372-25_0_4_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_1372-25_0_4_node_60 | 0.4 | n |  | TRUE
53 | bus_LV_1372-25_0_4_node_67 | 0.4 | n |  | TRUE
54 | bus_LV_1372-25_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_1372-25_0_4_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_1372-25_0_4_node_75 | 0.4 | n |  | TRUE
57 | bus_LV_1372-25_0_4_node_74 | 0.4 | n |  | TRUE
58 | bus_LV_1372-25_0_4_node_49 | 0.4 | n |  | TRUE
59 | bus_LV_1372-25_0_4_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_1372-25_0_4_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_1372-25_0_4_node_64 | 0.4 | n |  | TRUE
62 | bus_LV_1372-25_0_4_node_65 | 0.4 | n |  | TRUE
63 | bus_LV_1372-25_0_4_node_66 | 0.4 | n |  | TRUE
64 | bus_LV_1372-25_0_4_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_1372-25_0_4_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_1372-25_0_4_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_1372-25_0_4_node_76 | 0.4 | n |  | TRUE
68 | bus_LV_1372-25_0_4_node_128 | 0.4 | n |  | TRUE
69 | bus_LV_1372-25_0_4_node_127 | 0.4 | n |  | TRUE
70 | bus_LV_1372-25_0_4_node_71 | 0.4 | n |  | TRUE
71 | bus_LV_1372-25_0_4_node_69 | 0.4 | n |  | TRUE
72 | bus_LV_1372-25_0_4_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_1372-25_0_4_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_1372-25_0_4_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_1372-25_0_4_node_73 | 0.4 | n |  | TRUE
76 | bus_LV_1372-25_0_4_node_77 | 0.4 | n |  | TRUE
77 | bus_LV_1372-25_0_4_node_78 | 0.4 | n |  | TRUE
78 | bus_LV_1372-25_0_4_node_79 | 0.4 | n |  | TRUE
79 | bus_LV_1372-25_0_4_node_117 | 0.4 | n |  | TRUE
80 | bus_LV_1372-25_0_4_node_97 | 0.4 | n |  | TRUE
81 | bus_LV_1372-25_0_4_node_109 | 0.4 | n |  | TRUE
82 | bus_LV_1372-25_0_4_node_101 | 0.4 | n |  | TRUE
83 | bus_LV_1372-25_0_4_node_95 | 0.4 | n |  | TRUE
84 | bus_LV_1372-25_0_4_node_80 | 0.4 | n |  | TRUE
85 | bus_LV_1372-25_0_4_node_81 | 0.4 | n |  | TRUE
86 | bus_LV_1372-25_0_4_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_1372-25_0_4_node_83 | 0.4 | n |  | TRUE
88 | bus_LV_1372-25_0_4_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_1372-25_0_4_node_85 | 0.4 | n |  | TRUE
90 | bus_LV_1372-25_0_4_node_92 | 0.4 | n |  | TRUE
91 | bus_LV_1372-25_0_4_node_93 | 0.4 | n |  | TRUE
92 | bus_LV_1372-25_0_4_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_1372-25_0_4_node_98 | 0.4 | n |  | TRUE
94 | bus_LV_1372-25_0_4_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_1372-25_0_4_node_88 | 0.4 | n |  | TRUE
96 | bus_LV_1372-25_0_4_node_89 | 0.4 | n |  | TRUE
97 | bus_LV_1372-25_0_4_node_90 | 0.4 | n |  | TRUE
98 | bus_LV_1372-25_0_4_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_1372-25_0_4_node_99 | 0.4 | n |  | TRUE
100 | bus_LV_1372-25_0_4_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_1372-25_0_4_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_1372-25_0_4_node_103 | 0.4 | n |  | TRUE
103 | bus_LV_1372-25_0_4_node_104 | 0.4 | n |  | TRUE
104 | bus_LV_1372-25_0_4_node_105 | 0.4 | n |  | TRUE
105 | bus_LV_1372-25_0_4_node_106 | 0.4 | n |  | TRUE
106 | bus_LV_1372-25_0_4_node_107 | 0.4 | n |  | TRUE
107 | bus_LV_1372-25_0_4_node_108 | 0.4 | n |  | TRUE
108 | bus_LV_1372-25_0_4_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_1372-25_0_4_node_111 | 0.4 | n |  | TRUE
110 | bus_LV_1372-25_0_4_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_1372-25_0_4_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_1372-25_0_4_node_114 | 0.4 | n |  | TRUE
113 | bus_LV_1372-25_0_4_node_115 | 0.4 | n |  | TRUE
114 | bus_LV_1372-25_0_4_node_116 | 0.4 | n |  | TRUE
115 | bus_LV_1372-25_0_4_node_118 | 0.4 | n |  | TRUE
116 | bus_LV_1372-25_0_4_node_119 | 0.4 | n |  | TRUE
117 | bus_LV_1372-25_0_4_node_120 | 0.4 | n |  | TRUE
118 | bus_LV_1372-25_0_4_node_121 | 0.4 | n |  | TRUE
119 | bus_LV_1372-25_0_4_node_122 | 0.4 | n |  | TRUE
120 | bus_LV_1372-25_0_4_node_123 | 0.4 | n |  | TRUE
121 | bus_LV_1372-25_0_4_node_124 | 0.4 | n |  | TRUE
122 | bus_LV_1372-25_0_4_node_125 | 0.4 | n |  | TRUE
123 | bus_LV_1372-25_0_4_node_126 | 0.4 | n |  | TRUE
124 | bus_LV_1372-25_0_4_node_129 | 0.4 | n |  | TRUE
125 | bus_LV_1372-25_0_4_node_130 | 0.4 | n |  | TRUE
126 | bus_MV_22_1_node_224 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1372-25_0_4_load_0 | 0 | 0.00053185 | 0.00013329 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1372-25_0_4_load_9 | 2 | 0.00090024 | 0.00022562 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1372-25_0_4_load_2 | 4 | 0.00056002 | 0.00014036 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1372-25_0_4_load_25 | 6 | 0.0011652 | 0.00029202 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1372-25_0_4_load_5 | 7 | 0.00045941 | 0.00011514 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1372-25_0_4_load_7 | 10 | 0.00072854 | 0.00018259 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1372-25_0_4_load_43 | 11 | 0.00018251 | 4.5741e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1372-25_0_4_load_40 | 12 | 0.00044548 | 0.00011165 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1372-25_0_4_load_17 | 13 | 0.0015897 | 0.00039842 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1372-25_0_4_load_41 | 14 | 0.00027126 | 6.7985e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1372-25_0_4_load_31 | 15 | 0.00029328 | 7.3503e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1372-25_0_4_load_32 | 16 | 0.00089322 | 0.00022386 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1372-25_0_4_load_29 | 17 | 0.00024052 | 6.0281e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1372-25_0_4_load_27 | 18 | 0.00090935 | 0.0002279 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1372-25_0_4_load_10 | 19 | 0.00064626 | 0.00016197 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1372-25_0_4_load_12 | 21 | 0.00046369 | 0.00011621 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1372-25_0_4_load_13 | 22 | 0.00027666 | 6.9337e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1372-25_0_4_load_14 | 23 | 0.00094347 | 0.00023646 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1372-25_0_4_load_50 | 26 | 0.003459 | 0.00086691 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1372-25_0_4_load_35 | 30 | 0.00073746 | 0.00018482 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1372-25_0_4_load_54 | 32 | 0.0012366 | 0.00030992 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1372-25_0_4_load_24 | 33 | 0.0005057 | 0.00012674 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1372-25_0_4_load_53 | 34 | 0.00050925 | 0.00012763 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1372-25_0_4_load_18 | 36 | 0.0033151 | 0.00083084 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1372-25_0_4_load_19 | 37 | 0.00047634 | 0.00011938 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1372-25_0_4_load_20 | 38 | 0.0010261 | 0.00025716 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1372-25_0_4_load_21 | 39 | 0.0011292 | 0.000283 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1372-25_0_4_load_36 | 41 | 0.00040358 | 0.00010115 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1372-25_0_4_load_47 | 42 | 0.00026334 | 6.6e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1372-25_0_4_load_28 | 43 | 0.00091064 | 0.00022823 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1372-25_0_4_load_44 | 44 | 0.00023703 | 5.9406e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1372-25_0_4_load_63 | 47 | 0.0011166 | 0.00027984 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1372-25_0_4_load_62 | 49 | 0.0030185 | 0.00075652 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1372-25_0_4_load_61 | 50 | 0.00096521 | 0.00024191 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1372-25_0_4_load_38 | 51 | 0.00073223 | 0.00018351 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1372-25_0_4_load_60 | 52 | 0.00077079 | 0.00019318 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1372-25_0_4_load_67 | 53 | 0.001489 | 0.00037319 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1372-25_0_4_load_42 | 54 | 0.00021724 | 5.4445e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1372-25_0_4_load_46 | 55 | 0.00017925 | 4.4925e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1372-25_0_4_load_74 | 57 | 0.00020268 | 5.0796e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1372-25_0_4_load_49 | 58 | 0.0014889 | 0.00037316 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1372-25_0_4_load_51 | 59 | 0.0029206 | 0.00073198 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1372-25_0_4_load_65 | 62 | 0.0015412 | 0.00038625 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1372-25_0_4_load_58 | 65 | 0.0005115 | 0.00012819 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1372-25_0_4_load_59 | 66 | 0.0021903 | 0.00054893 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1372-25_0_4_load_76 | 67 | 0.00077364 | 0.00019389 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1372-25_0_4_load_128 | 68 | 0.0023397 | 0.00058638 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1372-25_0_4_load_127 | 69 | 0.001434 | 0.00035941 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1372-25_0_4_load_71 | 70 | 0.00090967 | 0.00022799 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1372-25_0_4_load_69 | 71 | 0.00071466 | 0.00017911 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1372-25_0_4_load_68 | 72 | 0.0016363 | 0.00041009 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1372-25_0_4_load_70 | 73 | 0.001798 | 0.00045063 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1372-25_0_4_load_72 | 74 | 0.0024992 | 0.00062636 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1372-25_0_4_load_73 | 75 | 0.0034124 | 0.00085523 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1372-25_0_4_load_77 | 76 | 0.0017495 | 0.00043848 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1372-25_0_4_load_78 | 77 | 0.0012095 | 0.00030312 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1372-25_0_4_load_117 | 79 | 0.0025683 | 0.00064367 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1372-25_0_4_load_109 | 81 | 0.00567 | 0.001421 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1372-25_0_4_load_101 | 82 | 0.0029512 | 0.00073964 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1372-25_0_4_load_95 | 83 | 0.0045636 | 0.0011438 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1372-25_0_4_load_80 | 84 | 0.0015111 | 0.00037871 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1372-25_0_4_load_82 | 86 | 0.0013464 | 0.00033744 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1372-25_0_4_load_85 | 89 | 0.0017476 | 0.000438 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1372-25_0_4_load_93 | 91 | 0.0015386 | 0.0003856 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1372-25_0_4_load_86 | 92 | 0.010389 | 0.0026037 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1372-25_0_4_load_98 | 93 | 0.0020834 | 0.00052214 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1372-25_0_4_load_87 | 94 | 0.00071113 | 0.00017823 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1372-25_0_4_load_89 | 96 | 0.0015299 | 0.00038343 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1372-25_0_4_load_99 | 99 | 0.0025772 | 0.00064592 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1372-25_0_4_load_96 | 100 | 0.0026268 | 0.00065833 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1372-25_0_4_load_102 | 101 | 0.0027648 | 0.00069294 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1372-25_0_4_load_103 | 102 | 0.005288 | 0.0013253 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1372-25_0_4_load_105 | 104 | 0.005271 | 0.001321 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1372-25_0_4_load_106 | 105 | 0.0028686 | 0.00071894 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1372-25_0_4_load_107 | 106 | 0.0017487 | 0.00043827 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1372-25_0_4_load_108 | 107 | 0.0053429 | 0.0013391 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1372-25_0_4_load_110 | 108 | 0.0024801 | 0.00062156 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1372-25_0_4_load_111 | 109 | 0.0081973 | 0.0020544 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1372-25_0_4_load_112 | 110 | 0.0051936 | 0.0013017 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1372-25_0_4_load_113 | 111 | 0.0051498 | 0.0012907 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1372-25_0_4_load_114 | 112 | 0.0083624 | 0.0020958 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1372-25_0_4_load_115 | 113 | 0.0018466 | 0.00046279 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1372-25_0_4_load_116 | 114 | 0.00020366 | 5.1042e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1372-25_0_4_load_118 | 115 | 0.00032825 | 8.2266e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1372-25_0_4_load_119 | 116 | 0.0026791 | 0.00067145 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1372-25_0_4_load_120 | 117 | 0.0037338 | 0.00093578 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1372-25_0_4_load_121 | 118 | 0.0031434 | 0.00078781 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1372-25_0_4_load_123 | 120 | 0.0033383 | 0.00083666 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1372-25_0_4_load_124 | 121 | 0.00077325 | 0.0001938 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1372-25_0_4_load_125 | 122 | 0.0013555 | 0.00033972 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1372-25_0_4_load_126 | 123 | 0.0009307 | 0.00023326 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1372-25_0_4_load_129 | 124 | 0.0012426 | 0.00031143 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1372-25_0_4_load_130 | 125 | 0.0013616 | 0.00034124 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 63 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1372-25_0_4_line_0 |  | 0 | 1 | 0.085309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1372-25_0_4_line_1 |  | 0 | 2 | 0.14913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1372-25_0_4_line_2 |  | 0 | 3 | 0.17296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1372-25_0_4_line_3 |  | 1 | 4 | 0.050511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1372-25_0_4_line_4 |  | 1 | 5 | 0.094557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1372-25_0_4_line_5 |  | 2 | 6 | 0.10658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1372-25_0_4_line_6 |  | 3 | 7 | 0.020324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1372-25_0_4_line_7 |  | 5 | 9 | 0.029846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1372-25_0_4_line_8 |  | 5 | 10 | 0.12382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1372-25_0_4_line_9 |  | 6 | 18 | 0.11503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1372-25_0_4_line_10 |  | 7 | 8 | 0.05536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1372-25_0_4_line_11 |  | 8 | 13 | 0.0061232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1372-25_0_4_line_12 |  | 9 | 11 | 0.05081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1372-25_0_4_line_13 |  | 10 | 12 | 0.035625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1372-25_0_4_line_14 |  | 12 | 14 | 0.017904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1372-25_0_4_line_15 |  | 13 | 15 | 0.2117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1372-25_0_4_line_16 |  | 14 | 54 | 0.097852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1372-25_0_4_line_17 |  | 15 | 16 | 0.041343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1372-25_0_4_line_18 |  | 15 | 17 | 0.17 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1372-25_0_4_line_19 |  | 16 | 47 | 0.18079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1372-25_0_4_line_20 |  | 17 | 31 | 0.10435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1372-25_0_4_line_21 |  | 18 | 43 | 0.030235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1372-25_0_4_line_22 |  | 19 | 20 | 0.01463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1372-25_0_4_line_23 |  | 19 | 21 | 0.027181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1372-25_0_4_line_24 |  | 20 | 22 | 0.030951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1372-25_0_4_line_25 |  | 20 | 23 | 0.052949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1372-25_0_4_line_26 |  | 22 | 24 | 0.017092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1372-25_0_4_line_27 |  | 23 | 25 | 0.060282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1372-25_0_4_line_28 |  | 24 | 26 | 0.094962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1372-25_0_4_line_29 |  | 24 | 27 | 0.083628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1372-25_0_4_line_30 |  | 25 | 28 | 0.029747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1372-25_0_4_line_31 |  | 25 | 29 | 0.19917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1372-25_0_4_line_32 |  | 27 | 30 | 0.03751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1372-25_0_4_line_33 |  | 27 | 31 | 0.097027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1372-25_0_4_line_34 |  | 28 | 32 | 0.092262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1372-25_0_4_line_35 |  | 29 | 34 | 0.018037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1372-25_0_4_line_36 |  | 30 | 50 | 0.062086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1372-25_0_4_line_37 |  | 31 | 46 | 0.008044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1372-25_0_4_line_38 |  | 33 | 34 | 0.016671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1372-25_0_4_line_39 |  | 33 | 35 | 0.033331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1372-25_0_4_line_40 |  | 35 | 38 | 0.0097079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1372-25_0_4_line_41 |  | 36 | 37 | 0.00661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1372-25_0_4_line_42 |  | 36 | 38 | 0.015605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1372-25_0_4_line_43 |  | 37 | 39 | 0.015264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1372-25_0_4_line_44 |  | 40 | 41 | 0.004361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1372-25_0_4_line_45 |  | 40 | 42 | 0.044665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1372-25_0_4_line_46 |  | 41 | 46 | 0.1034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1372-25_0_4_line_47 |  | 42 | 58 | 0.0064792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1372-25_0_4_line_48 |  | 43 | 44 | 0.053359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1372-25_0_4_line_49 |  | 44 | 45 | 0.032344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1372-25_0_4_line_50 |  | 45 | 55 | 0.0018694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1372-25_0_4_line_51 |  | 47 | 48 | 0.17216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1372-25_0_4_line_52 |  | 47 | 49 | 0.052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1372-25_0_4_line_53 |  | 48 | 51 | 0.013951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1372-25_0_4_line_54 |  | 49 | 60 | 0.016373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1372-25_0_4_line_55 |  | 51 | 52 | 0.0033084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1372-25_0_4_line_56 |  | 52 | 53 | 0.045768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1372-25_0_4_line_57 |  | 55 | 56 | 0.40417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1372-25_0_4_line_58 |  | 56 | 57 | 0.033309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1372-25_0_4_line_59 |  | 59 | 60 | 0.098317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1372-25_0_4_line_60 |  | 60 | 61 | 0.045177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1372-25_0_4_line_61 |  | 61 | 62 | 0.027299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1372-25_0_4_line_62 |  | 61 | 63 | 0.15355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1372-25_0_4_line_63 |  | 63 | 67 | 0.083955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_1372-25_0_4_line_64 |  | 64 | 65 | 0.019699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_1372-25_0_4_line_65 |  | 64 | 66 | 0.011996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1372-25_0_4_line_66 |  | 65 | 67 | 0.044377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_1372-25_0_4_line_67 |  | 66 | 68 | 0.011522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_1372-25_0_4_line_68 |  | 68 | 69 | 0.015085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_1372-25_0_4_line_69 |  | 69 | 122 | 0.0080812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_1372-25_0_4_line_70 |  | 70 | 71 | 0.010846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1372-25_0_4_line_71 |  | 71 | 72 | 0.049854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1372-25_0_4_line_72 |  | 72 | 73 | 0.057695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1372-25_0_4_line_73 |  | 73 | 74 | 0.022312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1372-25_0_4_line_74 |  | 74 | 75 | 0.01131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1372-25_0_4_line_75 |  | 75 | 76 | 0.0097269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1372-25_0_4_line_76 |  | 76 | 77 | 0.023578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1372-25_0_4_line_77 |  | 77 | 78 | 0.016101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1372-25_0_4_line_78 |  | 78 | 79 | 0.016829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1372-25_0_4_line_79 |  | 78 | 80 | 0.1016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1372-25_0_4_line_80 |  | 79 | 81 | 0.02323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1372-25_0_4_line_81 |  | 80 | 82 | 0.032287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1372-25_0_4_line_82 |  | 80 | 83 | 0.046995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1372-25_0_4_line_83 |  | 81 | 105 | 0.0038368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1372-25_0_4_line_84 |  | 83 | 98 | 0.057987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1372-25_0_4_line_85 |  | 84 | 85 | 0.01775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1372-25_0_4_line_86 |  | 85 | 86 | 0.011673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1372-25_0_4_line_87 |  | 85 | 87 | 0.023136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1372-25_0_4_line_88 |  | 87 | 88 | 0.042231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1372-25_0_4_line_89 |  | 87 | 89 | 0.012403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1372-25_0_4_line_90 |  | 88 | 90 | 0.022884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1372-25_0_4_line_91 |  | 88 | 91 | 0.0039915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1372-25_0_4_line_92 |  | 89 | 92 | 0.0667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1372-25_0_4_line_93 |  | 90 | 93 | 0.024661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1372-25_0_4_line_94 |  | 92 | 94 | 0.023359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1372-25_0_4_line_95 |  | 94 | 95 | 0.011267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1372-25_0_4_line_96 |  | 95 | 96 | 0.036548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1372-25_0_4_line_97 |  | 95 | 97 | 0.045126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1372-25_0_4_line_98 |  | 96 | 98 | 0.019462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1372-25_0_4_line_99 |  | 97 | 99 | 0.022459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1372-25_0_4_line_100 |  | 98 | 100 | 0.02961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1372-25_0_4_line_101 |  | 101 | 102 | 0.0035377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_1372-25_0_4_line_102 |  | 101 | 103 | 0.011202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1372-25_0_4_line_103 |  | 102 | 104 | 0.025992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_1372-25_0_4_line_104 |  | 103 | 105 | 0.019306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1372-25_0_4_line_105 |  | 103 | 106 | 0.027673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1372-25_0_4_line_106 |  | 104 | 107 | 0.0060057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_1372-25_0_4_line_107 |  | 106 | 108 | 0.01344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1372-25_0_4_line_108 |  | 107 | 109 | 0.024181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_1372-25_0_4_line_109 |  | 109 | 110 | 0.0019676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_1372-25_0_4_line_110 |  | 110 | 111 | 0.012359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_1372-25_0_4_line_111 |  | 111 | 112 | 0.013053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_1372-25_0_4_line_112 |  | 112 | 113 | 0.053151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_1372-25_0_4_line_113 |  | 113 | 114 | 0.00077933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_1372-25_0_4_line_114 |  | 114 | 115 | 0.0098335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_1372-25_0_4_line_115 |  | 115 | 116 | 0.0090892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_1372-25_0_4_line_116 |  | 116 | 117 | 0.0049834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_1372-25_0_4_line_117 |  | 117 | 118 | 0.013485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_1372-25_0_4_line_118 |  | 118 | 119 | 0.047436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_1372-25_0_4_line_119 |  | 119 | 120 | 0.0079868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_1372-25_0_4_line_120 |  | 119 | 121 | 0.058622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1372-25_0_4_line_121 |  | 120 | 122 | 0.023341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_1372-25_0_4_line_122 |  | 121 | 123 | 0.010282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1372-25_0_4_line_123 |  | 123 | 124 | 0.018691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1372-25_0_4_line_124 |  | 124 | 125 | 0.017968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1372-25_0_4_trafo_66 | 0.63 MVA 20/0.4 kV | 126 | 63 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2693543.2596 | 1209247.5072 | 2693508.7964 | 1209291.1632 | 2693501.8206 | 1209301.6165 | 2693499.1708 | 1209306.2448 | 2693497.4534 | 1209312.0106 | 2693496.9508 | 1209317.7618
1 | 2693496.9508 | 1209317.7618 | 2693633.8393 | 1209376.9325
2 | 2693496.9508 | 1209317.7618 | 2693386.2686 | 1209450.6743
3 | 2693543.2596 | 1209247.5072 | 2693539.0508 | 1209248.7643 | 2693530.582 | 1209254.0574 | 2693515.9829 | 1209263.4015 | 2693498.2712 | 1209270.0285
4 | 2693543.2596 | 1209247.5072 | 2693545.1512 | 1209245.6578 | 2693550.2804 | 1209242.436 | 2693555.6611 | 1209236.2607 | 2693560.3827 | 1209202.3118 | 2693566.6497 | 1209181.8074 | 2693571.0479 | 1209174.7827 | 2693574.158 | 1209168.4494 | 2693578.1114 | 1209163.1189
5 | 2693635.2034 | 1209483.5002 | 2693633.8393 | 1209376.9325
6 | 2693386.2686 | 1209450.6743 | 2693378.483 | 1209455.578 | 2693368.5649 | 1209460.6116
7 | 2693578.1114 | 1209163.1189 | 2693577.8505 | 1209157.9447 | 2693580.2995 | 1209152.5572 | 2693581.2219 | 1209146.1007 | 2693581.3971 | 1209141.2335 | 2693579.4862 | 1209134.1321
8 | 2693578.1114 | 1209163.1189 | 2693581.6088 | 1209164.5636 | 2693585.3093 | 1209163.243 | 2693586.9586 | 1209160.3669 | 2693588.3123 | 1209155.496 | 2693589.4469 | 1209149.0872 | 2693590.0742 | 1209140.6025 | 2693590.5148 | 1209125.1212 | 2693590.7613 | 1209118.6206 | 2693591.989 | 1209114.993 | 2693593.9431 | 1209110.6207 | 2693596.3097 | 1209108.0672 | 2693601.0779 | 1209105.0844 | 2693606.0905 | 1209103.4842 | 2693614.034 | 1209101.6409 | 2693623.3731 | 1209099.0412 | 2693640.3066 | 1209092.1355 | 2693650.3856 | 1209086.3879
9 | 2693745.512 | 1209516.1177 | 2693635.2034 | 1209483.5002
10 | 2693317.9558 | 1209482.1047 | 2693327.1728 | 1209480.4588 | 2693334.2702 | 1209478.235 | 2693342.0135 | 1209474.0866 | 2693368.5649 | 1209460.6116
11 | 2693317.9558 | 1209482.1047 | 2693311.8379 | 1209481.8492
12 | 2693538.1115 | 1209152.5626 | 2693542.6777 | 1209153.2457 | 2693556.1946 | 1209154.2694 | 2693566.5613 | 1209151.0964 | 2693572.3715 | 1209146.6289 | 2693577.2044 | 1209140.4895 | 2693579.4862 | 1209134.1321
13 | 2693682.2645 | 1209071.4959 | 2693673.4829 | 1209072.9432 | 2693651.0085 | 1209086.0327 | 2693650.3856 | 1209086.3879
14 | 2693682.2645 | 1209071.4959 | 2693687.2799 | 1209070.6693 | 2693689.4682 | 1209073.1721 | 2693690.0882 | 1209077.2623 | 2693688.7219 | 1209082.4444
15 | 2693261.2469 | 1209276.2839 | 2693311.8379 | 1209481.8492
16 | 2693688.7219 | 1209082.4444 | 2693722.9618 | 1209174.1104
17 | 2693220.8045 | 1209283.7084 | 2693242.6088 | 1209277.8673 | 2693254.1921 | 1209276.1249 | 2693261.2469 | 1209276.2839
18 | 2693393.5197 | 1209169.4957 | 2693261.2469 | 1209276.2839
19 | 2693064.7327 | 1209192.4557 | 2693220.8045 | 1209283.7084
20 | 2693419.9741 | 1209070.3791 | 2693421.4727 | 1209075.1836 | 2693421.9329 | 1209080.7501 | 2693421.0782 | 1209088.2306 | 2693419.5077 | 1209097.2454 | 2693411.7414 | 1209117.8711 | 2693402.9818 | 1209147.0759 | 2693400.2132 | 1209156.8613 | 2693397.6845 | 1209162.9815 | 2693394.5099 | 1209168.1019 | 2693393.5197 | 1209169.4957
21 | 2693775.5172 | 1209518.5082 | 2693773.8481 | 1209518.3196 | 2693763.4043 | 1209516.2653 | 2693756.4173 | 1209515.8108 | 2693745.512 | 1209516.1177
22 | 2693329.3095 | 1208918.792 | 2693314.7082 | 1208919.7063
23 | 2693292.1613 | 1208911.473 | 2693294.7235 | 1208917.3058 | 2693298.5527 | 1208919.9119 | 2693306.2952 | 1208920.2331 | 2693314.7082 | 1208919.7063
24 | 2693329.3095 | 1208918.792 | 2693309.2984 | 1208942.4034
25 | 2693329.3095 | 1208918.792 | 2693365.1687 | 1208879.8344
26 | 2693298.2479 | 1208955.4421 | 2693309.2984 | 1208942.4034
27 | 2693415.1993 | 1208850.4897 | 2693413.2027 | 1208853.694 | 2693410.6022 | 1208856.1327 | 2693407.3351 | 1208858.4164 | 2693403.4731 | 1208859.8458 | 2693399.3129 | 1208860.4145 | 2693393.4021 | 1208861.1002 | 2693388.5807 | 1208862.1366 | 2693383.4922 | 1208864.2028 | 2693378.3961 | 1208867.2473 | 2693372.9947 | 1208871.3322 | 2693365.1687 | 1208879.8344
28 | 2693211.302 | 1208977.6652 | 2693229.2085 | 1208963.4687 | 2693238.5387 | 1208957.0657 | 2693243.7962 | 1208954.3905 | 2693249.8771 | 1208953.029 | 2693256.6343 | 1208952.1785 | 2693265.0021 | 1208952.8652 | 2693277.8984 | 1208955.6798 | 2693286.0171 | 1208956.7407 | 2693298.2479 | 1208955.4421
29 | 2693298.2479 | 1208955.4421 | 2693298.874 | 1208963.5351 | 2693299.9993 | 1208970.3351 | 2693301.7566 | 1208975.1324 | 2693304.3678 | 1208979.7764 | 2693341.9601 | 1209024.2719
30 | 2693397.397 | 1208831.276 | 2693404.4626 | 1208832.5874 | 2693408.3387 | 1208834.6273 | 2693411.2943 | 1208837.1863 | 2693413.7797 | 1208840.6387 | 2693415.2572 | 1208845.8208 | 2693415.1993 | 1208850.4897
31 | 2693415.1993 | 1208850.4897 | 2693607.6284 | 1208799.1145
32 | 2693341.9601 | 1209024.2719 | 2693340.191 | 1209027.035 | 2693337.1629 | 1209042.2312 | 2693334.94 | 1209054.5603 | 2693338.0125 | 1209059.9531
33 | 2693419.9741 | 1209070.3791 | 2693387.9261 | 1209067.0976 | 2693380.6999 | 1209065.8614 | 2693377.5459 | 1209064.8114 | 2693373.885 | 1209062.6304 | 2693370.7844 | 1209060.1135 | 2693367.9456 | 1209056.9003 | 2693364.5044 | 1209051.3761 | 2693358.918 | 1209043.4945 | 2693351.0315 | 1209034.4095 | 2693341.9601 | 1209024.2719
34 | 2693397.397 | 1208831.276 | 2693395.4369 | 1208823.8959 | 2693395.3562 | 1208816.423 | 2693396.231 | 1208808.1422 | 2693406.6191 | 1208754.1129 | 2693410.9791 | 1208741.0128
35 | 2693607.6284 | 1208799.1145 | 2693612.7352 | 1208816.4133
36 | 2693359.6729 | 1209117.576 | 2693348.1734 | 1209080.0288 | 2693344.7241 | 1209069.1898 | 2693339.4908 | 1209062.5479 | 2693338.0125 | 1209059.9531
37 | 2693419.9741 | 1209070.3791 | 2693428.0061 | 1209071.1387
38 | 2693612.7352 | 1208816.4133 | 2693613.3101 | 1208818.361 | 2693616.4198 | 1208832.6667
39 | 2693625.5113 | 1208864.5057 | 2693621.8053 | 1208857.4428 | 2693616.4198 | 1208832.6667
40 | 2693625.5113 | 1208864.5057 | 2693631.84 | 1208863.8378 | 2693634.7056 | 1208862.1141
41 | 2693646.5217 | 1208852.0307 | 2693651.3051 | 1208847.4687
42 | 2693634.7056 | 1208862.1141 | 2693638.0726 | 1208860.0886 | 2693646.5217 | 1208852.0307
43 | 2693663.4183 | 1208838.2286 | 2693653.9578 | 1208844.9388 | 2693651.3051 | 1208847.4687
44 | 2693448.4185 | 1208968.8338 | 2693446.0704 | 1208972.5088
45 | 2693448.4185 | 1208968.8338 | 2693472.1542 | 1208981.9921 | 2693464.0507 | 1208997.5321
46 | 2693428.0061 | 1209071.1387 | 2693426.1576 | 1209062.9487 | 2693424.864 | 1209051.8543 | 2693424.983 | 1209039.4033 | 2693427.7443 | 1209016.0197 | 2693433.7812 | 1208991.7423 | 2693446.0704 | 1208972.5088
47 | 2693461.0548 | 1209003.2771 | 2693464.0507 | 1208997.5321
48 | 2693775.5172 | 1209518.5082 | 2693784.48 | 1209519.5209 | 2693791.8992 | 1209521.0163 | 2693803.6863 | 1209525.6268 | 2693814.3855 | 1209532.2217 | 2693822.3291 | 1209539.0401 | 2693823.1092 | 1209539.7822
49 | 2693845.4178 | 1209563.1638 | 2693832.9652 | 1209549.1586 | 2693823.1092 | 1209539.7822
50 | 2693845.4178 | 1209563.1638 | 2693846.0633 | 1209564.9183
51 | 2693064.7327 | 1209192.4557 | 2693013.3757 | 1209356.7766
52 | 2693064.7327 | 1209192.4557 | 2693070.1991 | 1209184.1687 | 2693079.1928 | 1209166.1635 | 2693088.004 | 1209146.2208 | 2693088.0636 | 1209146.0898
53 | 2693013.3757 | 1209356.7766 | 2693010.6975 | 1209356.4236 | 2692999.449 | 1209356.2481
54 | 2693092.2571 | 1209130.4321 | 2693091.522 | 1209133.6895 | 2693090.799 | 1209140.0714 | 2693088.0636 | 1209146.0898
55 | 2692996.141 | 1209356.1966 | 2692999.449 | 1209356.2481
56 | 2692996.141 | 1209356.1966 | 2692992.5319 | 1209356.1403 | 2692981.8704 | 1209357.2972 | 2692965.9828 | 1209367.4342 | 2692960.6882 | 1209375.4461 | 2692960.0144 | 1209378.3543
57 | 2693846.0633 | 1209564.9183 | 2694238.7816 | 1209660.4395
58 | 2694238.7816 | 1209660.4395 | 2694238.1779 | 1209666.8899 | 2694236.4585 | 1209683.3294 | 2694236.8621 | 1209693.6227
59 | 2693092.2571 | 1209130.4321 | 2693094.4294 | 1209128.1311 | 2693122.8656 | 1209114.3877 | 2693150.4237 | 1209097.9734 | 2693176.2607 | 1209079.9666
60 | 2693092.2571 | 1209130.4321 | 2693093.212 | 1209120.885 | 2693096.4122 | 1209111.184 | 2693098.7294 | 1209096.1878 | 2693099.9972 | 1209086.0786
61 | 2693082.3022 | 1209105.7714 | 2693091.2054 | 1209100.3955 | 2693093.8158 | 1209097.79 | 2693099.9972 | 1209086.0786
62 | 2693113.2786 | 1208935.1621 | 2693117.6296 | 1208954.0205 | 2693118.7259 | 1208961.2313 | 2693119.0613 | 1208970.4316 | 2693117.9286 | 1208981.1322 | 2693114.7557 | 1209020.2535 | 2693113.2627 | 1209028.2244 | 2693110.3805 | 1209038.4975 | 2693104.5738 | 1209055.9075 | 2693102.5794 | 1209065.316 | 2693099.9972 | 1209086.0786
63 | 2693113.2786 | 1208935.1621 | 2693112.0949 | 1208924.2919 | 2693112.3508 | 1208917.1578 | 2693113.6285 | 1208912.2633 | 2693117.3433 | 1208903.6933 | 2693128.2414 | 1208884.5171 | 2693144.6307 | 1208860.078
64 | 2693183.9077 | 1208809.8135 | 2693169.9659 | 1208823.7303
65 | 2693183.9077 | 1208809.8135 | 2693182.6486 | 1208806.2137 | 2693182.8066 | 1208802.4247 | 2693183.9177 | 1208798.1772
66 | 2693169.9659 | 1208823.7303 | 2693167.0624 | 1208826.6285 | 2693144.6307 | 1208860.078
67 | 2693189.8778 | 1208788.4249 | 2693189.1253 | 1208789.259 | 2693185.6677 | 1208794.0082 | 2693183.971 | 1208797.9732 | 2693183.9177 | 1208798.1772
68 | 2693189.8778 | 1208788.4249 | 2693194.5259 | 1208783.2726 | 2693196.6223 | 1208780.0031 | 2693198.2652 | 1208776.0706 | 2693198.2652 | 1208776.0706
69 | 2693198.2652 | 1208776.0706 | 2693198.1952 | 1208772.2781 | 2693196.0329 | 1208768.5751 | 2693196.0329 | 1208768.5751
70 | 2693049.921 | 1209004.7434 | 2693050.6484 | 1208999.7399 | 2693045.2375 | 1208997.6782
71 | 2692998.6345 | 1209003.7652 | 2693017.554 | 1209006.9622 | 2693028.6752 | 1209005.6235 | 2693037.3887 | 1208999.7443 | 2693042.4025 | 1208996.5981 | 2693045.2375 | 1208997.6782
72 | 2692998.6345 | 1209003.7652 | 2692998.6345 | 1209003.7652 | 2692987.9575 | 1208997.5836 | 2692976.5631 | 1208981.8177 | 2692977.5945 | 1208970.7708 | 2692976.2301 | 1208961.7212 | 2692970.8842 | 1208959.8675
73 | 2692970.8842 | 1208959.8675 | 2692964.5466 | 1208957.6698 | 2692950.4027 | 1208959.284 | 2692949.1043 | 1208959.7161
74 | 2692949.1043 | 1208959.7161 | 2692938.3731 | 1208963.2882
75 | 2692938.3731 | 1208963.2882 | 2692938.3731 | 1208963.2882 | 2692935.6353 | 1208958.9427 | 2692934.2364 | 1208954.5702
76 | 2692932.6376 | 1208931.7962 | 2692932.6564 | 1208935.9142 | 2692930.6908 | 1208943.4886 | 2692934.2364 | 1208954.5702
77 | 2692929.6355 | 1208916.5541 | 2692932.5891 | 1208921.2032 | 2692932.6376 | 1208931.7962
78 | 2692929.6355 | 1208916.5541 | 2692944.1168 | 1208907.9797
79 | 2692932.6825 | 1208871.2934 | 2692928.5732 | 1208882.259 | 2692915.1779 | 1208894.3697 | 2692911.8426 | 1208898.6095 | 2692899.1424 | 1208924.1845 | 2692900.0996 | 1208929.6031 | 2692921.5397 | 1208921.3424 | 2692929.6355 | 1208916.5541
80 | 2692944.1168 | 1208907.9797 | 2692964.1059 | 1208896.144
81 | 2692932.6825 | 1208871.2934 | 2692936.1718 | 1208867.9121 | 2692950.7972 | 1208860.3014 | 2692958.3281 | 1208852.3651
82 | 2692932.6825 | 1208871.2934 | 2692933.6148 | 1208867.5721 | 2692936.9243 | 1208863.532 | 2692943.3134 | 1208859.4732 | 2692949.024 | 1208855.0369 | 2692950.9232 | 1208849.7741 | 2692952.8586 | 1208841.2096 | 2692953.6105 | 1208832.4821
83 | 2692967.4074 | 1208894.1892 | 2692964.1059 | 1208896.144
84 | 2692920.7935 | 1208785.2505 | 2692924.9045 | 1208793.698 | 2692932.0111 | 1208801.1692 | 2692939.0469 | 1208810.2626 | 2692948.5959 | 1208822.0081 | 2692951.5347 | 1208827.124 | 2692953.6105 | 1208832.4821
85 | 2693055.7106 | 1208685.4966 | 2693052.2853 | 1208693.0483 | 2693055.0308 | 1208702.0992
86 | 2693055.7106 | 1208685.4966 | 2693065.9567 | 1208679.8526
87 | 2693033.6671 | 1208678.2704 | 2693055.7106 | 1208685.4966
88 | 2693033.6671 | 1208678.2704 | 2693052.1179 | 1208668.6849 | 2693067.2441 | 1208653.3882
89 | 2693033.6671 | 1208678.2704 | 2693022.2693 | 1208683.1627
90 | 2693090.1067 | 1208655.3905 | 2693067.2441 | 1208653.3882
91 | 2693067.2441 | 1208653.3882 | 2693068.4304 | 1208649.5771
92 | 2692970.8822 | 1208725.5575 | 2692985.0691 | 1208714.1816 | 2693002.6432 | 1208701.3246 | 2693022.2693 | 1208683.1627
93 | 2693090.1067 | 1208655.3905 | 2693103.5765 | 1208676.0701
94 | 2692970.8822 | 1208725.5575 | 2692957.9205 | 1208735.9511 | 2692951.3574 | 1208737.5055 | 2692951.3574 | 1208737.5055
95 | 2692940.4448 | 1208734.7003 | 2692951.3574 | 1208737.5055
96 | 2692940.4448 | 1208734.7003 | 2692922.5123 | 1208764.2298 | 2692922.0782 | 1208766.182
97 | 2692910.1206 | 1208720.6855 | 2692912.2975 | 1208722.4873 | 2692915.6896 | 1208718.5152 | 2692920.1075 | 1208718.495 | 2692920.1248 | 1208726.6563 | 2692933.6912 | 1208727.0122 | 2692939.3299 | 1208730.6136 | 2692940.4448 | 1208734.7003
98 | 2692920.7935 | 1208785.2505 | 2692919.5036 | 1208777.7587 | 2692922.0782 | 1208766.182
99 | 2692910.1206 | 1208720.6855 | 2692911.3376 | 1208719.1923 | 2692916.3704 | 1208711.421 | 2692916.5505 | 1208704.2523 | 2692914.396 | 1208700.7598
100 | 2692928.2467 | 1208813.908 | 2692920.7935 | 1208785.2505
101 | 2692993.6016 | 1208878.5506 | 2692996.6226 | 1208876.7098
102 | 2692984.0353 | 1208884.3798 | 2692993.6016 | 1208878.5506
103 | 2693018.8185 | 1208863.1848 | 2692996.6226 | 1208876.7098
104 | 2692984.0353 | 1208884.3798 | 2692979.3471 | 1208887.1197 | 2692967.4074 | 1208894.1892
105 | 2692984.0353 | 1208884.3798 | 2692988.8497 | 1208893.0495 | 2692987.5503 | 1208906.1714 | 2692984.5844 | 1208909.6487
106 | 2693018.8185 | 1208863.1848 | 2693023.9471 | 1208860.0598
107 | 2692984.5844 | 1208909.6487 | 2692975.8625 | 1208919.8747
108 | 2693023.9471 | 1208860.0598 | 2693025.6319 | 1208859.0332 | 2693030.0246 | 1208854.7654 | 2693034.9191 | 1208847.0921 | 2693038.2437 | 1208840.9525
109 | 2693039.1806 | 1208839.2223 | 2693038.2437 | 1208840.9525
110 | 2693039.1806 | 1208839.2223 | 2693045.0654 | 1208828.3546
111 | 2693045.0654 | 1208828.3546 | 2693051.2808 | 1208816.8763
112 | 2693051.2808 | 1208816.8763 | 2693055.1642 | 1208809.7048 | 2693058.0248 | 1208805.6912 | 2693063.6633 | 1208802.4769 | 2693070.8146 | 1208800.2536 | 2693080.4456 | 1208798.9363 | 2693096.6852 | 1208796.901
113 | 2693096.6852 | 1208796.901 | 2693097.4585 | 1208796.8041
114 | 2693107.1397 | 1208795.0945 | 2693099.0643 | 1208796.6029 | 2693097.4585 | 1208796.8041
115 | 2693107.1397 | 1208795.0945 | 2693107.1397 | 1208795.0945 | 2693115.4096 | 1208791.3234
116 | 2693115.4096 | 1208791.3234 | 2693115.5326 | 1208791.2673 | 2693119.6445 | 1208788.6986
117 | 2693130.3027 | 1208780.525 | 2693124.9613 | 1208785.3771 | 2693119.6445 | 1208788.6986
118 | 2693168.6134 | 1208754.5932 | 2693162.1376 | 1208755.426 | 2693155.4355 | 1208758.0899 | 2693150.0738 | 1208762.5648 | 2693130.3027 | 1208780.525
119 | 2693168.6134 | 1208754.5932 | 2693176.3555 | 1208756.5552
120 | 2693168.6134 | 1208754.5932 | 2693170.8447 | 1208752.9047 | 2693176.9225 | 1208752.2436 | 2693187.7412 | 1208752.2903 | 2693196.5642 | 1208751.1161 | 2693204.2783 | 1208748.8907 | 2693211.4863 | 1208745.4787 | 2693218.444 | 1208742.0295 | 2693223.2849 | 1208738.1217
121 | 2693176.3555 | 1208756.5552 | 2693180.4429 | 1208757.591 | 2693189.2253 | 1208762.9095 | 2693196.0329 | 1208768.5751
122 | 2693223.2849 | 1208738.1217 | 2693224.2271 | 1208737.3611 | 2693227.3406 | 1208728.8415
123 | 2693228.2402 | 1208710.193 | 2693227.4917 | 1208728.4283 | 2693227.3406 | 1208728.8415
124 | 2693236.1025 | 1208695.3352 | 2693228.5353 | 1208703.0053 | 2693228.2402 | 1208710.193

## bus_geodata
| x | y | coords
0 | 2693496.9508 | 1209317.7618
1 | 2693543.2596 | 1209247.5072
2 | 2693633.8393 | 1209376.9325
3 | 2693386.2686 | 1209450.6743
4 | 2693498.2712 | 1209270.0285
5 | 2693578.1114 | 1209163.1189
6 | 2693635.2034 | 1209483.5002
7 | 2693368.5649 | 1209460.6116
8 | 2693317.9558 | 1209482.1047
9 | 2693579.4862 | 1209134.1321
10 | 2693650.3856 | 1209086.3879
11 | 2693538.1115 | 1209152.5626
12 | 2693682.2645 | 1209071.4959
13 | 2693311.8379 | 1209481.8492
14 | 2693688.7219 | 1209082.4444
15 | 2693261.2469 | 1209276.2839
16 | 2693220.8045 | 1209283.7084
17 | 2693393.5197 | 1209169.4957
18 | 2693745.512 | 1209516.1177
19 | 2693314.7082 | 1208919.7063
20 | 2693329.3095 | 1208918.792
21 | 2693292.1613 | 1208911.473
22 | 2693309.2984 | 1208942.4034
23 | 2693365.1687 | 1208879.8344
24 | 2693298.2479 | 1208955.4421
25 | 2693415.1993 | 1208850.4897
26 | 2693211.302 | 1208977.6652
27 | 2693341.9601 | 1209024.2719
28 | 2693397.397 | 1208831.276
29 | 2693607.6284 | 1208799.1145
30 | 2693338.0125 | 1209059.9531
31 | 2693419.9741 | 1209070.3791
32 | 2693410.9791 | 1208741.0128
33 | 2693616.4198 | 1208832.6667
34 | 2693612.7352 | 1208816.4133
35 | 2693625.5113 | 1208864.5057
36 | 2693646.5217 | 1208852.0307
37 | 2693651.3051 | 1208847.4687
38 | 2693634.7056 | 1208862.1141
39 | 2693663.4183 | 1208838.2286
40 | 2693448.4185 | 1208968.8338
41 | 2693446.0704 | 1208972.5088
42 | 2693464.0507 | 1208997.5321
43 | 2693775.5172 | 1209518.5082
44 | 2693823.1092 | 1209539.7822
45 | 2693845.4178 | 1209563.1638
46 | 2693428.0061 | 1209071.1387
47 | 2693064.7327 | 1209192.4557
48 | 2693013.3757 | 1209356.7766
49 | 2693088.0636 | 1209146.0898
50 | 2693359.6729 | 1209117.576
51 | 2692999.449 | 1209356.2481
52 | 2692996.141 | 1209356.1966
53 | 2692960.0144 | 1209378.3543
54 | 2693722.9618 | 1209174.1104
55 | 2693846.0633 | 1209564.9183
56 | 2694238.7816 | 1209660.4395
57 | 2694236.8621 | 1209693.6227
58 | 2693461.0548 | 1209003.2771
59 | 2693176.2607 | 1209079.9666
60 | 2693092.2571 | 1209130.4321
61 | 2693099.9972 | 1209086.0786
62 | 2693082.3022 | 1209105.7714
63 | 2693113.2786 | 1208935.1621
64 | 2693183.9077 | 1208809.8135
65 | 2693169.9659 | 1208823.7303
66 | 2693183.9177 | 1208798.1772
67 | 2693144.6307 | 1208860.078
68 | 2693189.8778 | 1208788.4249
69 | 2693198.2652 | 1208776.0706
70 | 2693049.921 | 1209004.7434
71 | 2693045.2375 | 1208997.6782
72 | 2692998.6345 | 1209003.7652
73 | 2692970.8842 | 1208959.8675
74 | 2692949.1043 | 1208959.7161
75 | 2692938.3731 | 1208963.2882
76 | 2692934.2364 | 1208954.5702
77 | 2692932.6376 | 1208931.7962
78 | 2692929.6355 | 1208916.5541
79 | 2692944.1168 | 1208907.9797
80 | 2692932.6825 | 1208871.2934
81 | 2692964.1059 | 1208896.144
82 | 2692958.3281 | 1208852.3651
83 | 2692953.6105 | 1208832.4821
84 | 2693055.0308 | 1208702.0992
85 | 2693055.7106 | 1208685.4966
86 | 2693065.9567 | 1208679.8526
87 | 2693033.6671 | 1208678.2704
88 | 2693067.2441 | 1208653.3882
89 | 2693022.2693 | 1208683.1627
90 | 2693090.1067 | 1208655.3905
91 | 2693068.4304 | 1208649.5771
92 | 2692970.8822 | 1208725.5575
93 | 2693103.5765 | 1208676.0701
94 | 2692951.3574 | 1208737.5055
95 | 2692940.4448 | 1208734.7003
96 | 2692922.0782 | 1208766.182
97 | 2692910.1206 | 1208720.6855
98 | 2692920.7935 | 1208785.2505
99 | 2692914.396 | 1208700.7598
100 | 2692928.2467 | 1208813.908
101 | 2692993.6016 | 1208878.5506
102 | 2692996.6226 | 1208876.7098
103 | 2692984.0353 | 1208884.3798
104 | 2693018.8185 | 1208863.1848
105 | 2692967.4074 | 1208894.1892
106 | 2692984.5844 | 1208909.6487
107 | 2693023.9471 | 1208860.0598
108 | 2692975.8625 | 1208919.8747
109 | 2693038.2437 | 1208840.9525
110 | 2693039.1806 | 1208839.2223
111 | 2693045.0654 | 1208828.3546
112 | 2693051.2808 | 1208816.8763
113 | 2693096.6852 | 1208796.901
114 | 2693097.4585 | 1208796.8041
115 | 2693107.1397 | 1208795.0945
116 | 2693115.4096 | 1208791.3234
117 | 2693119.6445 | 1208788.6986
118 | 2693130.3027 | 1208780.525
119 | 2693168.6134 | 1208754.5932
120 | 2693176.3555 | 1208756.5552
121 | 2693223.2849 | 1208738.1217
122 | 2693196.0329 | 1208768.5751
123 | 2693227.3406 | 1208728.8415
124 | 2693228.2402 | 1208710.193
125 | 2693236.1025 | 1208695.3352
126 | 2693183.9077 | 1208809.8135

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98101 | -0.36635 | 0.00053185 | 0.00013329
1 | 0.98082 | -0.37009 | 0 | 0
2 | 0.98039 | -0.3786 | 0.00090024 | 0.00022562
3 | 0.9822 | -0.3429 | 0 | 0
4 | 0.98079 | -0.3706 | 0.00056002 | 0.00014036
5 | 0.98066 | -0.37328 | 0 | 0
6 | 0.98003 | -0.38561 | 0.0011652 | 0.00029202
7 | 0.98234 | -0.34015 | 0.00045941 | 0.00011514
8 | 0.98274 | -0.3322 | 0 | 0
9 | 0.98065 | -0.37338 | 0 | 0
10 | 0.98047 | -0.37702 | 0.00072854 | 0.00018259
11 | 0.98064 | -0.37354 | 0.00018251 | 4.5741e-05
12 | 0.98044 | -0.37763 | 0.00044548 | 0.00011165
13 | 0.98279 | -0.33132 | 0.0015897 | 0.00039842
14 | 0.98043 | -0.37779 | 0.00027126 | 6.7985e-05
15 | 0.98464 | -0.2949 | 0.00029328 | 7.3503e-05
16 | 0.98571 | -0.27413 | 0.00089322 | 0.00022386
17 | 0.98179 | -0.35047 | 0.00024052 | 6.0281e-05
18 | 0.97977 | -0.39074 | 0.00090935 | 0.0002279
19 | 0.97708 | -0.44274 | 0.00064626 | 0.00016197
20 | 0.97709 | -0.44244 | 0 | 0
21 | 0.97707 | -0.44297 | 0.00046369 | 0.00011621
22 | 0.97739 | -0.43664 | 0.00027666 | 6.9337e-05
23 | 0.97664 | -0.4513 | 0.00094347 | 0.00023646
24 | 0.97756 | -0.43335 | 0 | 0
25 | 0.97618 | -0.46035 | 0 | 0
26 | 0.97725 | -0.43935 | 0.003459 | 0.00086691
27 | 0.97864 | -0.412 | 0 | 0
28 | 0.97615 | -0.46102 | 0 | 0
29 | 0.97489 | -0.48577 | 0 | 0
30 | 0.97858 | -0.41316 | 0.00073746 | 0.00018482
31 | 0.98006 | -0.38428 | 0 | 0
32 | 0.97604 | -0.46311 | 0.0012366 | 0.00030992
33 | 0.97468 | -0.49005 | 0.0005057 | 0.00012674
34 | 0.97478 | -0.48807 | 0.00050925 | 0.00012763
35 | 0.97449 | -0.49368 | 0 | 0
36 | 0.97437 | -0.49615 | 0.0033151 | 0.00083084
37 | 0.97436 | -0.49635 | 0.00047634 | 0.00011938
38 | 0.97444 | -0.49474 | 0.0010261 | 0.00025716
39 | 0.97434 | -0.49667 | 0.0011292 | 0.000283
40 | 0.97983 | -0.38879 | 0 | 0
41 | 0.97983 | -0.38865 | 0.00040358 | 0.00010115
42 | 0.97975 | -0.39021 | 0.00026334 | 6.6e-05
43 | 0.97973 | -0.39159 | 0.00091064 | 0.00022823
44 | 0.9797 | -0.39221 | 0.00023703 | 5.9406e-05
45 | 0.97969 | -0.39244 | 0 | 0
46 | 0.98004 | -0.3846 | 0 | 0
47 | 0.99053 | -0.18093 | 0.0011166 | 0.00027984
48 | 0.99006 | -0.1901 | 0 | 0
49 | 0.99211 | -0.15049 | 0.0030185 | 0.00075652
50 | 0.97853 | -0.41426 | 0.00096521 | 0.00024191
51 | 0.99002 | -0.19084 | 0.00073223 | 0.00018351
52 | 0.99001 | -0.19097 | 0.00077079 | 0.00019318
53 | 0.98995 | -0.19218 | 0.001489 | 0.00037319
54 | 0.98041 | -0.37818 | 0.00021724 | 5.4445e-05
55 | 0.97969 | -0.39245 | 0.00017925 | 4.4925e-05
56 | 0.97961 | -0.394 | 0 | 0
57 | 0.97961 | -0.39412 | 0.00020268 | 5.0796e-05
58 | 0.97975 | -0.39039 | 0.0014889 | 0.00037316
59 | 0.99239 | -0.14514 | 0.0029206 | 0.00073198
60 | 0.99265 | -0.14005 | 0 | 0
61 | 0.99427 | -0.10899 | 0 | 0
62 | 0.99424 | -0.10973 | 0.0015412 | 0.00038625
63 | 1 | 0 | -0.18157 | -0.046165
64 | 0.99379 | -0.11792 | 0 | 0
65 | 0.99461 | -0.10225 | 0.0005115 | 0.00012819
66 | 0.99329 | -0.12748 | 0.0021903 | 0.00054893
67 | 0.99646 | -0.066899 | 0.00077364 | 0.00019389
68 | 0.99281 | -0.13652 | 0.0023397 | 0.00058638
69 | 0.9922 | -0.14816 | 0.001434 | 0.00035941
70 | 0.97849 | -0.41387 | 0.00090967 | 0.00022799
71 | 0.9785 | -0.41369 | 0.00071466 | 0.00017911
72 | 0.97857 | -0.41221 | 0.0016363 | 0.00041009
73 | 0.97875 | -0.40878 | 0.001798 | 0.00045063
74 | 0.97885 | -0.40673 | 0.0024992 | 0.00062636
75 | 0.97893 | -0.40517 | 0.0034124 | 0.00085523
76 | 0.97903 | -0.40323 | 0.0017495 | 0.00043848
77 | 0.97931 | -0.39778 | 0.0012095 | 0.00030312
78 | 0.97951 | -0.3937 | 0 | 0
79 | 0.98026 | -0.37918 | 0.0025683 | 0.00064367
80 | 0.97633 | -0.45591 | 0 | 0
81 | 0.98134 | -0.35809 | 0.00567 | 0.001421
82 | 0.97624 | -0.45765 | 0.0029512 | 0.00073964
83 | 0.97499 | -0.48227 | 0.0045636 | 0.0011438
84 | 0.97113 | -0.55857 | 0.0015111 | 0.00037871
85 | 0.97115 | -0.55808 | 0 | 0
86 | 0.97114 | -0.55837 | 0.0013464 | 0.00033744
87 | 0.97121 | -0.55685 | 0 | 0
88 | 0.97107 | -0.55968 | 0 | 0
89 | 0.97129 | -0.55537 | 0.0017476 | 0.000438
90 | 0.97103 | -0.56056 | 0 | 0
91 | 0.97106 | -0.55979 | 0.0015386 | 0.0003856
92 | 0.9718 | -0.54523 | 0.010389 | 0.0026037
93 | 0.97098 | -0.56151 | 0.0020834 | 0.00052214
94 | 0.97221 | -0.5372 | 0.00071113 | 0.00017823
95 | 0.97241 | -0.53318 | 0 | 0
96 | 0.97316 | -0.51843 | 0.0015299 | 0.00038343
97 | 0.9723 | -0.53533 | 0 | 0
98 | 0.97358 | -0.51004 | 0 | 0
99 | 0.97225 | -0.5364 | 0.0025772 | 0.00064592
100 | 0.97351 | -0.51147 | 0.0026268 | 0.00065833
101 | 0.98325 | -0.32105 | 0.0027648 | 0.00069294
102 | 0.98335 | -0.31896 | 0.005288 | 0.0013253
103 | 0.98259 | -0.33376 | 0 | 0
104 | 0.98421 | -0.30236 | 0.005271 | 0.001321
105 | 0.98154 | -0.35422 | 0.0028686 | 0.00071894
106 | 0.98248 | -0.33587 | 0.0017487 | 0.00043827
107 | 0.98435 | -0.29962 | 0.0053429 | 0.0013391
108 | 0.98245 | -0.33648 | 0.0024801 | 0.00062156
109 | 0.98496 | -0.2878 | 0.0081973 | 0.0020544
110 | 0.98501 | -0.28674 | 0.0051936 | 0.0013017
111 | 0.98538 | -0.27972 | 0.0051498 | 0.0012907
112 | 0.98578 | -0.27191 | 0.0083624 | 0.0020958
113 | 0.98756 | -0.23751 | 0.0018466 | 0.00046279
114 | 0.98759 | -0.237 | 0.00020366 | 5.1042e-05
115 | 0.98792 | -0.23052 | 0.00032825 | 8.2266e-05
116 | 0.98823 | -0.22453 | 0.0026791 | 0.00067145
117 | 0.98841 | -0.22117 | 0.0037338 | 0.00093578
118 | 0.98889 | -0.21177 | 0.0031434 | 0.00078781
119 | 0.99065 | -0.1779 | 0 | 0
120 | 0.99096 | -0.172 | 0.0033383 | 0.00083666
121 | 0.99042 | -0.18239 | 0.00077325 | 0.0001938
122 | 0.99188 | -0.15434 | 0.0013555 | 0.00033972
123 | 0.99039 | -0.18303 | 0.0009307 | 0.00023326
124 | 0.99035 | -0.1839 | 0.0012426 | 0.00031143
125 | 0.99032 | -0.18433 | 0.0013616 | 0.00034124
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0024061 | 0.00059604 | -0.0024057 | -0.00059684 | 4.2558e-07 | -8.0451e-07 | 0.0036472 | 0.0036475 | 0.0036475 | 0.98101 | -0.36635 | 0.98082 | -0.37009 | 1.0021
1 | 0.0045089 | 0.0011201 | -0.0045063 | -0.0011203 | 2.6133e-06 | -2.0914e-07 | 0.0068356 | 0.0068363 | 0.0068363 | 0.98101 | -0.36635 | 0.98039 | -0.3786 | 1.8781
2 | -0.0074468 | -0.0018495 | 0.0074551 | 0.0018526 | 8.2662e-06 | 3.1039e-06 | 0.01129 | 0.011289 | 0.01129 | 0.98101 | -0.36635 | 0.9822 | -0.3429 | 3.1015
3 | 0.00056004 | 0.00013973 | -0.00056002 | -0.00014036 | 1.367e-08 | -6.2872e-07 | 0.00084942 | 0.00084965 | 0.00084965 | 0.98082 | -0.37009 | 0.98079 | -0.3706 | 0.23342
4 | 0.0018456 | 0.00045712 | -0.0018454 | -0.00045813 | 2.7767e-07 | -1.0155e-06 | 0.0027981 | 0.0027985 | 0.0027985 | 0.98082 | -0.37009 | 0.98066 | -0.37328 | 0.76883
5 | 0.003606 | 0.00089471 | -0.0036048 | -0.00089528 | 1.1959e-06 | -5.7804e-07 | 0.0054699 | 0.0054704 | 0.0054704 | 0.98039 | -0.3786 | 0.98003 | -0.38561 | 1.5029
6 | -0.0074551 | -0.0018526 | 0.0074561 | 0.0018529 | 9.7122e-07 | 3.6432e-07 | 0.011289 | 0.011289 | 0.011289 | 0.9822 | -0.3429 | 0.98234 | -0.34015 | 3.1013
7 | 0.00018251 | 4.4725e-05 | -0.00018251 | -4.5101e-05 | 8.5656e-10 | -3.7601e-07 | 0.00027658 | 0.00027671 | 0.00027671 | 0.98066 | -0.37328 | 0.98065 | -0.37338 | 0.076019
8 | 0.0016629 | 0.00041341 | -0.0016626 | -0.00041478 | 2.9539e-07 | -1.3728e-06 | 0.002522 | 0.0025225 | 0.0025225 | 0.98066 | -0.37328 | 0.98047 | -0.37702 | 0.693
9 | 0.0024397 | 0.00060326 | -0.0024391 | -0.00060433 | 5.9103e-07 | -1.0708e-06 | 0.0037013 | 0.0037018 | 0.0037018 | 0.98003 | -0.38561 | 0.97977 | -0.39074 | 1.017
10 | -0.0079155 | -0.0019681 | 0.0079185 | 0.0019693 | 2.9817e-06 | 1.2071e-06 | 0.011985 | 0.011984 | 0.011985 | 0.98234 | -0.34015 | 0.98274 | -0.3322 | 3.2925
11 | -0.0079185 | -0.0019693 | 0.0079188 | 0.0019694 | 3.2979e-07 | 1.3348e-07 | 0.011984 | 0.011984 | 0.011984 | 0.98274 | -0.3322 | 0.98279 | -0.33132 | 3.2924
12 | 0.00018251 | 4.5101e-05 | -0.00018251 | -4.5741e-05 | 1.4601e-09 | -6.4011e-07 | 0.00027671 | 0.00027694 | 0.00027694 | 0.98065 | -0.37338 | 0.98064 | -0.37354 | 0.076082
13 | 0.00093401 | 0.00023219 | -0.00093399 | -0.00023262 | 2.6821e-08 | -4.3212e-07 | 0.0014168 | 0.001417 | 0.001417 | 0.98047 | -0.37702 | 0.98044 | -0.37763 | 0.38928
14 | 0.00048851 | 0.00012098 | -0.00048851 | -0.0001212 | 3.6858e-09 | -2.2342e-07 | 0.0007409 | 0.00074098 | 0.00074098 | 0.98044 | -0.37763 | 0.98043 | -0.37779 | 0.20356
15 | -0.0095085 | -0.0023678 | 0.0095249 | 0.0023757 | 1.6441e-05 | 7.8344e-06 | 0.014391 | 0.01439 | 0.014391 | 0.98279 | -0.33132 | 0.98464 | -0.2949 | 3.9536
16 | 0.00021724 | 5.3213e-05 | -0.00021724 | -5.4445e-05 | 3.9838e-09 | -1.2314e-06 | 0.00032928 | 0.00032971 | 0.00032971 | 0.98043 | -0.37779 | 0.98041 | -0.37818 | 0.09058
17 | -0.028042 | -0.0070519 | 0.02807 | 0.0070692 | 2.7855e-05 | 1.7301e-05 | 0.042387 | 0.042387 | 0.042387 | 0.98464 | -0.2949 | 0.98571 | -0.27413 | 11.6448
18 | 0.018224 | 0.0046027 | -0.018176 | -0.0045739 | 4.84e-05 | 2.882e-05 | 0.027553 | 0.027554 | 0.027554 | 0.98464 | -0.2949 | 0.98179 | -0.35047 | 7.5699
19 | -0.028963 | -0.0072931 | 0.029093 | 0.0073737 | 0.00012968 | 8.0677e-05 | 0.043735 | 0.043734 | 0.043735 | 0.98571 | -0.27413 | 0.99053 | -0.18093 | 12.0151
20 | 0.017935 | 0.0045136 | -0.017906 | -0.0044964 | 2.893e-05 | 1.7198e-05 | 0.02719 | 0.02719 | 0.02719 | 0.98179 | -0.35047 | 0.98006 | -0.38428 | 7.4698
21 | 0.0015297 | 0.00037643 | -0.0015296 | -0.00037677 | 6.107e-08 | -3.4168e-07 | 0.0023208 | 0.0023209 | 0.0023209 | 0.97977 | -0.39074 | 0.97973 | -0.39159 | 0.63761
22 | -0.00111 | -0.00027784 | 0.00111 | 0.00027767 | 1.5673e-08 | -1.7321e-07 | 0.0016903 | 0.0016902 | 0.0016903 | 0.97708 | -0.44274 | 0.97709 | -0.44244 | 0.46436
23 | 0.0004637 | 0.00011587 | -0.00046369 | -0.00011621 | 5.0822e-09 | -3.3718e-07 | 0.00070605 | 0.00070617 | 0.00070617 | 0.97708 | -0.44274 | 0.97707 | -0.44297 | 0.194
24 | -0.010271 | -0.0025741 | 0.010274 | 0.0025756 | 2.8396e-06 | 1.4295e-06 | 0.015641 | 0.015641 | 0.015641 | 0.97709 | -0.44244 | 0.97739 | -0.43664 | 4.2971
25 | 0.0091608 | 0.0022965 | -0.009157 | -0.0022947 | 3.8647e-06 | 1.8105e-06 | 0.013951 | 0.013951 | 0.013951 | 0.97709 | -0.44244 | 0.97664 | -0.4513 | 3.8328
26 | -0.01055 | -0.0026449 | 0.010552 | 0.0026458 | 1.6536e-06 | 8.4408e-07 | 0.016062 | 0.016062 | 0.016062 | 0.97739 | -0.43664 | 0.97756 | -0.43335 | 4.4128
27 | 0.0082135 | 0.0020582 | -0.0082099 | -0.0020567 | 3.5401e-06 | 1.5117e-06 | 0.012514 | 0.012514 | 0.012514 | 0.97664 | -0.4513 | 0.97618 | -0.46035 | 3.438
28 | 0.00346 | 0.00086636 | -0.003459 | -0.00086691 | 9.8777e-07 | -5.5799e-07 | 0.0052665 | 0.0052669 | 0.0052669 | 0.97756 | -0.43335 | 0.97725 | -0.43935 | 1.447
29 | -0.014012 | -0.0035121 | 0.014026 | 0.0035202 | 1.4266e-05 | 8.0808e-06 | 0.021329 | 0.021329 | 0.021329 | 0.97756 | -0.43335 | 0.97864 | -0.412 | 5.8596
30 | 0.0012368 | 0.0003085 | -0.0012367 | -0.00030885 | 3.9626e-08 | -3.4652e-07 | 0.0018847 | 0.0018848 | 0.0018848 | 0.97618 | -0.46035 | 0.97615 | -0.46102 | 0.51781
31 | 0.0069732 | 0.0017482 | -0.0069647 | -0.0017453 | 8.4396e-06 | 2.9146e-06 | 0.01063 | 0.01063 | 0.01063 | 0.97618 | -0.46035 | 0.97489 | -0.48577 | 2.9205
32 | 0.0017028 | 0.00042557 | -0.0017027 | -0.00042598 | 9.4269e-08 | -4.1095e-07 | 0.0025887 | 0.0025889 | 0.0025889 | 0.97864 | -0.412 | 0.97858 | -0.41316 | 0.71122
33 | -0.015729 | -0.0039458 | 0.01575 | 0.0039579 | 2.0813e-05 | 1.2099e-05 | 0.023917 | 0.023917 | 0.023917 | 0.97864 | -0.412 | 0.98006 | -0.38428 | 6.5707
34 | 0.0012367 | 0.00030885 | -0.0012366 | -0.00030992 | 1.2294e-07 | -1.0746e-06 | 0.0018848 | 0.0018852 | 0.0018852 | 0.97615 | -0.46102 | 0.97604 | -0.46311 | 0.51792
35 | 0.0069647 | 0.0017453 | -0.006964 | -0.001745 | 7.6436e-07 | 2.6432e-07 | 0.01063 | 0.010631 | 0.010631 | 0.97489 | -0.48577 | 0.97478 | -0.48807 | 2.9205
36 | 0.00096526 | 0.00024116 | -0.00096521 | -0.00024191 | 5.0148e-08 | -7.4786e-07 | 0.0014675 | 0.0014678 | 0.0014678 | 0.97858 | -0.41316 | 0.97853 | -0.41426 | 0.40323
37 | 0.0021564 | 0.00053858 | -0.0021564 | -0.00053866 | 3.2323e-08 | -8.0676e-08 | 0.0032734 | 0.0032735 | 0.0032735 | 0.98006 | -0.38428 | 0.98004 | -0.3846 | 0.89931
38 | -0.0064541 | -0.0016172 | 0.0064547 | 0.0016174 | 6.0693e-07 | 1.8064e-07 | 0.0098532 | 0.0098532 | 0.0098532 | 0.97468 | -0.49005 | 0.97478 | -0.48807 | 2.7069
39 | 0.0059484 | 0.0014905 | -0.0059474 | -0.0014902 | 1.0308e-06 | 2.4437e-07 | 0.0090812 | 0.0090814 | 0.0090814 | 0.97468 | -0.49005 | 0.97449 | -0.49368 | 2.4949
40 | 0.0059474 | 0.0014902 | -0.0059471 | -0.0014902 | 3.0023e-07 | 7.121e-08 | 0.0090814 | 0.0090814 | 0.0090814 | 0.97449 | -0.49368 | 0.97444 | -0.49474 | 2.4949
41 | 0.0016056 | 0.00040213 | -0.0016056 | -0.00040221 | 1.4902e-08 | -7.2792e-08 | 0.0024519 | 0.0024519 | 0.0024519 | 0.97437 | -0.49615 | 0.97436 | -0.49635 | 0.6736
42 | -0.0049207 | -0.001233 | 0.004921 | 0.001233 | 3.3044e-07 | 1.7105e-08 | 0.0075146 | 0.0075145 | 0.0075146 | 0.97437 | -0.49615 | 0.97444 | -0.49474 | 2.0644
43 | 0.0011292 | 0.00028283 | -0.0011292 | -0.000283 | 1.7023e-08 | -1.7922e-07 | 0.0017244 | 0.0017245 | 0.0017245 | 0.97436 | -0.49635 | 0.97434 | -0.49667 | 0.47377
44 | -0.0017524 | -0.0004386 | 0.0017524 | 0.00043855 | 1.1581e-08 | -4.7517e-08 | 0.0026611 | 0.002661 | 0.0026611 | 0.97983 | -0.38879 | 0.97983 | -0.38865 | 0.73106
45 | 0.0017524 | 0.0004386 | -0.0017523 | -0.00043909 | 1.1862e-07 | -4.8661e-07 | 0.0026611 | 0.0026613 | 0.0026613 | 0.97983 | -0.38879 | 0.97975 | -0.39021 | 0.73112
46 | -0.002156 | -0.0005397 | 0.0021564 | 0.00053866 | 4.1558e-07 | -1.0367e-06 | 0.0032739 | 0.0032735 | 0.0032739 | 0.97983 | -0.38865 | 0.98004 | -0.3846 | 0.89944
47 | 0.0014889 | 0.00037309 | -0.0014889 | -0.00037316 | 1.2425e-08 | -7.3643e-08 | 0.0022613 | 0.0022613 | 0.0022613 | 0.97975 | -0.39021 | 0.97975 | -0.39039 | 0.62125
48 | 0.000619 | 0.00014854 | -0.00061899 | -0.0001492 | 1.7603e-08 | -6.6065e-07 | 0.00093783 | 0.00093806 | 0.00093806 | 0.97973 | -0.39159 | 0.9797 | -0.39221 | 0.25771
49 | 0.00038195 | 8.9795e-05 | -0.00038195 | -9.02e-05 | 4.054e-09 | -4.0468e-07 | 0.00057807 | 0.0005782 | 0.0005782 | 0.9797 | -0.39221 | 0.97969 | -0.39244 | 0.15885
50 | 0.00038195 | 9.02e-05 | -0.00038195 | -9.0223e-05 | 2.3436e-10 | -2.339e-08 | 0.0005782 | 0.00057821 | 0.00057821 | 0.97969 | -0.39244 | 0.97969 | -0.39245 | 0.15885
51 | 0.0029936 | 0.00074782 | -0.0029923 | -0.0007492 | 1.3054e-06 | -1.3795e-06 | 0.0044962 | 0.004497 | 0.004497 | 0.99053 | -0.18093 | 0.99006 | -0.1901 | 1.2354
52 | -0.033203 | -0.0084014 | 0.033252 | 0.0084318 | 4.8571e-05 | 3.0415e-05 | 0.049908 | 0.049908 | 0.049908 | 0.99053 | -0.18093 | 0.99211 | -0.15049 | 13.7109
53 | 0.0029923 | 0.0007492 | -0.0029922 | -0.00074932 | 1.058e-07 | -1.1169e-07 | 0.004497 | 0.0044971 | 0.0044971 | 0.99006 | -0.1901 | 0.99002 | -0.19084 | 1.2355
54 | -0.03627 | -0.0091883 | 0.036289 | 0.0091998 | 1.8193e-05 | 1.1432e-05 | 0.054435 | 0.054435 | 0.054435 | 0.99211 | -0.15049 | 0.99265 | -0.14005 | 14.9547
55 | 0.0022599 | 0.0005658 | -0.0022599 | -0.00056584 | 1.4313e-08 | -3.3382e-08 | 0.0033965 | 0.0033965 | 0.0033965 | 0.99002 | -0.19084 | 0.99001 | -0.19097 | 0.93311
56 | 0.0014891 | 0.00037266 | -0.001489 | -0.00037319 | 8.5973e-08 | -5.3345e-07 | 0.002238 | 0.0022382 | 0.0022382 | 0.99001 | -0.19097 | 0.98995 | -0.19218 | 0.6149
57 | 0.00020269 | 4.5298e-05 | -0.00020268 | -5.0378e-05 | 1.4269e-08 | -5.0797e-06 | 0.000306 | 0.00030772 | 0.00030772 | 0.97969 | -0.39245 | 0.97961 | -0.394 | 0.084538
58 | 0.00020268 | 5.0378e-05 | -0.00020268 | -5.0796e-05 | 1.1833e-09 | -4.1859e-07 | 0.00030772 | 0.00030787 | 0.00030787 | 0.97961 | -0.394 | 0.97961 | -0.39412 | 0.084579
59 | -0.0029206 | -0.00073198 | 0.0029213 | 0.00073116 | 7.07e-07 | -8.1815e-07 | 0.0043793 | 0.0043788 | 0.0043793 | 0.99239 | -0.14514 | 0.99265 | -0.14005 | 1.2031
60 | -0.03921 | -0.0099309 | 0.039269 | 0.0099679 | 5.8601e-05 | 3.692e-05 | 0.058814 | 0.058813 | 0.058814 | 0.99265 | -0.14005 | 0.99427 | -0.10899 | 16.1576
61 | 0.0015412 | 0.00038593 | -0.0015412 | -0.00038625 | 5.4461e-08 | -3.1919e-07 | 0.0023064 | 0.0023066 | 0.0023066 | 0.99427 | -0.10899 | 0.99424 | -0.10973 | 0.63367
62 | -0.04081 | -0.010354 | 0.041025 | 0.010489 | 0.0002151 | 0.00013566 | 0.06112 | 0.061119 | 0.06112 | 0.99427 | -0.10899 | 1 | 0 | 16.7912
63 | 0.1389 | 0.035675 | -0.13845 | -0.035391 | 0.00044961 | 0.00028446 | 0.20699 | 0.20699 | 0.20699 | 1 | 0 | 0.99646 | -0.066899 | 18.9548
64 | -0.13682 | -0.034854 | 0.13693 | 0.03492 | 0.00010355 | 6.5505e-05 | 0.20507 | 0.20507 | 0.20507 | 0.99379 | -0.11792 | 0.99461 | -0.10225 | 18.7791
65 | 0.13682 | 0.034854 | -0.13676 | -0.034814 | 6.306e-05 | 3.9892e-05 | 0.20507 | 0.20507 | 0.20507 | 0.99379 | -0.11792 | 0.99329 | -0.12748 | 18.7791
66 | -0.13744 | -0.035048 | 0.13767 | 0.035197 | 0.00023501 | 0.00014868 | 0.20583 | 0.20583 | 0.20583 | 0.99461 | -0.10225 | 0.99646 | -0.066899 | 18.8491
67 | 0.13457 | 0.034266 | -0.13451 | -0.034228 | 5.8641e-05 | 3.7083e-05 | 0.20179 | 0.20179 | 0.20179 | 0.99329 | -0.12748 | 0.99281 | -0.13652 | 18.4786
68 | 0.13217 | 0.033642 | -0.1321 | -0.033595 | 7.4133e-05 | 4.686e-05 | 0.19828 | 0.19828 | 0.19828 | 0.99281 | -0.13652 | 0.9922 | -0.14816 | 18.1575
69 | 0.13066 | 0.033236 | -0.13062 | -0.033211 | 3.8857e-05 | 2.4556e-05 | 0.19613 | 0.19613 | 0.19613 | 0.9922 | -0.14816 | 0.99188 | -0.15434 | 17.9606
70 | -0.00090967 | -0.00022799 | 0.00090968 | 0.00022785 | 7.7835e-09 | -1.3126e-07 | 0.0013834 | 0.0013833 | 0.0013834 | 0.97849 | -0.41387 | 0.9785 | -0.41369 | 0.38005
71 | -0.0016243 | -0.00040697 | 0.0016245 | 0.00040641 | 1.1406e-07 | -5.5327e-07 | 0.0024701 | 0.0024699 | 0.0024701 | 0.9785 | -0.41369 | 0.97857 | -0.41221 | 0.6786
72 | -0.0032607 | -0.0008165 | 0.0032612 | 0.00081611 | 5.3181e-07 | -3.8459e-07 | 0.004958 | 0.0049577 | 0.004958 | 0.97857 | -0.41221 | 0.97875 | -0.40878 | 1.3621
73 | -0.0050593 | -0.0012667 | 0.0050598 | 0.0012668 | 4.9495e-07 | 3.6334e-08 | 0.0076913 | 0.0076912 | 0.0076913 | 0.97875 | -0.40878 | 0.97885 | -0.40673 | 2.113
74 | -0.007559 | -0.0018931 | 0.0075595 | 0.0018934 | 5.5997e-07 | 2.162e-07 | 0.01149 | 0.01149 | 0.01149 | 0.97885 | -0.40673 | 0.97893 | -0.40517 | 3.1567
75 | -0.010972 | -0.0027486 | 0.010973 | 0.0027491 | 1.0145e-06 | 5.2699e-07 | 0.016677 | 0.016677 | 0.016677 | 0.97893 | -0.40517 | 0.97903 | -0.40323 | 4.5817
76 | -0.012722 | -0.0031876 | 0.012726 | 0.0031894 | 3.3059e-06 | 1.8192e-06 | 0.019336 | 0.019336 | 0.019336 | 0.97903 | -0.40323 | 0.97931 | -0.39778 | 5.3122
77 | -0.013935 | -0.0034925 | 0.013938 | 0.0034941 | 2.707e-06 | 1.5299e-06 | 0.021174 | 0.021174 | 0.021174 | 0.97931 | -0.39778 | 0.97951 | -0.3937 | 5.8171
78 | -0.04773 | -0.012039 | 0.047763 | 0.01206 | 3.3205e-05 | 2.1039e-05 | 0.072535 | 0.072535 | 0.072535 | 0.97951 | -0.3937 | 0.98026 | -0.37918 | 19.9273
79 | 0.033792 | 0.0085448 | -0.033691 | -0.0084818 | 0.00010051 | 6.3052e-05 | 0.051361 | 0.051362 | 0.051362 | 0.97951 | -0.3937 | 0.97633 | -0.45591 | 14.1104
80 | -0.050331 | -0.012704 | 0.050382 | 0.012736 | 5.0893e-05 | 3.2278e-05 | 0.076434 | 0.076434 | 0.076434 | 0.98026 | -0.37918 | 0.98134 | -0.35809 | 20.9983
81 | 0.0029515 | 0.0007394 | -0.0029512 | -0.00073964 | 2.4498e-07 | -2.4694e-07 | 0.0044982 | 0.0044983 | 0.0044983 | 0.97633 | -0.45591 | 0.97624 | -0.45765 | 1.2358
82 | 0.03074 | 0.0077424 | -0.030701 | -0.0077182 | 3.8704e-05 | 2.4184e-05 | 0.046864 | 0.046864 | 0.046864 | 0.97633 | -0.45591 | 0.97499 | -0.48227 | 12.8747
83 | -0.056052 | -0.014157 | 0.056062 | 0.014164 | 1.0403e-05 | 6.6094e-06 | 0.085031 | 0.085031 | 0.085031 | 0.98134 | -0.35809 | 0.98154 | -0.35422 | 23.3602
84 | 0.026137 | 0.0065744 | -0.026103 | -0.006553 | 3.4617e-05 | 2.1433e-05 | 0.039899 | 0.039899 | 0.039899 | 0.97499 | -0.48227 | 0.97358 | -0.51004 | 10.9613
85 | -0.0015111 | -0.00037871 | 0.0015111 | 0.00037851 | 3.5683e-08 | -1.9679e-07 | 0.0023153 | 0.0023153 | 0.0023153 | 0.97113 | -0.55857 | 0.97115 | -0.55808 | 0.63608
86 | 0.0013464 | 0.00033731 | -0.0013464 | -0.00033744 | 1.863e-08 | -1.3251e-07 | 0.002063 | 0.002063 | 0.002063 | 0.97115 | -0.55808 | 0.97114 | -0.55837 | 0.56676
87 | -0.0028575 | -0.00071582 | 0.0028577 | 0.00071564 | 1.663e-07 | -1.7985e-07 | 0.0043782 | 0.0043781 | 0.0043782 | 0.97115 | -0.55808 | 0.97121 | -0.55685 | 1.2028
88 | 0.0036226 | 0.00090702 | -0.0036221 | -0.00090723 | 4.8782e-07 | -2.1032e-07 | 0.00555 | 0.0055502 | 0.0055502 | 0.97121 | -0.55685 | 0.97107 | -0.55968 | 1.5248
89 | -0.0064803 | -0.0016227 | 0.0064808 | 0.0016228 | 4.5846e-07 | 1.3991e-07 | 0.0099281 | 0.009928 | 0.0099281 | 0.97121 | -0.55685 | 0.97129 | -0.55537 | 2.7275
90 | 0.0020835 | 0.00052167 | -0.0020835 | -0.0005219 | 8.7468e-08 | -2.2711e-07 | 0.0031925 | 0.0031926 | 0.0031926 | 0.97107 | -0.55968 | 0.97103 | -0.56056 | 0.8771
91 | 0.0015386 | 0.00038556 | -0.0015386 | -0.0003856 | 8.3198e-09 | -4.4054e-08 | 0.0023576 | 0.0023576 | 0.0023576 | 0.97107 | -0.55968 | 0.97106 | -0.55979 | 0.6477
92 | -0.0082284 | -0.0020608 | 0.0082324 | 0.0020625 | 3.9743e-06 | 1.7176e-06 | 0.012605 | 0.012605 | 0.012605 | 0.97129 | -0.55537 | 0.9718 | -0.54523 | 3.463
93 | 0.0020835 | 0.0005219 | -0.0020834 | -0.00052214 | 9.4266e-08 | -2.4471e-07 | 0.0031926 | 0.0031927 | 0.0031927 | 0.97103 | -0.56056 | 0.97098 | -0.56151 | 0.87713
94 | -0.018621 | -0.0046663 | 0.018629 | 0.0046705 | 7.1213e-06 | 4.2681e-06 | 0.028513 | 0.028513 | 0.028513 | 0.9718 | -0.54523 | 0.97221 | -0.5372 | 7.8332
95 | -0.01934 | -0.0048488 | 0.019343 | 0.004851 | 3.7023e-06 | 2.2297e-06 | 0.029601 | 0.029601 | 0.029601 | 0.97221 | -0.5372 | 0.97241 | -0.53318 | 8.1322
96 | -0.021921 | -0.0054963 | 0.021936 | 0.0055057 | 1.5422e-05 | 9.4166e-06 | 0.033545 | 0.033545 | 0.033545 | 0.97241 | -0.53318 | 0.97316 | -0.51843 | 9.2157
97 | 0.0025776 | 0.00064533 | -0.0025774 | -0.00064572 | 2.6326e-07 | -3.9125e-07 | 0.0039442 | 0.0039444 | 0.0039444 | 0.97241 | -0.53318 | 0.9723 | -0.53533 | 1.0836
98 | -0.023466 | -0.0058892 | 0.023476 | 0.0058949 | 9.3977e-06 | 5.7726e-06 | 0.035884 | 0.035884 | 0.035884 | 0.97316 | -0.51843 | 0.97358 | -0.51004 | 9.8584
99 | 0.0025774 | 0.00064572 | -0.0025772 | -0.00064592 | 1.3104e-07 | -1.9468e-07 | 0.0039444 | 0.0039445 | 0.0039445 | 0.9723 | -0.53533 | 0.97225 | -0.5364 | 1.0836
100 | 0.002627 | 0.00065808 | -0.0026268 | -0.00065833 | 1.7899e-07 | -2.5362e-07 | 0.0040149 | 0.0040151 | 0.0040151 | 0.97358 | -0.51004 | 0.97351 | -0.51147 | 1.103
101 | -0.066021 | -0.016696 | 0.066028 | 0.0167 | 6.629e-06 | 4.1528e-06 | 0.099969 | 0.099969 | 0.099969 | 0.98325 | -0.32105 | 0.98335 | -0.31896 | 13.732
102 | 0.063257 | 0.016003 | -0.063218 | -0.015979 | 3.8542e-05 | 2.4525e-05 | 0.095784 | 0.095784 | 0.095784 | 0.98325 | -0.32105 | 0.98259 | -0.33376 | 26.3144
103 | -0.071316 | -0.018026 | 0.071373 | 0.018061 | 5.6813e-05 | 3.57e-05 | 0.10797 | 0.10797 | 0.10797 | 0.98335 | -0.31896 | 0.98421 | -0.30236 | 14.8311
104 | 0.058989 | 0.014919 | -0.058931 | -0.014882 | 5.7836e-05 | 3.6771e-05 | 0.08938 | 0.08938 | 0.08938 | 0.98259 | -0.33376 | 0.98154 | -0.35422 | 24.5549
105 | 0.0042293 | 0.0010596 | -0.0042289 | -0.0010597 | 4.2568e-07 | -7.8047e-08 | 0.0064046 | 0.0064047 | 0.0064047 | 0.98259 | -0.33376 | 0.98248 | -0.33587 | 1.7595
106 | -0.076644 | -0.019382 | 0.076654 | 0.019389 | 1.0091e-05 | 6.2292e-06 | 0.11594 | 0.11594 | 0.11594 | 0.98421 | -0.30236 | 0.98435 | -0.29962 | 10.6172
107 | 0.0024801 | 0.00062144 | -0.0024801 | -0.00062156 | 7.1113e-08 | -1.2469e-07 | 0.0037562 | 0.0037563 | 0.0037563 | 0.98248 | -0.33587 | 0.98245 | -0.33648 | 1.0319
108 | -0.081997 | -0.020728 | 0.082043 | 0.020757 | 4.6487e-05 | 2.8829e-05 | 0.12402 | 0.12402 | 0.12402 | 0.98435 | -0.29962 | 0.98496 | -0.2878 | 11.3568
109 | -0.090241 | -0.022811 | 0.090245 | 0.022814 | 4.5758e-06 | 2.8534e-06 | 0.1364 | 0.1364 | 0.1364 | 0.98496 | -0.2878 | 0.98501 | -0.28674 | 12.4908
110 | -0.095439 | -0.024116 | 0.095471 | 0.024136 | 3.2143e-05 | 2.0099e-05 | 0.14425 | 0.14425 | 0.14425 | 0.98501 | -0.28674 | 0.98538 | -0.27972 | 13.2093
111 | -0.10062 | -0.025426 | 0.10066 | 0.02545 | 3.7708e-05 | 2.3634e-05 | 0.15202 | 0.15202 | 0.15202 | 0.98538 | -0.27972 | 0.98578 | -0.27191 | 13.9214
112 | -0.10902 | -0.027546 | 0.1092 | 0.027659 | 0.0001801 | 0.00011323 | 0.16464 | 0.16464 | 0.16464 | 0.98578 | -0.27191 | 0.98756 | -0.23751 | 15.0773
113 | -0.11105 | -0.028122 | 0.11105 | 0.028123 | 2.7307e-06 | 1.7178e-06 | 0.16743 | 0.16743 | 0.16743 | 0.98756 | -0.23751 | 0.98759 | -0.237 | 15.3321
114 | -0.11125 | -0.028175 | 0.11129 | 0.028196 | 3.4582e-05 | 2.1755e-05 | 0.16773 | 0.16773 | 0.16773 | 0.98759 | -0.237 | 0.98792 | -0.23052 | 15.3602
115 | -0.11162 | -0.028279 | 0.11165 | 0.028299 | 3.2153e-05 | 2.0229e-05 | 0.16823 | 0.16823 | 0.16823 | 0.98792 | -0.23052 | 0.98823 | -0.22453 | 15.4054
116 | -0.11433 | -0.02897 | 0.11435 | 0.028982 | 1.8485e-05 | 1.1639e-05 | 0.17226 | 0.17226 | 0.17226 | 0.98823 | -0.22453 | 0.98841 | -0.22117 | 15.7748
117 | -0.11808 | -0.029918 | 0.11813 | 0.029951 | 5.3337e-05 | 3.3617e-05 | 0.17788 | 0.17788 | 0.17788 | 0.98841 | -0.22117 | 0.98889 | -0.21177 | 16.2896
118 | -0.12128 | -0.030739 | 0.12147 | 0.030864 | 0.00019773 | 0.00012472 | 0.18261 | 0.18261 | 0.18261 | 0.98889 | -0.21177 | 0.99065 | -0.1779 | 16.7227
119 | -0.12578 | -0.031943 | 0.12582 | 0.031965 | 3.5694e-05 | 2.2535e-05 | 0.18908 | 0.18908 | 0.18908 | 0.99065 | -0.1779 | 0.99096 | -0.172 | 17.3154
120 | 0.0043093 | 0.0010791 | -0.0043084 | -0.0010793 | 9.2099e-07 | -1.6516e-07 | 0.0064725 | 0.0064728 | 0.0064728 | 0.99065 | -0.1779 | 0.99042 | -0.18239 | 1.7782
121 | -0.12916 | -0.032802 | 0.12927 | 0.032872 | 0.00010992 | 6.9443e-05 | 0.1941 | 0.1941 | 0.1941 | 0.99096 | -0.172 | 0.99188 | -0.15434 | 17.7744
122 | 0.0035351 | 0.00088548 | -0.003535 | -0.00088554 | 1.0876e-07 | -6.2708e-08 | 0.005311 | 0.0053111 | 0.0053111 | 0.99042 | -0.18239 | 0.99039 | -0.18303 | 1.4591
123 | 0.0026043 | 0.00065229 | -0.0026042 | -0.00065246 | 1.0731e-07 | -1.7183e-07 | 0.0039127 | 0.0039128 | 0.0039128 | 0.99039 | -0.18303 | 0.99035 | -0.1839 | 1.075
124 | 0.0013616 | 0.00034103 | -0.0013616 | -0.00034124 | 2.82e-08 | -2.1315e-07 | 0.0020457 | 0.0020458 | 0.0020458 | 0.99035 | -0.1839 | 0.99032 | -0.18433 | 0.56204

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.18157 | 0.046165

## res_load
| p_mw | q_mvar
0 | 0.00053185 | 0.00013329
1 | 0.00090024 | 0.00022562
2 | 0.00056002 | 0.00014036
3 | 0.0011652 | 0.00029202
4 | 0.00045941 | 0.00011514
5 | 0.00072854 | 0.00018259
6 | 0.00018251 | 4.5741e-05
7 | 0.00044548 | 0.00011165
8 | 0.0015897 | 0.00039842
9 | 0.00027126 | 6.7985e-05
10 | 0.00029328 | 7.3503e-05
11 | 0.00089322 | 0.00022386
12 | 0.00024052 | 6.0281e-05
13 | 0.00090935 | 0.0002279
14 | 0.00064626 | 0.00016197
15 | 0.00046369 | 0.00011621
16 | 0.00027666 | 6.9337e-05
17 | 0.00094347 | 0.00023646
18 | 0.003459 | 0.00086691
19 | 0.00073746 | 0.00018482
20 | 0.0012366 | 0.00030992
21 | 0.0005057 | 0.00012674
22 | 0.00050925 | 0.00012763
23 | 0.0033151 | 0.00083084
24 | 0.00047634 | 0.00011938
25 | 0.0010261 | 0.00025716
26 | 0.0011292 | 0.000283
27 | 0.00040358 | 0.00010115
28 | 0.00026334 | 6.6e-05
29 | 0.00091064 | 0.00022823
30 | 0.00023703 | 5.9406e-05
31 | 0.0011166 | 0.00027984
32 | 0.0030185 | 0.00075652
33 | 0.00096521 | 0.00024191
34 | 0.00073223 | 0.00018351
35 | 0.00077079 | 0.00019318
36 | 0.001489 | 0.00037319
37 | 0.00021724 | 5.4445e-05
38 | 0.00017925 | 4.4925e-05
39 | 0.00020268 | 5.0796e-05
40 | 0.0014889 | 0.00037316
41 | 0.0029206 | 0.00073198
42 | 0.0015412 | 0.00038625
43 | 0.0005115 | 0.00012819
44 | 0.0021903 | 0.00054893
45 | 0.00077364 | 0.00019389
46 | 0.0023397 | 0.00058638
47 | 0.001434 | 0.00035941
48 | 0.00090967 | 0.00022799
49 | 0.00071466 | 0.00017911
50 | 0.0016363 | 0.00041009
51 | 0.001798 | 0.00045063
52 | 0.0024992 | 0.00062636
53 | 0.0034124 | 0.00085523
54 | 0.0017495 | 0.00043848
55 | 0.0012095 | 0.00030312
56 | 0.0025683 | 0.00064367
57 | 0.00567 | 0.001421
58 | 0.0029512 | 0.00073964
59 | 0.0045636 | 0.0011438
60 | 0.0015111 | 0.00037871
61 | 0.0013464 | 0.00033744
62 | 0.0017476 | 0.000438
63 | 0.0015386 | 0.0003856
64 | 0.010389 | 0.0026037
65 | 0.0020834 | 0.00052214
66 | 0.00071113 | 0.00017823
67 | 0.0015299 | 0.00038343
68 | 0.0025772 | 0.00064592
69 | 0.0026268 | 0.00065833
70 | 0.0027648 | 0.00069294
71 | 0.005288 | 0.0013253
72 | 0.005271 | 0.001321
73 | 0.0028686 | 0.00071894
74 | 0.0017487 | 0.00043827
75 | 0.0053429 | 0.0013391
76 | 0.0024801 | 0.00062156
77 | 0.0081973 | 0.0020544
78 | 0.0051936 | 0.0013017
79 | 0.0051498 | 0.0012907
80 | 0.0083624 | 0.0020958
81 | 0.0018466 | 0.00046279
82 | 0.00020366 | 5.1042e-05
83 | 0.00032825 | 8.2266e-05
84 | 0.0026791 | 0.00067145
85 | 0.0037338 | 0.00093578
86 | 0.0031434 | 0.00078781
87 | 0.0033383 | 0.00083666
88 | 0.00077325 | 0.0001938
89 | 0.0013555 | 0.00033972
90 | 0.0009307 | 0.00023326
91 | 0.0012426 | 0.00031143
92 | 0.0013616 | 0.00034124

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1