## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1372-36_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1372-36_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1372-36_0_5_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_1372-36_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1372-36_0_5_node_24 | 0.4 | n |  | TRUE
5 | bus_LV_1372-36_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1372-36_0_5_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_1372-36_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1372-36_0_5_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_1372-36_0_5_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_1372-36_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1372-36_0_5_node_49 | 0.4 | n |  | TRUE
12 | bus_LV_1372-36_0_5_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1372-36_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1372-36_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1372-36_0_5_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1372-36_0_5_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_1372-36_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1372-36_0_5_node_47 | 0.4 | n |  | TRUE
19 | bus_LV_1372-36_0_5_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_1372-36_0_5_node_35 | 0.4 | n |  | TRUE
21 | bus_LV_1372-36_0_5_node_48 | 0.4 | n |  | TRUE
22 | bus_LV_1372-36_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1372-36_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1372-36_0_5_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_1372-36_0_5_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_1372-36_0_5_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1372-36_0_5_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_1372-36_0_5_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1372-36_0_5_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_1372-36_0_5_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1372-36_0_5_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1372-36_0_5_node_45 | 0.4 | n |  | TRUE
33 | bus_LV_1372-36_0_5_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_1372-36_0_5_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_1372-36_0_5_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_1372-36_0_5_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_1372-36_0_5_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_1372-36_0_5_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_1372-36_0_5_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_1372-36_0_5_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1372-36_0_5_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1372-36_0_5_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1372-36_0_5_node_44 | 0.4 | n |  | TRUE
44 | bus_LV_1372-36_0_5_node_42 | 0.4 | n |  | TRUE
45 | bus_MV_22_1_node_166 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1372-36_0_5_load_0 | 0 | 0.036004 | 0.0090236 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1372-36_0_5_load_19 | 6 | 0.035416 | 0.008876 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1372-36_0_5_load_15 | 8 | 0.068572 | 0.017186 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1372-36_0_5_load_21 | 9 | 0.048832 | 0.012238 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1372-36_0_5_load_49 | 11 | 0.013077 | 0.0032775 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1372-36_0_5_load_22 | 15 | 0.029002 | 0.0072687 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1372-36_0_5_load_27 | 16 | 0.030587 | 0.0076658 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1372-36_0_5_load_47 | 18 | 0.0035079 | 0.00087917 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1372-36_0_5_load_46 | 19 | 0.0045483 | 0.0011399 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1372-36_0_5_load_48 | 21 | 0.044141 | 0.011063 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1372-36_0_5_load_40 | 24 | 0.0044711 | 0.0011206 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1372-36_0_5_load_38 | 25 | 0.0042957 | 0.0010766 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1372-36_0_5_load_23 | 27 | 0.0066849 | 0.0016754 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1372-36_0_5_load_17 | 30 | 0.030863 | 0.007735 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1372-36_0_5_load_26 | 31 | 0.007944 | 0.0019909 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1372-36_0_5_load_34 | 34 | 0.024331 | 0.0060979 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1372-36_0_5_load_41 | 35 | 0.013178 | 0.0033028 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1372-36_0_5_load_28 | 36 | 0.0058001 | 0.0014536 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1372-36_0_5_load_29 | 37 | 0.012473 | 0.003126 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1372-36_0_5_load_30 | 38 | 0.0073301 | 0.0018371 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1372-36_0_5_load_33 | 41 | 0.0018357 | 0.00046006 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1372-36_0_5_load_43 | 42 | 0.0059866 | 0.0015004 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1372-36_0_5_load_44 | 43 | 0.0040642 | 0.0010186 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1372-36_0_5_load_42 | 44 | 0.009771 | 0.0024488 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1372-36_0_5_line_0 |  | 0 | 1 | 0.014877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1372-36_0_5_line_1 |  | 1 | 2 | 0.023189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1372-36_0_5_line_2 |  | 2 | 7 | 0.016474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1372-36_0_5_line_3 |  | 2 | 8 | 0.02743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1372-36_0_5_line_4 |  | 3 | 4 | 0.044619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1372-36_0_5_line_5 |  | 3 | 5 | 0.035107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1372-36_0_5_line_6 |  | 4 | 26 | 0.007147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1372-36_0_5_line_7 |  | 4 | 27 | 0.011367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1372-36_0_5_line_8 |  | 5 | 6 | 0.0023378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1372-36_0_5_line_9 |  | 7 | 9 | 0.0087459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1372-36_0_5_line_10 |  | 8 | 28 | 0.00779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1372-36_0_5_line_11 |  | 9 | 15 | 0.033594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1372-36_0_5_line_12 |  | 10 | 11 | 0.030128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1372-36_0_5_line_13 |  | 10 | 12 | 0.051224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1372-36_0_5_line_14 |  | 12 | 20 | 0.048608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1372-36_0_5_line_15 |  | 12 | 21 | 0.031115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1372-36_0_5_line_16 |  | 13 | 14 | 0.14397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1372-36_0_5_line_17 |  | 13 | 15 | 0.0043421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1372-36_0_5_line_18 |  | 14 | 16 | 0.038533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1372-36_0_5_line_19 |  | 16 | 31 | 0.032118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1372-36_0_5_line_20 |  | 17 | 18 | 0.0864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1372-36_0_5_line_21 |  | 17 | 19 | 0.049821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1372-36_0_5_line_22 |  | 19 | 32 | 0.0098184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1372-36_0_5_line_23 |  | 20 | 33 | 0.011938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1372-36_0_5_line_24 |  | 20 | 34 | 0.018664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1372-36_0_5_line_25 |  | 21 | 29 | 0.018168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_1372-36_0_5_line_26 |  | 22 | 23 | 0.029642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1372-36_0_5_line_27 |  | 22 | 24 | 0.012438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1372-36_0_5_line_28 |  | 23 | 25 | 0.015403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1372-36_0_5_line_29 |  | 24 | 35 | 0.021281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1372-36_0_5_line_30 |  | 25 | 33 | 0.029698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1372-36_0_5_line_31 |  | 26 | 29 | 0.060774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1372-36_0_5_line_32 |  | 26 | 30 | 0.0020789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1372-36_0_5_line_33 |  | 28 | 30 | 0.019633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1372-36_0_5_line_34 |  | 31 | 36 | 0.032925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1372-36_0_5_line_35 |  | 32 | 43 | 0.024561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1372-36_0_5_line_36 |  | 32 | 44 | 0.0084841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1372-36_0_5_line_37 |  | 35 | 44 | 0.022531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1372-36_0_5_line_38 |  | 37 | 38 | 0.0064306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1372-36_0_5_line_39 |  | 37 | 39 | 0.0084386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1372-36_0_5_line_40 |  | 38 | 40 | 0.019616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1372-36_0_5_line_41 |  | 39 | 41 | 0.017236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1372-36_0_5_line_42 |  | 40 | 42 | 0.011161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1372-36_0_5_line_43 |  | 42 | 43 | 0.015894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1372-36_0_5_trafo_18 | 0.63 MVA 20/0.4 kV | 45 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2692333.0267 | 1208474.7878 | 2692335.9443 | 1208476.4006 | 2692341.8326 | 1208486.3288
1 | 2692328.3256 | 1208457.7259 | 2692329.4145 | 1208460.0776 | 2692329.5115 | 1208462.6586 | 2692328.6148 | 1208465.0797 | 2692334.96 | 1208470.2368 | 2692336.8108 | 1208472 | 2692333.0267 | 1208474.7878
2 | 2692320.7862 | 1208444.2447 | 2692323.9945 | 1208455.0793 | 2692326.4214 | 1208455.973 | 2692328.3256 | 1208457.7259
3 | 2692328.3256 | 1208457.7259 | 2692331.7734 | 1208452.1088 | 2692349.1154 | 1208440.553
4 | 2692413.2698 | 1208449.6127 | 2692385.3757 | 1208437.5951 | 2692378.9357 | 1208434.6268 | 2692375.3515 | 1208428.4338
5 | 2692413.2698 | 1208449.6127 | 2692417.2019 | 1208456.4226 | 2692407.8576 | 1208461.2923 | 2692397.857 | 1208466.8079 | 2692394.3368 | 1208468.7547 | 2692393.2472 | 1208469.3938
6 | 2692371.7748 | 1208422.241 | 2692375.3515 | 1208428.4338
7 | 2692375.3515 | 1208428.4338 | 2692385.7384 | 1208423.8155
8 | 2692393.2472 | 1208469.3938 | 2692390.9516 | 1208469.8363
9 | 2692320.7862 | 1208444.2447 | 2692326.3951 | 1208441.9521 | 2692324.9695 | 1208439.6751
10 | 2692355.598 | 1208436.2334 | 2692349.1154 | 1208440.553
11 | 2692324.9695 | 1208439.6751 | 2692311.3098 | 1208417.8582 | 2692310.9162 | 1208413.3158 | 2692312.2177 | 1208410.2894
12 | 2692377.1075 | 1208298.841 | 2692368.8773 | 1208302.9497 | 2692370.6013 | 1208306.5232 | 2692358.8871 | 1208311.7121 | 2692354.7723 | 1208310.8034
13 | 2692377.1075 | 1208298.841 | 2692381.4181 | 1208307.7247 | 2692399.4636 | 1208344.9289
14 | 2692399.4636 | 1208344.9289 | 2692402.481 | 1208343.5414 | 2692420.5162 | 1208335.2595 | 2692442.9582 | 1208323.2768
15 | 2692399.4636 | 1208344.9289 | 2692371.3552 | 1208358.2721
16 | 2692269.9132 | 1208300.0171 | 2692274.765 | 1208304.4062 | 2692279.5216 | 1208312.9854 | 2692286.7857 | 1208326.0954 | 2692294.5531 | 1208340.0915 | 2692268.6415 | 1208360.1154 | 2692274.0039 | 1208366.8806 | 2692277.3517 | 1208371.1686 | 2692278.6246 | 1208372.9339 | 2692278.9779 | 1208377.6203 | 2692301.1136 | 1208402.6014 | 2692306.2662 | 1208404.2489 | 2692309.1708 | 1208407.1958
17 | 2692309.1708 | 1208407.1958 | 2692312.2177 | 1208410.2894
18 | 2692269.9132 | 1208300.0171 | 2692281.7971 | 1208298.5999 | 2692299.2821 | 1208290.9874 | 2692303.3031 | 1208284.6624
19 | 2692325.6384 | 1208264.9844 | 2692308.1268 | 1208274.1907 | 2692308.9695 | 1208275.7492 | 2692303.3031 | 1208284.6624
20 | 2692388.6644 | 1208168.7995 | 2692408.5908 | 1208147.9274 | 2692411.598 | 1208147.2068 | 2692419.8145 | 1208152.3374 | 2692448.166 | 1208171.7227 | 2692456.4844 | 1208177.9964
21 | 2692388.6644 | 1208168.7995 | 2692411.7071 | 1208192.6833 | 2692421.8597 | 1208205.8589
22 | 2692427.8526 | 1208213.6362 | 2692421.8597 | 1208205.8589
23 | 2692451.1027 | 1208315.3754 | 2692448.908 | 1208320.1002 | 2692442.9582 | 1208323.2768
24 | 2692442.9582 | 1208323.2768 | 2692435.5532 | 1208306.1445
25 | 2692355.2459 | 1208366.648 | 2692363.331 | 1208362.0812 | 2692371.3552 | 1208358.2721
26 | 2692483.0178 | 1208290.2419 | 2692465.4663 | 1208266.3206
27 | 2692465.4663 | 1208266.3206 | 2692458.239 | 1208256.1975
28 | 2692483.0178 | 1208290.2419 | 2692471.1253 | 1208300.0308
29 | 2692458.239 | 1208256.1975 | 2692445.8738 | 1208238.8779
30 | 2692451.1027 | 1208315.3754 | 2692459.3015 | 1208313.2899 | 2692467.6535 | 1208309.1721 | 2692465.8883 | 1208304.3415 | 2692471.1253 | 1208300.0308
31 | 2692371.7748 | 1208422.241 | 2692375.447 | 1208415.3933 | 2692372.0272 | 1208401.0307 | 2692355.2459 | 1208366.648
32 | 2692371.7748 | 1208422.241 | 2692370.6053 | 1208423.9598
33 | 2692355.598 | 1208436.2334 | 2692368.0167 | 1208427.7643 | 2692370.6053 | 1208423.9598
34 | 2692355.9599 | 1208252.4531 | 2692338.8608 | 1208258.033 | 2692325.6384 | 1208264.9844
35 | 2692427.8526 | 1208213.6362 | 2692411.7572 | 1208223.3157 | 2692407.394 | 1208227.1052
36 | 2692427.8526 | 1208213.6362 | 2692432.7824 | 1208220.5411
37 | 2692445.8738 | 1208238.8779 | 2692432.7824 | 1208220.5411
38 | 2692414.3771 | 1208257.4726 | 2692418.6663 | 1208262.2638
39 | 2692424.2948 | 1208268.5512 | 2692418.6663 | 1208262.2638
40 | 2692400.1573 | 1208247.619 | 2692404.1584 | 1208246.0577 | 2692414.3771 | 1208257.4726
41 | 2692424.2948 | 1208268.5512 | 2692435.6336 | 1208281.213 | 2692435.7417 | 1208281.4267
42 | 2692400.1573 | 1208247.619 | 2692399.3599 | 1208246.0834 | 2692395.3939 | 1208237.5274
43 | 2692395.3939 | 1208237.5274 | 2692407.394 | 1208227.1052

## bus_geodata
| x | y | coords
0 | 2692341.8326 | 1208486.3288
1 | 2692333.0267 | 1208474.7878
2 | 2692328.3256 | 1208457.7258
3 | 2692413.2698 | 1208449.6127
4 | 2692375.3515 | 1208428.4338
5 | 2692393.2472 | 1208469.3938
6 | 2692390.9516 | 1208469.8363
7 | 2692320.7862 | 1208444.2447
8 | 2692349.1154 | 1208440.5531
9 | 2692324.9695 | 1208439.6751
10 | 2692377.1075 | 1208298.841
11 | 2692354.7723 | 1208310.8034
12 | 2692399.4636 | 1208344.9289
13 | 2692309.1708 | 1208407.1958
14 | 2692269.9132 | 1208300.0171
15 | 2692312.2177 | 1208410.2894
16 | 2692303.3031 | 1208284.6624
17 | 2692388.6644 | 1208168.7995
18 | 2692456.4844 | 1208177.9964
19 | 2692421.8597 | 1208205.8589
20 | 2692442.9582 | 1208323.2768
21 | 2692371.3552 | 1208358.2721
22 | 2692465.4663 | 1208266.3206
23 | 2692483.0178 | 1208290.2419
24 | 2692458.239 | 1208256.1975
25 | 2692471.1253 | 1208300.0308
26 | 2692371.7748 | 1208422.241
27 | 2692385.7384 | 1208423.8155
28 | 2692355.598 | 1208436.2334
29 | 2692355.2459 | 1208366.648
30 | 2692370.6053 | 1208423.9598
31 | 2692325.6384 | 1208264.9844
32 | 2692427.8526 | 1208213.6362
33 | 2692451.1027 | 1208315.3754
34 | 2692435.5532 | 1208306.1445
35 | 2692445.8738 | 1208238.8779
36 | 2692355.9599 | 1208252.4531
37 | 2692418.6663 | 1208262.2638
38 | 2692414.3771 | 1208257.4726
39 | 2692424.2948 | 1208268.5512
40 | 2692400.1573 | 1208247.619
41 | 2692435.7417 | 1208281.4267
42 | 2692395.3939 | 1208237.5274
43 | 2692407.394 | 1208227.1052
44 | 2692432.7824 | 1208220.5411
45 | 2692368.5261 | 1208393.8574

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9891 | -0.20905 | 0.036004 | 0.0090236
1 | 0.98959 | -0.19951 | 0 | 0
2 | 0.99036 | -0.18466 | 0 | 0
3 | 0.99271 | -0.13964 | 0 | 0
4 | 0.99415 | -0.11173 | 0 | 0
5 | 0.99157 | -0.16165 | 0 | 0
6 | 0.99149 | -0.16312 | 0.035416 | 0.008876
7 | 0.9885 | -0.22049 | 0 | 0
8 | 0.99236 | -0.14619 | 0.068572 | 0.017186
9 | 0.98752 | -0.23957 | 0.048832 | 0.012238
10 | 0.995 | -0.095436 | 0 | 0
11 | 0.99464 | -0.10237 | 0.013077 | 0.0032775
12 | 0.99561 | -0.083648 | 0 | 0
13 | 0.98506 | -0.28717 | 0 | 0
14 | 0.97913 | -0.40252 | 0 | 0
15 | 0.98524 | -0.28371 | 0.029002 | 0.0072687
16 | 0.97755 | -0.43362 | 0.030587 | 0.0076658
17 | 0.98219 | -0.34273 | 0 | 0
18 | 0.98191 | -0.34821 | 0.0035079 | 0.00087917
19 | 0.98235 | -0.33957 | 0.0045483 | 0.0011399
20 | 0.99132 | -0.16589 | 0 | 0
21 | 0.99873 | -0.02426 | 0.044141 | 0.011063
22 | 0.98577 | -0.27294 | 0 | 0
23 | 0.98761 | -0.23729 | 0 | 0
24 | 0.985 | -0.28793 | 0.0044711 | 0.0011206
25 | 0.98857 | -0.21882 | 0.0042957 | 0.0010766
26 | 0.99443 | -0.10642 | 0 | 0
27 | 0.99408 | -0.11307 | 0.0066849 | 0.0016754
28 | 0.9929 | -0.13577 | 0 | 0
29 | 1 | 0 | -0.45907 | -0.11646
30 | 0.99426 | -0.10957 | 0.030863 | 0.007735
31 | 0.97714 | -0.44168 | 0.007944 | 0.0019909
32 | 0.98243 | -0.33814 | 0 | 0
33 | 0.99053 | -0.18103 | 0 | 0
34 | 0.9909 | -0.17395 | 0.024331 | 0.0060979
35 | 0.98377 | -0.31194 | 0.013178 | 0.0033028
36 | 0.97696 | -0.44517 | 0.0058001 | 0.0014536
37 | 0.9806 | -0.37388 | 0.012473 | 0.003126
38 | 0.98069 | -0.37222 | 0.0073301 | 0.0018371
39 | 0.98059 | -0.37416 | 0 | 0
40 | 0.98108 | -0.36453 | 0 | 0
41 | 0.98056 | -0.37474 | 0.0018357 | 0.00046006
42 | 0.9813 | -0.36015 | 0.0059866 | 0.0015004
43 | 0.98171 | -0.35221 | 0.0040642 | 0.0010186
44 | 0.98274 | -0.33205 | 0.009771 | 0.0024488
45 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.036004 | -0.0090236 | 0.036021 | 0.0090339 | 1.6368e-05 | 1.0284e-05 | 0.054166 | 0.054166 | 0.054166 | 0.9891 | -0.20905 | 0.98959 | -0.19951 | 14.8807
1 | -0.036021 | -0.0090339 | 0.036046 | 0.0090499 | 2.5513e-05 | 1.603e-05 | 0.054166 | 0.054165 | 0.054166 | 0.98959 | -0.19951 | 0.99036 | -0.18466 | 14.8806
2 | 0.12297 | 0.031128 | -0.12276 | -0.030994 | 0.00021114 | 0.00013492 | 0.18487 | 0.18487 | 0.18487 | 0.99036 | -0.18466 | 0.9885 | -0.22049 | 50.7891
3 | -0.15902 | -0.040178 | 0.15931 | 0.040366 | 0.00029387 | 0.00018737 | 0.23904 | 0.23904 | 0.23904 | 0.99036 | -0.18466 | 0.99236 | -0.14619 | 32.8348
4 | -0.035455 | -0.0089009 | 0.035503 | 0.0089306 | 4.7269e-05 | 2.9674e-05 | 0.053151 | 0.053151 | 0.053151 | 0.99271 | -0.13964 | 0.99415 | -0.11173 | 14.602
5 | 0.035455 | 0.0089009 | -0.035418 | -0.0088776 | 3.7192e-05 | 2.335e-05 | 0.053151 | 0.053151 | 0.053151 | 0.99271 | -0.13964 | 0.99157 | -0.16165 | 14.602
6 | -0.042188 | -0.010606 | 0.042199 | 0.010613 | 1.0691e-05 | 6.7493e-06 | 0.063157 | 0.063157 | 0.063157 | 0.99415 | -0.11173 | 0.99443 | -0.10642 | 17.3509
7 | 0.0066853 | 0.0016755 | -0.0066849 | -0.0016754 | 4.2682e-07 | 1.2578e-07 | 0.010006 | 0.010006 | 0.010006 | 0.99415 | -0.11173 | 0.99408 | -0.11307 | 2.749
8 | 0.035418 | 0.0088776 | -0.035416 | -0.008876 | 2.4767e-06 | 1.5549e-06 | 0.053151 | 0.053151 | 0.053151 | 0.99157 | -0.16165 | 0.99149 | -0.16312 | 14.602
9 | 0.12276 | 0.030994 | -0.12265 | -0.030922 | 0.00011209 | 7.1627e-05 | 0.18487 | 0.18487 | 0.18487 | 0.9885 | -0.22049 | 0.98752 | -0.23957 | 50.7891
10 | -0.22788 | -0.057552 | 0.228 | 0.057624 | 0.0001138 | 7.253e-05 | 0.34186 | 0.34186 | 0.34186 | 0.99236 | -0.14619 | 0.9929 | -0.13577 | 31.3058
11 | 0.073815 | 0.018684 | -0.073659 | -0.018584 | 0.00015603 | 9.9433e-05 | 0.11129 | 0.11129 | 0.11129 | 0.98752 | -0.23957 | 0.98524 | -0.28371 | 30.5746
12 | 0.013082 | 0.0032799 | -0.013077 | -0.0032775 | 4.3244e-06 | 2.3765e-06 | 0.019564 | 0.019564 | 0.019564 | 0.995 | -0.095436 | 0.99464 | -0.10237 | 5.3748
13 | -0.013082 | -0.0032799 | 0.013089 | 0.0032839 | 7.3523e-06 | 4.0397e-06 | 0.019564 | 0.019564 | 0.019564 | 0.995 | -0.095436 | 0.99561 | -0.083648 | 5.3748
14 | 0.096769 | 0.024627 | -0.096387 | -0.024383 | 0.00038198 | 0.00024384 | 0.14476 | 0.14476 | 0.14476 | 0.99561 | -0.083648 | 0.99132 | -0.16589 | 39.7697
15 | -0.10986 | -0.027911 | 0.11017 | 0.028112 | 0.00031507 | 0.00020124 | 0.16433 | 0.16433 | 0.16433 | 0.99561 | -0.083648 | 0.99873 | -0.02426 | 45.1443
16 | 0.044649 | 0.011311 | -0.044403 | -0.011155 | 0.00024591 | 0.00015556 | 0.067489 | 0.06749 | 0.06749 | 0.98506 | -0.28717 | 0.97913 | -0.40252 | 18.5412
17 | -0.044649 | -0.011311 | 0.044656 | 0.011315 | 7.4165e-06 | 4.6913e-06 | 0.067489 | 0.067489 | 0.067489 | 0.98506 | -0.28717 | 0.98524 | -0.28371 | 18.541
18 | 0.044403 | 0.011155 | -0.044337 | -0.011114 | 6.5818e-05 | 4.164e-05 | 0.06749 | 0.06749 | 0.06749 | 0.97913 | -0.40252 | 0.97755 | -0.43362 | 18.5412
19 | 0.01375 | 0.0034478 | -0.013745 | -0.0034448 | 5.2767e-06 | 2.9746e-06 | 0.020931 | 0.020931 | 0.020931 | 0.97755 | -0.43362 | 0.97714 | -0.44168 | 5.7503
20 | 0.0035088 | 0.00087866 | -0.0035079 | -0.00087917 | 9.1555e-07 | -5.0724e-07 | 0.0053156 | 0.005316 | 0.005316 | 0.98219 | -0.34273 | 0.98191 | -0.34821 | 1.4604
21 | -0.0035088 | -0.00087866 | 0.0035094 | 0.00087837 | 5.2787e-07 | -2.9281e-07 | 0.0053156 | 0.0053154 | 0.0053156 | 0.98219 | -0.34273 | 0.98235 | -0.33957 | 1.4603
22 | -0.0080577 | -0.0020183 | 0.0080582 | 0.0020185 | 5.4845e-07 | 2.2669e-07 | 0.012205 | 0.012205 | 0.012205 | 0.98235 | -0.33957 | 0.98243 | -0.33814 | 3.353
23 | 0.072046 | 0.018279 | -0.071994 | -0.018246 | 5.2434e-05 | 3.3404e-05 | 0.10822 | 0.10822 | 0.10822 | 0.99132 | -0.16589 | 0.99053 | -0.18103 | 29.732
24 | 0.02434 | 0.0061037 | -0.024331 | -0.0060979 | 9.3436e-06 | 5.7394e-06 | 0.036537 | 0.036537 | 0.036537 | 0.99132 | -0.16589 | 0.9909 | -0.17395 | 10.0377
25 | -0.15431 | -0.039175 | 0.15449 | 0.03929 | 0.00018035 | 0.00011495 | 0.23009 | 0.23009 | 0.23009 | 0.99873 | -0.02426 | 1 | 0 | 31.606
26 | -0.067393 | -0.016975 | 0.067508 | 0.017048 | 0.0001151 | 7.3287e-05 | 0.10176 | 0.10176 | 0.10176 | 0.98577 | -0.27294 | 0.98761 | -0.23729 | 27.9558
27 | 0.067393 | 0.016975 | -0.067345 | -0.016944 | 4.8299e-05 | 3.0753e-05 | 0.10176 | 0.10176 | 0.10176 | 0.98577 | -0.27294 | 0.985 | -0.28793 | 27.9558
28 | -0.067508 | -0.017048 | 0.067568 | 0.017086 | 5.9811e-05 | 3.8082e-05 | 0.10176 | 0.10176 | 0.10176 | 0.98761 | -0.23729 | 0.98857 | -0.21882 | 27.9557
29 | 0.062873 | 0.015823 | -0.062801 | -0.015777 | 7.2029e-05 | 4.5828e-05 | 0.095005 | 0.095005 | 0.095005 | 0.985 | -0.28793 | 0.98377 | -0.31194 | 26.1002
30 | -0.071863 | -0.018163 | 0.071994 | 0.018246 | 0.00013044 | 8.31e-05 | 0.10822 | 0.10822 | 0.10822 | 0.98857 | -0.21882 | 0.99053 | -0.18103 | 29.7321
31 | -0.30138 | -0.07618 | 0.30293 | 0.077167 | 0.0015466 | 0.00098744 | 0.45121 | 0.45121 | 0.45121 | 0.99443 | -0.10642 | 1 | 0 | 41.3192
32 | 0.25918 | 0.065567 | -0.25915 | -0.065542 | 3.9131e-05 | 2.4963e-05 | 0.38805 | 0.38805 | 0.38805 | 0.99443 | -0.10642 | 0.99426 | -0.10957 | 35.5356
33 | -0.228 | -0.057624 | 0.22828 | 0.057807 | 0.00028681 | 0.0001828 | 0.34186 | 0.34186 | 0.34186 | 0.9929 | -0.13577 | 0.99426 | -0.10957 | 31.3058
34 | 0.005801 | 0.0014538 | -0.0058001 | -0.0014536 | 9.6354e-07 | 2.0432e-07 | 0.0088339 | 0.0088341 | 0.0088341 | 0.97714 | -0.44168 | 0.97696 | -0.44517 | 2.4269
35 | 0.031735 | 0.0079699 | -0.031714 | -0.0079566 | 2.1285e-05 | 1.3312e-05 | 0.048072 | 0.048073 | 0.048073 | 0.98243 | -0.33814 | 0.98171 | -0.35221 | 13.2067
36 | -0.039793 | -0.0099884 | 0.039805 | 0.0099957 | 1.156e-05 | 7.2907e-06 | 0.060277 | 0.060277 | 0.060277 | 0.98243 | -0.33814 | 0.98274 | -0.33205 | 16.5597
37 | 0.049623 | 0.012475 | -0.049576 | -0.012445 | 4.7616e-05 | 3.0189e-05 | 0.075072 | 0.075072 | 0.075072 | 0.98377 | -0.31194 | 0.98274 | -0.33205 | 20.6242
38 | -0.014309 | -0.0035858 | 0.01431 | 0.0035864 | 1.1369e-06 | 6.4645e-07 | 0.021713 | 0.021713 | 0.021713 | 0.9806 | -0.37388 | 0.98069 | -0.37222 | 5.965
39 | 0.0018357 | 0.00045979 | -0.0018357 | -0.00045988 | 2.4554e-08 | -9.0739e-08 | 0.0027855 | 0.0027856 | 0.0027856 | 0.9806 | -0.37388 | 0.98059 | -0.37416 | 0.76527
40 | -0.02164 | -0.0054235 | 0.021648 | 0.0054284 | 7.9304e-06 | 4.8279e-06 | 0.032835 | 0.032835 | 0.032835 | 0.98069 | -0.37222 | 0.98108 | -0.36453 | 9.0205
41 | 0.0018357 | 0.00045988 | -0.0018357 | -0.00046006 | 5.0155e-08 | -1.8533e-07 | 0.0027856 | 0.0027857 | 0.0027857 | 0.98059 | -0.37416 | 0.98056 | -0.37474 | 0.76529
42 | -0.021648 | -0.0054284 | 0.021652 | 0.0054311 | 4.5122e-06 | 2.7468e-06 | 0.032835 | 0.032834 | 0.032835 | 0.98108 | -0.36453 | 0.9813 | -0.36015 | 9.0205
43 | -0.027639 | -0.0069315 | 0.027649 | 0.006938 | 1.047e-05 | 6.5e-06 | 0.041912 | 0.041912 | 0.041912 | 0.9813 | -0.36015 | 0.98171 | -0.35221 | 11.5144

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45907 | 0.11646

## res_load
| p_mw | q_mvar
0 | 0.036004 | 0.0090236
1 | 0.035416 | 0.008876
2 | 0.068572 | 0.017186
3 | 0.048832 | 0.012238
4 | 0.013077 | 0.0032775
5 | 0.029002 | 0.0072687
6 | 0.030587 | 0.0076658
7 | 0.0035079 | 0.00087917
8 | 0.0045483 | 0.0011399
9 | 0.044141 | 0.011063
10 | 0.0044711 | 0.0011206
11 | 0.0042957 | 0.0010766
12 | 0.0066849 | 0.0016754
13 | 0.030863 | 0.007735
14 | 0.007944 | 0.0019909
15 | 0.024331 | 0.0060979
16 | 0.013178 | 0.0033028
17 | 0.0058001 | 0.0014536
18 | 0.012473 | 0.003126
19 | 0.0073301 | 0.0018371
20 | 0.0018357 | 0.00046006
21 | 0.0059866 | 0.0015004
22 | 0.0040642 | 0.0010186
23 | 0.009771 | 0.0024488

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1