## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1372-37_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1372-37_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1372-37_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1372-37_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1372-37_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1372-37_0_4_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_1372-37_0_4_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1372-37_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1372-37_0_4_node_50 | 0.4 | n |  | TRUE
9 | bus_LV_1372-37_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1372-37_0_4_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_1372-37_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1372-37_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1372-37_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1372-37_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1372-37_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1372-37_0_4_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1372-37_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1372-37_0_4_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_1372-37_0_4_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_1372-37_0_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_1372-37_0_4_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_1372-37_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1372-37_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1372-37_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1372-37_0_4_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1372-37_0_4_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_1372-37_0_4_node_38 | 0.4 | n |  | TRUE
28 | bus_LV_1372-37_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1372-37_0_4_node_39 | 0.4 | n |  | TRUE
30 | bus_LV_1372-37_0_4_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_1372-37_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_1372-37_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1372-37_0_4_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_1372-37_0_4_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_1372-37_0_4_node_49 | 0.4 | n |  | TRUE
36 | bus_LV_1372-37_0_4_node_51 | 0.4 | n |  | TRUE
37 | bus_LV_1372-37_0_4_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_1372-37_0_4_node_42 | 0.4 | n |  | TRUE
39 | bus_LV_1372-37_0_4_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_1372-37_0_4_node_52 | 0.4 | n |  | TRUE
41 | bus_LV_1372-37_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_1372-37_0_4_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_1372-37_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1372-37_0_4_node_47 | 0.4 | n |  | TRUE
45 | bus_LV_1372-37_0_4_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_1372-37_0_4_node_48 | 0.4 | n |  | TRUE
47 | bus_LV_1372-37_0_4_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_1372-37_0_4_node_40 | 0.4 | n |  | TRUE
49 | bus_MV_22_1_node_121 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1372-37_0_4_load_0 | 0 | 0.015584 | 0.0039058 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1372-37_0_4_load_1 | 1 | 0.0034311 | 0.00085992 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1372-37_0_4_load_2 | 2 | 0.0035561 | 0.00089125 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1372-37_0_4_load_16 | 6 | 0.0052871 | 0.0013251 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1372-37_0_4_load_11 | 7 | 0.016175 | 0.0040538 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1372-37_0_4_load_50 | 8 | 0.010426 | 0.002613 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1372-37_0_4_load_29 | 10 | 0.002684 | 0.00067268 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1372-37_0_4_load_5 | 12 | 0.00052062 | 0.00013048 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1372-37_0_4_load_10 | 17 | 0.0091462 | 0.0022923 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1372-37_0_4_load_17 | 18 | 0.00046548 | 0.00011666 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1372-37_0_4_load_23 | 19 | 0.017365 | 0.004352 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1372-37_0_4_load_13 | 22 | 0.0029626 | 0.00074249 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1372-37_0_4_load_14 | 23 | 0.0096852 | 0.0024273 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1372-37_0_4_load_15 | 24 | 0.0025327 | 0.00063476 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1372-37_0_4_load_27 | 25 | 0.0010133 | 0.00025396 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1372-37_0_4_load_31 | 26 | 0.033443 | 0.0083816 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1372-37_0_4_load_38 | 27 | 0.0048207 | 0.0012082 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1372-37_0_4_load_28 | 28 | 0.0087298 | 0.0021879 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1372-37_0_4_load_39 | 29 | 0.0029913 | 0.00074968 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1372-37_0_4_load_30 | 30 | 0.0034794 | 0.00087202 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1372-37_0_4_load_19 | 31 | 0.0029137 | 0.00073023 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1372-37_0_4_load_36 | 34 | 0.04486 | 0.011243 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1372-37_0_4_load_49 | 35 | 0.006056 | 0.0015178 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1372-37_0_4_load_51 | 36 | 0.049458 | 0.012395 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1372-37_0_4_load_42 | 38 | 0.0012687 | 0.00031797 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1372-37_0_4_load_44 | 39 | 0.0022401 | 0.00056141 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1372-37_0_4_load_52 | 40 | 0.0015292 | 0.00038325 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1372-37_0_4_load_32 | 41 | 0.0041813 | 0.0010479 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1372-37_0_4_load_33 | 42 | 0.0031256 | 0.00078334 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1372-37_0_4_load_45 | 45 | 0.091787 | 0.023004 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1372-37_0_4_load_46 | 47 | 0.024288 | 0.0060871 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1372-37_0_4_load_40 | 48 | 0.0022914 | 0.00057429 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1372-37_0_4_line_0 |  | 0 | 1 | 0.016734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1372-37_0_4_line_1 |  | 0 | 2 | 0.0012344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1372-37_0_4_line_2 |  | 1 | 3 | 0.085727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1372-37_0_4_line_3 |  | 2 | 4 | 0.037003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1372-37_0_4_line_4 |  | 3 | 5 | 0.090329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1372-37_0_4_line_5 |  | 4 | 6 | 0.020796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1372-37_0_4_line_6 |  | 4 | 7 | 0.0053668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1372-37_0_4_line_7 |  | 5 | 8 | 0.066806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1372-37_0_4_line_8 |  | 5 | 9 | 0.16706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1372-37_0_4_line_9 |  | 6 | 10 | 0.0079028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1372-37_0_4_line_10 |  | 7 | 11 | 0.041152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1372-37_0_4_line_11 |  | 8 | 35 | 0.018831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1372-37_0_4_line_12 |  | 9 | 31 | 0.030057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1372-37_0_4_line_13 |  | 10 | 30 | 0.0068045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1372-37_0_4_line_14 |  | 11 | 22 | 0.06936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1372-37_0_4_line_15 |  | 11 | 23 | 0.024855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1372-37_0_4_line_16 |  | 11 | 24 | 0.15582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1372-37_0_4_line_17 |  | 12 | 13 | 0.0079429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1372-37_0_4_line_18 |  | 12 | 14 | 0.032356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1372-37_0_4_line_19 |  | 13 | 15 | 0.067579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1372-37_0_4_line_20 |  | 14 | 16 | 0.017407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1372-37_0_4_line_21 |  | 14 | 17 | 0.062724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1372-37_0_4_line_22 |  | 15 | 18 | 0.051491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1372-37_0_4_line_23 |  | 16 | 19 | 0.012908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1372-37_0_4_line_24 |  | 19 | 20 | 0.005484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1372-37_0_4_line_25 |  | 20 | 21 | 0.022757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1372-37_0_4_line_26 |  | 21 | 26 | 0.062555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1372-37_0_4_line_27 |  | 22 | 25 | 0.012481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1372-37_0_4_line_28 |  | 23 | 26 | 0.017396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1372-37_0_4_line_29 |  | 24 | 27 | 0.0342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1372-37_0_4_line_30 |  | 25 | 28 | 0.04938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1372-37_0_4_line_31 |  | 27 | 29 | 0.015349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1372-37_0_4_line_32 |  | 28 | 37 | 0.14133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1372-37_0_4_line_33 |  | 29 | 48 | 0.015936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1372-37_0_4_line_34 |  | 30 | 40 | 0.022313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1372-37_0_4_line_35 |  | 32 | 33 | 0.044061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1372-37_0_4_line_36 |  | 32 | 34 | 0.0055552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1372-37_0_4_line_37 |  | 33 | 36 | 0.049512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1372-37_0_4_line_38 |  | 35 | 44 | 0.012824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1372-37_0_4_line_39 |  | 36 | 46 | 0.010923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1372-37_0_4_line_40 |  | 37 | 39 | 0.081536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1372-37_0_4_line_41 |  | 37 | 38 | 0.06813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1372-37_0_4_line_42 |  | 41 | 42 | 0.008887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1372-37_0_4_line_43 |  | 42 | 43 | 0.009792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1372-37_0_4_line_44 |  | 43 | 44 | 0.002043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1372-37_0_4_line_45 |  | 44 | 45 | 0.012852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_1372-37_0_4_line_46 |  | 45 | 47 | 0.010917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1372-37_0_4_line_47 |  | 46 | 47 | 0.0016921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1372-37_0_4_trafo_3 | 0.63 MVA 20/0.4 kV | 49 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2692695.0175 | 1208066.6825 | 2692694.5236 | 1208083.4089
1 | 2692695.0175 | 1208066.6825 | 2692695.0539 | 1208065.4486
2 | 2692693.025 | 1208169.1183 | 2692693.3735 | 1208129.5639 | 2692693.4545 | 1208122.8829 | 2692693.5136 | 1208117.6136 | 2692694.5236 | 1208083.4089
3 | 2692696.146 | 1208028.4615 | 2692695.0539 | 1208065.4486
4 | 2692693.025 | 1208169.1183 | 2692692.9836 | 1208172.7645 | 2692693.252 | 1208184.8546 | 2692692.8954 | 1208240.5863 | 2692693.5455 | 1208259.4313
5 | 2692696.146 | 1208028.4615 | 2692716.9238 | 1208029.3365
6 | 2692696.146 | 1208028.4615 | 2692696.3048 | 1208023.097
7 | 2692693.5455 | 1208259.4313 | 2692693.4859 | 1208270.1153 | 2692694.0773 | 1208284.4118 | 2692693.8759 | 1208291.5023 | 2692693.6298 | 1208324.465 | 2692693.496 | 1208326.2158
8 | 2692693.5455 | 1208259.4313 | 2692703.4812 | 1208251.2801 | 2692708.5614 | 1208245.355 | 2692713.7092 | 1208234.1052 | 2692741.0849 | 1208175.3134 | 2692760.4155 | 1208131.7179 | 2692754.6885 | 1208127.3926 | 2692741.5691 | 1208121.6739
9 | 2692716.9238 | 1208029.3365 | 2692718.3205 | 1208029.3954 | 2692724.2184 | 1208026.6518 | 2692724.2184 | 1208026.6518
10 | 2692697.5225 | 1207981.9628 | 2692696.3048 | 1208023.097
11 | 2692693.496 | 1208326.2158 | 2692692.4369 | 1208340.0681 | 2692691.7167 | 1208344.9541
12 | 2692741.5691 | 1208121.6739 | 2692752.2811 | 1208093.5908
13 | 2692724.2184 | 1208026.6518 | 2692729.3896 | 1208022.2292
14 | 2692697.5225 | 1207981.9628 | 2692689.7489 | 1207979.6517 | 2692652.9214 | 1207951.7502 | 2692640.3733 | 1207943.4472
15 | 2692697.5225 | 1207981.9628 | 2692712.6055 | 1207980.2515 | 2692722.0308 | 1207978.0647
16 | 2692697.5225 | 1207981.9628 | 2692697.8729 | 1207970.6718 | 2692698.296 | 1207960.5717 | 2692701.3407 | 1207854.1922 | 2692701.3432 | 1207826.2001
17 | 2692893.0824 | 1207929.1453 | 2692886.5348 | 1207933.6418
18 | 2692856.6739 | 1207945.2007 | 2692874.631 | 1207940.5881 | 2692881.1299 | 1207937.3537 | 2692886.5348 | 1207933.6418
19 | 2692893.0824 | 1207929.1453 | 2692931.1345 | 1207961.3591 | 2692936.3386 | 1207969.4789 | 2692938.1842 | 1207977.4352
20 | 2692856.6739 | 1207945.2007 | 2692839.8062 | 1207949.6858
21 | 2692856.6739 | 1207945.2007 | 2692859.5041 | 1207882.5404
22 | 2692938.1842 | 1207977.4352 | 2692939.4095 | 1207982.7356 | 2692936.306 | 1207997.9308 | 2692931.4879 | 1208010.92 | 2692923.1835 | 1208025.3946
23 | 2692839.8062 | 1207949.6858 | 2692827.2598 | 1207952.7211
24 | 2692821.9296 | 1207954.0107 | 2692827.2598 | 1207952.7211
25 | 2692799.9134 | 1207959.9946 | 2692816.1744 | 1207955.3999 | 2692821.9296 | 1207954.0107
26 | 2692799.9134 | 1207959.9946 | 2692738.9766 | 1207974.133
27 | 2692640.3733 | 1207943.4472 | 2692638.003 | 1207941.8787 | 2692629.8463 | 1207936.7434
28 | 2692738.9766 | 1207974.133 | 2692722.0308 | 1207978.0647
29 | 2692701.3432 | 1207826.2001 | 2692701.3463 | 1207792.0005
30 | 2692586.8177 | 1207912.5316 | 2692604.2678 | 1207921.9531 | 2692627.2115 | 1207935.0845 | 2692629.8463 | 1207936.7434
31 | 2692701.3463 | 1207792.0005 | 2692701.3477 | 1207776.6511
32 | 2692586.8177 | 1207912.5316 | 2692471.6343 | 1207830.636
33 | 2692701.5765 | 1207760.7174 | 2692701.348 | 1207772.9713 | 2692701.3477 | 1207776.6511
34 | 2692744.26 | 1208007.7727 | 2692736.2703 | 1208010.0724 | 2692733.1884 | 1208014.6164 | 2692729.3896 | 1208022.2292
35 | 2692755.265 | 1208313.7931 | 2692733.6741 | 1208283.7041 | 2692726.6101 | 1208283.2163
36 | 2692726.6101 | 1208283.2163 | 2692726.3442 | 1208288.7652
37 | 2692755.265 | 1208313.7931 | 2692721.7299 | 1208350.2183
38 | 2692689.7612 | 1208357.6272 | 2692690.4649 | 1208353.4464 | 2692691.7167 | 1208344.9541
39 | 2692714.9883 | 1208358.753 | 2692717.2891 | 1208355.0418 | 2692721.7299 | 1208350.2183
40 | 2692471.6343 | 1207830.636 | 2692461.8003 | 1207837.5994 | 2692419.22 | 1207838.7853 | 2692408.425 | 1207839.0628 | 2692392.3432 | 1207839.604
41 | 2692471.6343 | 1207830.636 | 2692446.2013 | 1207893.8408
42 | 2692670.7802 | 1208357.3864 | 2692678.303 | 1208358.0718 | 2692679.6231 | 1208358.2575
43 | 2692689.3196 | 1208359.6216 | 2692679.6231 | 1208358.2575
44 | 2692689.7612 | 1208357.6272 | 2692689.3196 | 1208359.6216
45 | 2692689.7612 | 1208357.6272 | 2692702.4704 | 1208359.5352
46 | 2692702.4704 | 1208359.5352 | 2692704.7134 | 1208359.872 | 2692710.6289 | 1208359.3969 | 2692713.3143 | 1208359.0003
47 | 2692714.9883 | 1208358.753 | 2692713.3143 | 1208359.0003

## bus_geodata
| x | y | coords
0 | 2692695.0175 | 1208066.6825
1 | 2692694.5236 | 1208083.4089
2 | 2692695.0539 | 1208065.4486
3 | 2692693.025 | 1208169.1183
4 | 2692696.146 | 1208028.4615
5 | 2692693.5455 | 1208259.4313
6 | 2692716.9238 | 1208029.3365
7 | 2692696.3048 | 1208023.097
8 | 2692693.496 | 1208326.2158
9 | 2692741.5691 | 1208121.6739
10 | 2692724.2184 | 1208026.6518
11 | 2692697.5225 | 1207981.9628
12 | 2692886.5348 | 1207933.6418
13 | 2692893.0824 | 1207929.1453
14 | 2692856.6739 | 1207945.2007
15 | 2692938.1842 | 1207977.4352
16 | 2692839.8062 | 1207949.6858
17 | 2692859.5041 | 1207882.5404
18 | 2692923.1835 | 1208025.3946
19 | 2692827.2598 | 1207952.7211
20 | 2692821.9296 | 1207954.0107
21 | 2692799.9134 | 1207959.9946
22 | 2692640.3733 | 1207943.4472
23 | 2692722.0308 | 1207978.0647
24 | 2692701.3432 | 1207826.2001
25 | 2692629.8463 | 1207936.7434
26 | 2692738.9766 | 1207974.133
27 | 2692701.3463 | 1207792.0005
28 | 2692586.8177 | 1207912.5316
29 | 2692701.3477 | 1207776.6511
30 | 2692729.3896 | 1208022.2292
31 | 2692752.2811 | 1208093.5908
32 | 2692726.6101 | 1208283.2163
33 | 2692755.265 | 1208313.7931
34 | 2692726.3442 | 1208288.7652
35 | 2692691.7167 | 1208344.9541
36 | 2692721.7299 | 1208350.2183
37 | 2692471.6343 | 1207830.636
38 | 2692446.2013 | 1207893.8408
39 | 2692392.3432 | 1207839.604
40 | 2692744.26 | 1208007.7727
41 | 2692670.7802 | 1208357.3864
42 | 2692679.6231 | 1208358.2575
43 | 2692689.3196 | 1208359.6216
44 | 2692689.7612 | 1208357.6272
45 | 2692702.4704 | 1208359.5352
46 | 2692714.9883 | 1208358.753
47 | 2692713.3143 | 1208359.0003
48 | 2692701.5765 | 1207760.7174
49 | 2692692.8954 | 1208240.5863

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99288 | -0.13551 | 0.015584 | 0.0039058
1 | 0.99402 | -0.11367 | 0.0034311 | 0.00085992
2 | 0.99273 | -0.1384 | 0.0035561 | 0.00089125
3 | 1 | 0 | -0.39732 | -0.10201
4 | 0.98833 | -0.22298 | 0 | 0
5 | 0.99004 | -0.18853 | 0 | 0
6 | 0.98809 | -0.22779 | 0.0052871 | 0.0013251
7 | 0.98776 | -0.23406 | 0.016175 | 0.0040538
8 | 0.98277 | -0.32866 | 0.010426 | 0.002613
9 | 0.9896 | -0.1972 | 0 | 0
10 | 0.98803 | -0.22888 | 0.002684 | 0.00067268
11 | 0.98398 | -0.3075 | 0 | 0
12 | 0.97875 | -0.4098 | 0.00052062 | 0.00013048
13 | 0.97874 | -0.40987 | 0 | 0
14 | 0.97877 | -0.40922 | 0 | 0
15 | 0.97871 | -0.41045 | 0 | 0
16 | 0.97894 | -0.40601 | 0 | 0
17 | 0.97824 | -0.41966 | 0.0091462 | 0.0022923
18 | 0.97869 | -0.41088 | 0.00046548 | 0.00011666
19 | 0.97906 | -0.40363 | 0.017365 | 0.004352
20 | 0.9792 | -0.40089 | 0 | 0
21 | 0.97978 | -0.38951 | 0 | 0
22 | 0.98294 | -0.32778 | 0.0029626 | 0.00074249
23 | 0.98235 | -0.33915 | 0.0096852 | 0.0024273
24 | 0.98216 | -0.34302 | 0.0025327 | 0.00063476
25 | 0.98279 | -0.33076 | 0.0010133 | 0.00025396
26 | 0.98137 | -0.35832 | 0.033443 | 0.0083816
27 | 0.98184 | -0.34927 | 0.0048207 | 0.0012082
28 | 0.98223 | -0.34169 | 0.0087298 | 0.0021879
29 | 0.98176 | -0.35073 | 0.0029913 | 0.00074968
30 | 0.988 | -0.22949 | 0.0034794 | 0.00087202
31 | 0.98952 | -0.19876 | 0.0029137 | 0.00073023
32 | 0.97203 | -0.53916 | 0 | 0
33 | 0.97388 | -0.50277 | 0 | 0
34 | 0.9718 | -0.54376 | 0.04486 | 0.011243
35 | 0.98082 | -0.36676 | 0.006056 | 0.0015178
36 | 0.97595 | -0.46203 | 0.049458 | 0.012395
37 | 0.98177 | -0.35067 | 0 | 0
38 | 0.98169 | -0.35223 | 0.0012687 | 0.00031797
39 | 0.9816 | -0.35397 | 0.0022401 | 0.00056141
40 | 0.98797 | -0.2301 | 0.0015292 | 0.00038325
41 | 0.97941 | -0.39433 | 0.0041813 | 0.0010479
42 | 0.97944 | -0.39365 | 0.0031256 | 0.00078334
43 | 0.97951 | -0.39235 | 0 | 0
44 | 0.97952 | -0.39208 | 0 | 0
45 | 0.97826 | -0.41667 | 0.091787 | 0.023004
46 | 0.97691 | -0.4432 | 0 | 0
47 | 0.97706 | -0.44029 | 0.024288 | 0.0060871
48 | 0.98173 | -0.35139 | 0.0022914 | 0.00057429
49 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.14901 | -0.037815 | 0.14917 | 0.037915 | 0.00015672 | 9.9865e-05 | 0.22349 | 0.22349 | 0.22349 | 0.99288 | -0.13551 | 0.99402 | -0.11367 | 30.6993
1 | 0.13343 | 0.033909 | -0.13341 | -0.033898 | 1.854e-05 | 1.185e-05 | 0.20014 | 0.20014 | 0.20014 | 0.99288 | -0.13551 | 0.99273 | -0.1384 | 54.9821
2 | -0.1526 | -0.038775 | 0.15344 | 0.03931 | 0.00084018 | 0.00053548 | 0.22863 | 0.22863 | 0.22863 | 0.99402 | -0.11367 | 1 | 0 | 31.4048
3 | 0.12985 | 0.033006 | -0.12933 | -0.03267 | 0.00052659 | 0.00033654 | 0.1948 | 0.1948 | 0.1948 | 0.99273 | -0.1384 | 0.98833 | -0.22298 | 53.5178
4 | 0.24223 | 0.0627 | -0.24002 | -0.061288 | 0.0022091 | 0.0014115 | 0.36115 | 0.36115 | 0.36115 | 1 | 0 | 0.99004 | -0.18853 | 49.6092
5 | 0.012983 | 0.0032546 | -0.01298 | -0.0032529 | 2.9799e-06 | 1.6407e-06 | 0.019548 | 0.019548 | 0.019548 | 0.98833 | -0.22298 | 0.98809 | -0.22779 | 5.3703
6 | 0.11634 | 0.029415 | -0.11628 | -0.029376 | 6.1816e-05 | 3.9494e-05 | 0.17526 | 0.17526 | 0.17526 | 0.98833 | -0.22298 | 0.98776 | -0.23406 | 48.1476
7 | 0.23711 | 0.060559 | -0.23551 | -0.059541 | 0.0015944 | 0.0010187 | 0.35677 | 0.35677 | 0.35677 | 0.99004 | -0.18853 | 0.98277 | -0.32866 | 49.0075
8 | 0.0029151 | 0.00072861 | -0.0029139 | -0.00072999 | 1.2024e-06 | -1.3778e-06 | 0.0043806 | 0.0043814 | 0.0043814 | 0.99004 | -0.18853 | 0.9896 | -0.1972 | 1.2037
9 | 0.0076932 | 0.0019278 | -0.0076928 | -0.0019277 | 3.9778e-07 | 1.5336e-07 | 0.011586 | 0.011586 | 0.011586 | 0.98809 | -0.22779 | 0.98803 | -0.22888 | 3.1828
10 | 0.10011 | 0.025322 | -0.099756 | -0.025097 | 0.00035136 | 0.00022434 | 0.15089 | 0.15089 | 0.15089 | 0.98776 | -0.23406 | 0.98398 | -0.3075 | 41.4535
11 | 0.22509 | 0.056928 | -0.22468 | -0.056665 | 0.00041055 | 0.00026228 | 0.34099 | 0.34099 | 0.34099 | 0.98277 | -0.32866 | 0.98082 | -0.36676 | 46.8391
12 | 0.0029139 | 0.00072999 | -0.0029137 | -0.00073023 | 2.1638e-07 | -2.4765e-07 | 0.0043814 | 0.0043815 | 0.0043815 | 0.9896 | -0.1972 | 0.98952 | -0.19876 | 1.2037
13 | 0.0050088 | 0.001255 | -0.0050086 | -0.001255 | 1.4519e-07 | 5.7816e-09 | 0.0075433 | 0.0075433 | 0.0075433 | 0.98803 | -0.22888 | 0.988 | -0.22949 | 2.0723
14 | 0.01624 | 0.004075 | -0.016225 | -0.0040658 | 1.5691e-05 | 9.162e-06 | 0.024561 | 0.024561 | 0.024561 | 0.98398 | -0.3075 | 0.98294 | -0.32778 | 6.7477
15 | 0.070855 | 0.017842 | -0.070748 | -0.017774 | 0.00010707 | 6.8212e-05 | 0.10718 | 0.10718 | 0.10718 | 0.98398 | -0.3075 | 0.98235 | -0.33915 | 29.4452
16 | 0.012661 | 0.00318 | -0.01264 | -0.0031683 | 2.1427e-05 | 1.1738e-05 | 0.019149 | 0.01915 | 0.01915 | 0.98398 | -0.3075 | 0.98216 | -0.34302 | 5.2609
17 | 0.0004655 | 0.00011508 | -0.0004655 | -0.00011518 | 1.4895e-09 | -9.8869e-08 | 0.00070715 | 0.00070718 | 0.00070718 | 0.97875 | -0.4098 | 0.97874 | -0.40987 | 0.19428
18 | -0.00098612 | -0.00024556 | 0.00098615 | 0.00024517 | 2.7249e-08 | -3.8921e-07 | 0.0014987 | 0.0014985 | 0.0014987 | 0.97875 | -0.4098 | 0.97877 | -0.40922 | 0.41172
19 | 0.0004655 | 0.00011518 | -0.00046549 | -0.00011602 | 1.2679e-08 | -8.4115e-07 | 0.00070718 | 0.00070749 | 0.00070749 | 0.97874 | -0.40987 | 0.97871 | -0.41045 | 0.19436
20 | -0.010137 | -0.0025396 | 0.010138 | 0.0025403 | 1.5502e-06 | 7.7333e-07 | 0.015411 | 0.015411 | 0.015411 | 0.97877 | -0.40922 | 0.97894 | -0.40601 | 4.2337
21 | 0.0091508 | 0.0022944 | -0.0091462 | -0.0022923 | 4.5526e-06 | 2.1258e-06 | 0.013912 | 0.013912 | 0.013912 | 0.97877 | -0.40922 | 0.97824 | -0.41966 | 3.8221
22 | 0.00046549 | 0.00011602 | -0.00046548 | -0.00011666 | 9.668e-09 | -6.4087e-07 | 0.00070749 | 0.00070772 | 0.00070772 | 0.97871 | -0.41045 | 0.97869 | -0.41088 | 0.19443
23 | -0.010138 | -0.0025403 | 0.01014 | 0.0025409 | 1.1496e-06 | 5.7342e-07 | 0.015411 | 0.015411 | 0.015411 | 0.97894 | -0.40601 | 0.97906 | -0.40363 | 4.2337
24 | -0.027504 | -0.0068929 | 0.027508 | 0.0068951 | 3.5935e-06 | 2.2309e-06 | 0.041802 | 0.041802 | 0.041802 | 0.97906 | -0.40363 | 0.9792 | -0.40089 | 11.4841
25 | -0.027508 | -0.0068951 | 0.027523 | 0.0069044 | 1.4912e-05 | 9.2573e-06 | 0.041802 | 0.041802 | 0.041802 | 0.9792 | -0.40089 | 0.97978 | -0.38951 | 11.4841
26 | -0.027523 | -0.0069044 | 0.027564 | 0.0069298 | 4.0991e-05 | 2.5445e-05 | 0.041802 | 0.041802 | 0.041802 | 0.97978 | -0.38951 | 0.98137 | -0.35832 | 11.4841
27 | 0.013262 | 0.0033233 | -0.01326 | -0.0033223 | 1.8865e-06 | 1.0492e-06 | 0.020077 | 0.020077 | 0.020077 | 0.98294 | -0.32778 | 0.98279 | -0.33076 | 5.5156
28 | 0.061063 | 0.015347 | -0.061007 | -0.015311 | 5.5828e-05 | 3.551e-05 | 0.09251 | 0.09251 | 0.09251 | 0.98235 | -0.33915 | 0.98137 | -0.35832 | 25.4148
29 | 0.010107 | 0.0025335 | -0.010104 | -0.0025321 | 3.0072e-06 | 1.4919e-06 | 0.015313 | 0.015313 | 0.015313 | 0.98216 | -0.34302 | 0.98184 | -0.34927 | 4.2068
30 | 0.012247 | 0.0030683 | -0.012241 | -0.0030649 | 6.3668e-06 | 3.4494e-06 | 0.018542 | 0.018543 | 0.018543 | 0.98279 | -0.33076 | 0.98223 | -0.34169 | 5.0941
31 | 0.0052832 | 0.0013239 | -0.0052828 | -0.0013238 | 3.6901e-07 | 4.2056e-08 | 0.0080068 | 0.0080068 | 0.0080068 | 0.98184 | -0.34927 | 0.98176 | -0.35073 | 2.1997
32 | 0.0035107 | 0.00087694 | -0.0035092 | -0.00087777 | 1.4987e-06 | -8.288e-07 | 0.0053175 | 0.0053181 | 0.0053181 | 0.98223 | -0.34169 | 0.98177 | -0.35067 | 1.461
33 | 0.0022915 | 0.00057413 | -0.0022914 | -0.00057429 | 7.2085e-08 | -1.5537e-07 | 0.0034731 | 0.0034731 | 0.0034731 | 0.98176 | -0.35073 | 0.98173 | -0.35139 | 0.95416
34 | 0.0015292 | 0.00038299 | -0.0015292 | -0.00038325 | 4.4382e-08 | -2.5733e-07 | 0.002303 | 0.0023032 | 0.0023032 | 0.988 | -0.22949 | 0.98797 | -0.2301 | 0.63273
35 | -0.04487 | -0.011249 | 0.044948 | 0.011299 | 7.7958e-05 | 4.9346e-05 | 0.068689 | 0.068689 | 0.068689 | 0.97203 | -0.53916 | 0.97388 | -0.50277 | 18.8707
36 | 0.04487 | 0.011249 | -0.04486 | -0.011243 | 9.829e-06 | 6.2217e-06 | 0.068689 | 0.068689 | 0.068689 | 0.97203 | -0.53916 | 0.9718 | -0.54376 | 18.8707
37 | -0.044948 | -0.011299 | 0.045035 | 0.011354 | 8.7602e-05 | 5.5448e-05 | 0.068689 | 0.068689 | 0.068689 | 0.97388 | -0.50277 | 0.97595 | -0.46203 | 18.8706
38 | 0.21862 | 0.055148 | -0.21836 | -0.054979 | 0.00026471 | 0.00016909 | 0.3318 | 0.3318 | 0.3318 | 0.98082 | -0.36676 | 0.97952 | -0.39208 | 45.5771
39 | -0.094494 | -0.023749 | 0.094579 | 0.023804 | 8.5052e-05 | 5.4297e-05 | 0.1441 | 0.1441 | 0.1441 | 0.97595 | -0.46203 | 0.97691 | -0.4432 | 39.5871
40 | 0.0022404 | 0.00056061 | -0.0022401 | -0.00056141 | 3.5253e-07 | -8.0525e-07 | 0.0033954 | 0.0033957 | 0.0033957 | 0.98177 | -0.35067 | 0.9816 | -0.35397 | 0.93289
41 | 0.0012688 | 0.00031717 | -0.0012687 | -0.00031797 | 9.4468e-08 | -8.01e-07 | 0.0019228 | 0.0019231 | 0.0019231 | 0.98177 | -0.35067 | 0.98169 | -0.35223 | 0.52831
42 | -0.0041813 | -0.0010479 | 0.0041814 | 0.0010479 | 1.3449e-07 | -2.5769e-08 | 0.0063526 | 0.0063526 | 0.0063526 | 0.97941 | -0.39433 | 0.97944 | -0.39365 | 1.7452
43 | -0.007307 | -0.0018312 | 0.0073074 | 0.0018314 | 4.5252e-07 | 1.6637e-07 | 0.011101 | 0.011101 | 0.011101 | 0.97944 | -0.39365 | 0.97951 | -0.39235 | 3.0498
44 | -0.0073074 | -0.0018314 | 0.0073075 | 0.0018314 | 9.4412e-08 | 3.4708e-08 | 0.011101 | 0.011101 | 0.011101 | 0.97951 | -0.39235 | 0.97952 | -0.39208 | 3.0497
45 | 0.21105 | 0.053147 | -0.2108 | -0.052989 | 0.00024783 | 0.00015829 | 0.3207 | 0.3207 | 0.3207 | 0.97952 | -0.39208 | 0.97826 | -0.41667 | 44.0523
46 | 0.11901 | 0.029985 | -0.11888 | -0.029899 | 0.00013425 | 8.5783e-05 | 0.18109 | 0.18109 | 0.18109 | 0.97826 | -0.41667 | 0.97706 | -0.44029 | 49.7489
47 | -0.094579 | -0.023804 | 0.094592 | 0.023812 | 1.3175e-05 | 8.4111e-06 | 0.1441 | 0.1441 | 0.1441 | 0.97691 | -0.4432 | 0.97706 | -0.44029 | 39.587

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39732 | 0.10201

## res_load
| p_mw | q_mvar
0 | 0.015584 | 0.0039058
1 | 0.0034311 | 0.00085992
2 | 0.0035561 | 0.00089125
3 | 0.0052871 | 0.0013251
4 | 0.016175 | 0.0040538
5 | 0.010426 | 0.002613
6 | 0.002684 | 0.00067268
7 | 0.00052062 | 0.00013048
8 | 0.0091462 | 0.0022923
9 | 0.00046548 | 0.00011666
10 | 0.017365 | 0.004352
11 | 0.0029626 | 0.00074249
12 | 0.0096852 | 0.0024273
13 | 0.0025327 | 0.00063476
14 | 0.0010133 | 0.00025396
15 | 0.033443 | 0.0083816
16 | 0.0048207 | 0.0012082
17 | 0.0087298 | 0.0021879
18 | 0.0029913 | 0.00074968
19 | 0.0034794 | 0.00087202
20 | 0.0029137 | 0.00073023
21 | 0.04486 | 0.011243
22 | 0.006056 | 0.0015178
23 | 0.049458 | 0.012395
24 | 0.0012687 | 0.00031797
25 | 0.0022401 | 0.00056141
26 | 0.0015292 | 0.00038325
27 | 0.0041813 | 0.0010479
28 | 0.0031256 | 0.00078334
29 | 0.091787 | 0.023004
30 | 0.024288 | 0.0060871
31 | 0.0022914 | 0.00057429

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1