## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1372-44_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1372-44_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1372-44_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1372-44_0_2_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_1372-44_0_2_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_1372-44_0_2_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1372-44_0_2_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1372-44_0_2_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1372-44_0_2_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1372-44_0_2_node_40 | 0.4 | n |  | TRUE
10 | bus_LV_1372-44_0_2_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1372-44_0_2_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1372-44_0_2_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1372-44_0_2_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1372-44_0_2_node_229 | 0.4 | n |  | TRUE
15 | bus_LV_1372-44_0_2_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1372-44_0_2_node_43 | 0.4 | n |  | TRUE
17 | bus_LV_1372-44_0_2_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1372-44_0_2_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1372-44_0_2_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1372-44_0_2_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1372-44_0_2_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1372-44_0_2_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1372-44_0_2_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1372-44_0_2_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_1372-44_0_2_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_1372-44_0_2_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1372-44_0_2_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_1372-44_0_2_node_35 | 0.4 | n |  | TRUE
29 | bus_LV_1372-44_0_2_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_1372-44_0_2_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1372-44_0_2_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1372-44_0_2_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1372-44_0_2_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1372-44_0_2_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_1372-44_0_2_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_1372-44_0_2_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_1372-44_0_2_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_1372-44_0_2_node_38 | 0.4 | n |  | TRUE
39 | bus_LV_1372-44_0_2_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_1372-44_0_2_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_1372-44_0_2_node_45 | 0.4 | n |  | TRUE
42 | bus_LV_1372-44_0_2_node_51 | 0.4 | n |  | TRUE
43 | bus_LV_1372-44_0_2_node_52 | 0.4 | n |  | TRUE
44 | bus_LV_1372-44_0_2_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_1372-44_0_2_node_54 | 0.4 | n |  | TRUE
46 | bus_LV_1372-44_0_2_node_230 | 0.4 | n |  | TRUE
47 | bus_LV_1372-44_0_2_node_210 | 0.4 | n |  | TRUE
48 | bus_LV_1372-44_0_2_node_215 | 0.4 | n |  | TRUE
49 | bus_LV_1372-44_0_2_node_211 | 0.4 | n |  | TRUE
50 | bus_LV_1372-44_0_2_node_212 | 0.4 | n |  | TRUE
51 | bus_LV_1372-44_0_2_node_213 | 0.4 | n |  | TRUE
52 | bus_LV_1372-44_0_2_node_214 | 0.4 | n |  | TRUE
53 | bus_LV_1372-44_0_2_node_216 | 0.4 | n |  | TRUE
54 | bus_LV_1372-44_0_2_node_219 | 0.4 | n |  | TRUE
55 | bus_LV_1372-44_0_2_node_217 | 0.4 | n |  | TRUE
56 | bus_LV_1372-44_0_2_node_218 | 0.4 | n |  | TRUE
57 | bus_MV_22_1_node_99 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1372-44_0_2_load_0 | 0 | 0.00048187 | 0.00012077 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1372-44_0_2_load_2 | 2 | 0.00361 | 0.00090475 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1372-44_0_2_load_8 | 5 | 0.0025459 | 0.00063805 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1372-44_0_2_load_9 | 6 | 0.00069918 | 0.00017523 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1372-44_0_2_load_11 | 7 | 0.00074923 | 0.00018778 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1372-44_0_2_load_12 | 8 | 0.0026924 | 0.00067478 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1372-44_0_2_load_40 | 9 | 0.00021562 | 5.404e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1372-44_0_2_load_13 | 10 | 0.00078933 | 0.00019782 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1372-44_0_2_load_16 | 13 | 0.00087327 | 0.00021886 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1372-44_0_2_load_24 | 15 | 0.00041118 | 0.00010305 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1372-44_0_2_load_43 | 16 | 0.00073146 | 0.00018332 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1372-44_0_2_load_17 | 17 | 0.00052361 | 0.00013123 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1372-44_0_2_load_18 | 18 | 0.0004195 | 0.00010514 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1372-44_0_2_load_19 | 19 | 0.00045659 | 0.00011443 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1372-44_0_2_load_20 | 20 | 0.00051204 | 0.00012833 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1372-44_0_2_load_21 | 21 | 0.0006313 | 0.00015822 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1372-44_0_2_load_23 | 23 | 0.00095974 | 0.00024053 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1372-44_0_2_load_36 | 24 | 0.010122 | 0.0025369 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1372-44_0_2_load_32 | 25 | 0.0010301 | 0.00025817 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1372-44_0_2_load_25 | 26 | 0.0012393 | 0.00031059 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1372-44_0_2_load_35 | 28 | 0.0027349 | 0.00068544 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1372-44_0_2_load_37 | 29 | 0.0079117 | 0.0019829 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1372-44_0_2_load_27 | 30 | 0.0045574 | 0.0011422 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1372-44_0_2_load_31 | 33 | 0.0075864 | 0.0019013 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1372-44_0_2_load_42 | 34 | 0.00034592 | 8.6695e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1372-44_0_2_load_41 | 35 | 0.00066012 | 0.00016544 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1372-44_0_2_load_33 | 36 | 0.0006664 | 0.00016702 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1372-44_0_2_load_34 | 37 | 0.0074315 | 0.0018625 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1372-44_0_2_load_38 | 38 | 0.0015018 | 0.00037639 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1372-44_0_2_load_39 | 39 | 0.0010195 | 0.00025551 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1372-44_0_2_load_44 | 40 | 0.0015378 | 0.0003854 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1372-44_0_2_load_45 | 41 | 0.0031834 | 0.00079783 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1372-44_0_2_load_51 | 42 | 0.0031233 | 0.00078278 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1372-44_0_2_load_53 | 44 | 0.00636 | 0.001594 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1372-44_0_2_load_54 | 45 | 0.0015655 | 0.00039234 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1372-44_0_2_load_230 | 46 | 0.0047485 | 0.0011901 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1372-44_0_2_load_210 | 47 | 0.0010199 | 0.00025562 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1372-44_0_2_load_215 | 48 | 0.00051235 | 0.00012841 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1372-44_0_2_load_211 | 49 | 0.00044821 | 0.00011233 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1372-44_0_2_load_213 | 51 | 0.00033055 | 8.2843e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1372-44_0_2_load_214 | 52 | 0.0003546 | 8.8872e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1372-44_0_2_load_216 | 53 | 0.00045956 | 0.00011518 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1372-44_0_2_load_219 | 54 | 0.00074742 | 0.00018732 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1372-44_0_2_load_218 | 56 | 0.0013437 | 0.00033677 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1372-44_0_2_line_0 |  | 0 | 1 | 0.026749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1372-44_0_2_line_1 |  | 0 | 2 | 0.017651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1372-44_0_2_line_2 |  | 1 | 3 | 0.13258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1372-44_0_2_line_3 |  | 2 | 4 | 0.12425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1372-44_0_2_line_4 |  | 3 | 6 | 0.065615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1372-44_0_2_line_5 |  | 4 | 33 | 0.055894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1372-44_0_2_line_6 |  | 4 | 30 | 0.033732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1372-44_0_2_line_7 |  | 5 | 6 | 0.04022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1372-44_0_2_line_8 |  | 7 | 8 | 0.0051901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1372-44_0_2_line_9 |  | 8 | 9 | 0.23489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1372-44_0_2_line_10 |  | 9 | 10 | 0.19401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1372-44_0_2_line_11 |  | 9 | 38 | 0.042096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1372-44_0_2_line_12 |  | 11 | 12 | 0.069227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1372-44_0_2_line_13 |  | 11 | 13 | 0.010112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1372-44_0_2_line_14 |  | 11 | 14 | 0.16632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1372-44_0_2_line_15 |  | 12 | 15 | 0.018122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1372-44_0_2_line_16 |  | 13 | 16 | 0.0047551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1372-44_0_2_line_17 |  | 14 | 46 | 0.034613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1372-44_0_2_line_18 |  | 14 | 49 | 0.074109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1372-44_0_2_line_19 |  | 15 | 26 | 0.05034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1372-44_0_2_line_20 |  | 16 | 40 | 0.0086312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1372-44_0_2_line_21 |  | 17 | 18 | 0.01816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1372-44_0_2_line_22 |  | 17 | 19 | 0.010397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1372-44_0_2_line_23 |  | 19 | 20 | 0.0099574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1372-44_0_2_line_24 |  | 20 | 21 | 0.040538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1372-44_0_2_line_25 |  | 21 | 22 | 0.055305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1372-44_0_2_line_26 |  | 22 | 23 | 0.034037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1372-44_0_2_line_27 |  | 22 | 24 | 0.24053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1372-44_0_2_line_28 |  | 23 | 25 | 0.020433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1372-44_0_2_line_29 |  | 24 | 37 | 0.018993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1372-44_0_2_line_30 |  | 25 | 36 | 0.00050012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1372-44_0_2_line_31 |  | 26 | 27 | 0.013821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1372-44_0_2_line_32 |  | 27 | 28 | 0.022335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1372-44_0_2_line_33 |  | 27 | 29 | 0.029386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1372-44_0_2_line_34 |  | 28 | 37 | 0.019093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1372-44_0_2_line_35 |  | 29 | 33 | 0.038906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1372-44_0_2_line_36 |  | 30 | 31 | 0.030829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1372-44_0_2_line_37 |  | 31 | 32 | 0.010606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1372-44_0_2_line_38 |  | 32 | 34 | 0.018966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1372-44_0_2_line_39 |  | 32 | 35 | 0.0142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1372-44_0_2_line_40 |  | 35 | 39 | 0.014794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1372-44_0_2_line_41 |  | 38 | 39 | 0.0017008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1372-44_0_2_line_42 |  | 40 | 41 | 0.016111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1372-44_0_2_line_43 |  | 42 | 43 | 0.055505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1372-44_0_2_line_44 |  | 42 | 44 | 0.0071555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1372-44_0_2_line_45 |  | 43 | 45 | 0.017045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1372-44_0_2_line_46 |  | 44 | 46 | 0.058473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1372-44_0_2_line_47 |  | 47 | 48 | 0.050846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1372-44_0_2_line_48 |  | 48 | 54 | 0.065706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1372-44_0_2_line_49 |  | 48 | 51 | 0.027346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1372-44_0_2_line_50 |  | 49 | 50 | 0.017857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1372-44_0_2_line_51 |  | 50 | 51 | 0.027252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1372-44_0_2_line_52 |  | 50 | 52 | 0.003197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1372-44_0_2_line_53 |  | 52 | 53 | 0.02549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1372-44_0_2_line_54 |  | 54 | 55 | 0.052907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1372-44_0_2_line_55 |  | 55 | 56 | 0.012517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1372-44_0_2_trafo_25 | 0.63 MVA 20/0.4 kV | 57 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2692745.564 | 1206967.0418 | 2692741.4545 | 1206966.7111 | 2692719.0468 | 1206963.5772
1 | 2692701.5664 | 1206961.1323 | 2692719.0468 | 1206963.5772
2 | 2692745.564 | 1206967.0418 | 2692754.3666 | 1206834.757
3 | 2692674.4402 | 1207082.381 | 2692701.5664 | 1206961.1323
4 | 2692754.3666 | 1206834.757 | 2692758.4343 | 1206769.2682
5 | 2692674.4402 | 1207082.381 | 2692660.0805 | 1207136.399
6 | 2692674.4402 | 1207082.381 | 2692706.8822 | 1207091.6196
7 | 2692756.6763 | 1206729.163 | 2692758.3798 | 1206743.9254 | 2692758.8202 | 1206763.0561 | 2692758.4343 | 1206769.2682
8 | 2693008.7133 | 1206974.5405 | 2693004.5622 | 1206971.4251
9 | 2692808.9046 | 1207101.3936 | 2693004.5622 | 1206971.4251
10 | 2692808.9046 | 1207101.3936 | 2692940.5521 | 1207243.9075
11 | 2692808.9046 | 1207101.3936 | 2692767.1123 | 1207106.4437
12 | 2692727.0166 | 1207305.502 | 2692731.3073 | 1207236.4225
13 | 2692727.0166 | 1207305.502 | 2692717.6512 | 1207301.6886
14 | 2692727.0166 | 1207305.502 | 2692717.88 | 1207471.571
15 | 2692731.3073 | 1207236.4225 | 2692726.6113 | 1207236.1605 | 2692717.3409 | 1207232.225 | 2692714.5788 | 1207230.3345
16 | 2692717.6512 | 1207301.6886 | 2692713.2472 | 1207299.8955 | 2692713.2472 | 1207299.8955
17 | 2692698.9921 | 1207497.8286 | 2692709.7558 | 1207475.1361 | 2692712.0203 | 1207472.3138 | 2692717.88 | 1207471.571
18 | 2692770.8364 | 1207523.4152 | 2692717.88 | 1207471.571
19 | 2692714.5788 | 1207230.3345 | 2692695.0663 | 1207216.98 | 2692680.986 | 1207210.3236 | 2692670.1545 | 1207207.8039
20 | 2692709.3906 | 1207292.2997 | 2692710.3318 | 1207295.6585 | 2692713.2472 | 1207299.8955
21 | 2692316.3119 | 1207020.5612 | 2692322.1813 | 1207018.9812 | 2692332.8872 | 1207013.3817
22 | 2692342.0997 | 1207008.5634 | 2692332.8872 | 1207013.3817
23 | 2692350.9277 | 1207003.9574 | 2692350.6125 | 1207004.111 | 2692342.0997 | 1207008.5634
24 | 2692350.9277 | 1207003.9574 | 2692362.2913 | 1206998.4212 | 2692373.7309 | 1206995.9076 | 2692384.8955 | 1206998.382 | 2692389.0271 | 1207000.7248
25 | 2692440.9711 | 1207017.5072 | 2692436.0567 | 1207016.6083 | 2692416.1301 | 1207013.6756 | 2692405.719 | 1207010.1899 | 2692389.0271 | 1207000.7248
26 | 2692440.9711 | 1207017.5072 | 2692444.3962 | 1206994.2669 | 2692448.3307 | 1206984.4827
27 | 2692597.0933 | 1207200.4819 | 2692440.9711 | 1207017.5072
28 | 2692455.954 | 1206965.5254 | 2692448.3307 | 1206984.4827
29 | 2692597.0933 | 1207200.4819 | 2692616.0741 | 1207201.1576
30 | 2692456.1406 | 1206965.0614 | 2692455.954 | 1206965.5254
31 | 2692657.476 | 1207202.6313 | 2692664.4435 | 1207206.4754 | 2692670.1545 | 1207207.8039
32 | 2692657.476 | 1207202.6313 | 2692635.1553 | 1207201.8368
33 | 2692657.476 | 1207202.6313 | 2692654.476 | 1207196.4918 | 2692651.8318 | 1207182.6193 | 2692651.9801 | 1207174.1902
34 | 2692616.0741 | 1207201.1576 | 2692635.1553 | 1207201.8368
35 | 2692660.0805 | 1207136.399 | 2692656.6379 | 1207149.3494 | 2692652.1566 | 1207164.1564 | 2692651.9801 | 1207174.1902
36 | 2692737.1035 | 1207096.419 | 2692727.0704 | 1207096.5188 | 2692718.3799 | 1207094.8938 | 2692706.8822 | 1207091.6196
37 | 2692737.1035 | 1207096.419 | 2692736.4902 | 1207107.0054
38 | 2692736.4902 | 1207107.0054 | 2692736.3867 | 1207108.7717 | 2692735.4836 | 1207125.9449
39 | 2692736.4902 | 1207107.0054 | 2692750.6863 | 1207107.358
40 | 2692750.6863 | 1207107.358 | 2692758.0355 | 1207107.5405 | 2692765.4238 | 1207106.6477
41 | 2692767.1123 | 1207106.4437 | 2692765.4238 | 1207106.6477
42 | 2692705.0429 | 1207276.786 | 2692709.3906 | 1207292.2997
43 | 2692708.6228 | 1207607.2624 | 2692702.0025 | 1207604.5911 | 2692699.9342 | 1207601.6459 | 2692682.707 | 1207571.9475 | 2692682.3382 | 1207569.2511 | 2692684.2178 | 1207561.7708
44 | 2692685.9616 | 1207554.831 | 2692684.2178 | 1207561.7708
45 | 2692708.6228 | 1207607.2624 | 2692707.6296 | 1207621.7455 | 2692707.4119 | 1207624.2635
46 | 2692685.9616 | 1207554.831 | 2692698.9921 | 1207497.8286
47 | 2692833.7971 | 1207545.6553 | 2692876.5673 | 1207573.1518
48 | 2692833.7971 | 1207545.6553 | 2692887.1414 | 1207507.2928
49 | 2692833.7971 | 1207545.6553 | 2692813.7876 | 1207535.9599 | 2692809.5297 | 1207533.1317
50 | 2692787.5328 | 1207517.0836 | 2692770.8364 | 1207523.4152
51 | 2692787.5328 | 1207517.0836 | 2692798.8238 | 1207526.0207 | 2692809.5297 | 1207533.1317
52 | 2692787.5328 | 1207517.0836 | 2692790.5102 | 1207515.9193
53 | 2692790.5102 | 1207515.9193 | 2692814.2498 | 1207506.6362
54 | 2692887.1414 | 1207507.2928 | 2692885.5437 | 1207480.4722 | 2692888.1372 | 1207454.573
55 | 2692897.0954 | 1207445.8065 | 2692888.1372 | 1207454.573

## bus_geodata
| x | y | coords
0 | 2692719.0468 | 1206963.5772
1 | 2692745.564 | 1206967.0418
2 | 2692701.5664 | 1206961.1323
3 | 2692754.3666 | 1206834.757
4 | 2692674.4402 | 1207082.381
5 | 2692756.6763 | 1206729.163
6 | 2692758.4343 | 1206769.2682
7 | 2693008.7133 | 1206974.5405
8 | 2693004.5622 | 1206971.4251
9 | 2692808.9046 | 1207101.3936
10 | 2692940.5521 | 1207243.9075
11 | 2692727.0166 | 1207305.502
12 | 2692731.3073 | 1207236.4225
13 | 2692717.6512 | 1207301.6886
14 | 2692717.88 | 1207471.571
15 | 2692714.5788 | 1207230.3345
16 | 2692713.2472 | 1207299.8955
17 | 2692332.8872 | 1207013.3817
18 | 2692316.3119 | 1207020.5612
19 | 2692342.0997 | 1207008.5634
20 | 2692350.9277 | 1207003.9574
21 | 2692389.0271 | 1207000.7248
22 | 2692440.9711 | 1207017.5072
23 | 2692448.3307 | 1206984.4827
24 | 2692597.0933 | 1207200.4819
25 | 2692455.954 | 1206965.5254
26 | 2692670.1545 | 1207207.8039
27 | 2692657.476 | 1207202.6313
28 | 2692635.1553 | 1207201.8368
29 | 2692651.9801 | 1207174.1902
30 | 2692706.8822 | 1207091.6196
31 | 2692737.1035 | 1207096.419
32 | 2692736.4902 | 1207107.0054
33 | 2692660.0805 | 1207136.399
34 | 2692735.4836 | 1207125.9449
35 | 2692750.6863 | 1207107.358
36 | 2692456.1406 | 1206965.0614
37 | 2692616.0741 | 1207201.1576
38 | 2692767.1123 | 1207106.4437
39 | 2692765.4238 | 1207106.6477
40 | 2692709.3906 | 1207292.2997
41 | 2692705.0429 | 1207276.786
42 | 2692684.2178 | 1207561.7708
43 | 2692708.6228 | 1207607.2624
44 | 2692685.9616 | 1207554.831
45 | 2692707.4119 | 1207624.2635
46 | 2692698.9921 | 1207497.8286
47 | 2692876.5673 | 1207573.1518
48 | 2692833.7972 | 1207545.6553
49 | 2692770.8364 | 1207523.4152
50 | 2692787.5328 | 1207517.0836
51 | 2692809.5297 | 1207533.1317
52 | 2692790.5102 | 1207515.9193
53 | 2692814.2498 | 1207506.6362
54 | 2692887.1414 | 1207507.2928
55 | 2692888.1372 | 1207454.573
56 | 2692897.0954 | 1207445.8065
57 | 2692657.476 | 1207202.6313

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99542 | -0.088304 | 0.00048187 | 0.00012077
1 | 0.99534 | -0.089835 | 0 | 0
2 | 0.99548 | -0.087144 | 0.00361 | 0.00090475
3 | 0.99494 | -0.09742 | 0 | 0
4 | 0.99631 | -0.071099 | 0 | 0
5 | 0.99466 | -0.10298 | 0.0025459 | 0.00063805
6 | 0.99475 | -0.10117 | 0.00069918 | 0.00017523
7 | 0.99451 | -0.10589 | 0.00074923 | 0.00018778
8 | 0.99451 | -0.10582 | 0.0026924 | 0.00067478
9 | 0.99525 | -0.091566 | 0.00021562 | 5.404e-05
10 | 0.99511 | -0.094272 | 0.00078933 | 0.00019782
11 | 0.99654 | -0.066264 | 0 | 0
12 | 0.99827 | -0.033074 | 0 | 0
13 | 0.99649 | -0.067387 | 0.00087327 | 0.00021886
14 | 0.99335 | -0.12786 | 0 | 0
15 | 0.99872 | -0.024404 | 0.00041118 | 0.00010305
16 | 0.99646 | -0.067842 | 0.00073146 | 0.00018332
17 | 0.9967 | -0.063526 | 0.00052361 | 0.00013123
18 | 0.9967 | -0.063659 | 0.0004195 | 0.00010514
19 | 0.99671 | -0.063354 | 0.00045659 | 0.00011443
20 | 0.99672 | -0.063109 | 0.00051204 | 0.00012833
21 | 0.99679 | -0.061748 | 0.0006313 | 0.00015822
22 | 0.99692 | -0.059278 | 0 | 0
23 | 0.99684 | -0.060864 | 0.00095974 | 0.00024053
24 | 0.99806 | -0.037327 | 0.010122 | 0.0025369
25 | 0.99681 | -0.061472 | 0.0010301 | 0.00025817
26 | 1 | 0 | -0.090588 | -0.022387
27 | 0.99924 | -0.014684 | 0 | 0
28 | 0.99872 | -0.024632 | 0.0027349 | 0.00068544
29 | 0.99829 | -0.032862 | 0.0079117 | 0.0019829
30 | 0.99592 | -0.078536 | 0.0045574 | 0.0011422
31 | 0.9957 | -0.082867 | 0 | 0
32 | 0.99562 | -0.084357 | 0 | 0
33 | 0.99732 | -0.051586 | 0.0075864 | 0.0019013
34 | 0.99561 | -0.084472 | 0.00034592 | 8.6695e-05
35 | 0.99552 | -0.086266 | 0.00066012 | 0.00016544
36 | 0.99681 | -0.061478 | 0.0006664 | 0.00016702
37 | 0.99832 | -0.032232 | 0.0074315 | 0.0018625
38 | 0.99542 | -0.088261 | 0.0015018 | 0.00037639
39 | 0.99543 | -0.088083 | 0.0010195 | 0.00025551
40 | 0.99643 | -0.068558 | 0.0015378 | 0.0003854
41 | 0.99638 | -0.069458 | 0.0031834 | 0.00079783
42 | 0.99223 | -0.14955 | 0.0031233 | 0.00078278
43 | 0.99215 | -0.15109 | 0 | 0
44 | 0.99226 | -0.14896 | 0.00636 | 0.001594
45 | 0.99213 | -0.15157 | 0.0015655 | 0.00039234
46 | 0.99285 | -0.13753 | 0.0047485 | 0.0011901
47 | 0.99269 | -0.14079 | 0.0010199 | 0.00025562
48 | 0.99273 | -0.13988 | 0.00051235 | 0.00012841
49 | 0.993 | -0.1347 | 0.00044821 | 0.00011233
50 | 0.99292 | -0.13621 | 0 | 0
51 | 0.99282 | -0.13812 | 0.00033055 | 8.2843e-05
52 | 0.99292 | -0.13626 | 0.0003546 | 8.8872e-05
53 | 0.99291 | -0.13647 | 0.00045956 | 0.00011518
54 | 0.99261 | -0.14231 | 0.00074742 | 0.00018732
55 | 0.99254 | -0.14357 | 0 | 0
56 | 0.99253 | -0.14387 | 0.0013437 | 0.00033677
57 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0032472 | 0.00081125 | -0.003247 | -0.00081145 | 2.3627e-07 | -1.9647e-07 | 0.0048533 | 0.0048534 | 0.0048534 | 0.99542 | -0.088304 | 0.99534 | -0.089835 | 1.3334
1 | -0.0037291 | -0.00093202 | 0.0037293 | 0.00093192 | 2.0562e-07 | -9.7864e-08 | 0.0055736 | 0.0055735 | 0.0055736 | 0.99542 | -0.088304 | 0.99548 | -0.087144 | 1.5312
2 | 0.003247 | 0.00081145 | -0.0032458 | -0.00081242 | 1.1713e-06 | -9.7286e-07 | 0.0048534 | 0.004854 | 0.004854 | 0.99534 | -0.089835 | 0.99494 | -0.09742 | 1.3335
3 | -0.0073393 | -0.0018367 | 0.0073449 | 0.0018386 | 5.6063e-06 | 1.9714e-06 | 0.01097 | 0.010969 | 0.01097 | 0.99548 | -0.087144 | 0.99631 | -0.071099 | 3.0137
4 | 0.0032458 | 0.00081242 | -0.0032453 | -0.0008129 | 5.7978e-07 | -4.8091e-07 | 0.004854 | 0.0048543 | 0.0048543 | 0.99494 | -0.09742 | 0.99475 | -0.10117 | 1.3336
5 | -0.019887 | -0.0049786 | 0.019906 | 0.0049897 | 1.8489e-05 | 1.1105e-05 | 0.0297 | 0.0297 | 0.0297 | 0.99631 | -0.071099 | 0.99732 | -0.051586 | 8.1595
6 | 0.012542 | 0.00314 | -0.012538 | -0.0031376 | 4.4383e-06 | 2.4014e-06 | 0.018731 | 0.018732 | 0.018732 | 0.99631 | -0.071099 | 0.99592 | -0.078536 | 5.146
7 | -0.0025459 | -0.00063805 | 0.0025461 | 0.00063767 | 2.1877e-07 | -3.8207e-07 | 0.0038086 | 0.0038084 | 0.0038086 | 0.99466 | -0.10298 | 0.99475 | -0.10117 | 1.0463
8 | -0.00074923 | -0.00018778 | 0.00074924 | 0.00018771 | 2.4459e-09 | -6.5779e-08 | 0.001121 | 0.001121 | 0.001121 | 0.99451 | -0.10589 | 0.99451 | -0.10582 | 0.30798
9 | -0.0034417 | -0.00086249 | 0.003444 | 0.00086094 | 2.3353e-06 | -1.5556e-06 | 0.0051495 | 0.0051484 | 0.0051495 | 0.99451 | -0.10582 | 0.99525 | -0.091566 | 1.4147
10 | 0.00078943 | 0.00019537 | -0.00078933 | -0.00019782 | 1.0128e-07 | -2.456e-06 | 0.0011794 | 0.0011803 | 0.0011803 | 0.99525 | -0.091566 | 0.99511 | -0.094272 | 0.32426
11 | -0.004449 | -0.0011103 | 0.0044497 | 0.0011102 | 6.9813e-07 | -1.0033e-07 | 0.0066502 | 0.00665 | 0.0066502 | 0.99525 | -0.091566 | 0.99542 | -0.088261 | 1.827
12 | -0.027419 | -0.0068932 | 0.027462 | 0.0069201 | 4.3529e-05 | 2.6955e-05 | 0.040949 | 0.040948 | 0.040949 | 0.99654 | -0.066264 | 0.99827 | -0.033074 | 11.2496
13 | 0.0063266 | 0.0015854 | -0.0063263 | -0.0015853 | 3.384e-07 | 8.4837e-08 | 0.0094467 | 0.0094468 | 0.0094468 | 0.99654 | -0.066264 | 0.99649 | -0.067387 | 2.5953
14 | 0.021092 | 0.0053078 | -0.02103 | -0.0052703 | 6.1896e-05 | 3.7453e-05 | 0.031502 | 0.031503 | 0.031503 | 0.99654 | -0.066264 | 0.99335 | -0.12786 | 8.6546
15 | -0.027462 | -0.0069201 | 0.027474 | 0.0069272 | 1.1395e-05 | 7.0555e-06 | 0.040948 | 0.040948 | 0.040948 | 0.99827 | -0.033074 | 0.99872 | -0.024404 | 11.2496
16 | 0.005453 | 0.0013664 | -0.0054529 | -0.0013664 | 1.1823e-07 | 1.3724e-08 | 0.0081427 | 0.0081428 | 0.0081428 | 0.99649 | -0.067387 | 0.99646 | -0.067842 | 2.237
17 | 0.015811 | 0.0039656 | -0.015804 | -0.0039614 | 7.2817e-06 | 4.2124e-06 | 0.023685 | 0.023685 | 0.023685 | 0.99335 | -0.12786 | 0.99285 | -0.13753 | 6.507
18 | 0.0052195 | 0.0013047 | -0.0052178 | -0.0013046 | 1.6984e-06 | 1.2797e-07 | 0.0078174 | 0.0078178 | 0.0078178 | 0.99335 | -0.12786 | 0.993 | -0.1347 | 2.1477
19 | -0.027885 | -0.0070302 | 0.027918 | 0.0070504 | 3.2607e-05 | 2.0209e-05 | 0.041561 | 0.041561 | 0.041561 | 0.99872 | -0.024404 | 1 | 0 | 11.4178
20 | 0.0047215 | 0.0011831 | -0.0047213 | -0.0011831 | 1.6089e-07 | -9.459e-09 | 0.0070505 | 0.0070505 | 0.0070505 | 0.99646 | -0.067842 | 0.99643 | -0.068558 | 1.937
21 | 0.0004195 | 0.0001049 | -0.0004195 | -0.00010514 | 2.6708e-09 | -2.3497e-07 | 0.0006262 | 0.00062629 | 0.00062629 | 0.9967 | -0.063526 | 0.9967 | -0.063659 | 0.17206
22 | -0.00094311 | -0.00023613 | 0.00094312 | 0.000236 | 7.728e-09 | -1.3055e-07 | 0.0014079 | 0.0014079 | 0.0014079 | 0.9967 | -0.063526 | 0.99671 | -0.063354 | 0.38679
23 | -0.0013997 | -0.00035043 | 0.0013997 | 0.00035031 | 1.6303e-08 | -1.1934e-07 | 0.0020895 | 0.0020895 | 0.0020895 | 0.99671 | -0.063354 | 0.99672 | -0.063109 | 0.57405
24 | -0.0019118 | -0.00047864 | 0.0019119 | 0.00047819 | 1.2381e-07 | -4.4915e-07 | 0.0028539 | 0.0028537 | 0.0028539 | 0.99672 | -0.063109 | 0.99679 | -0.061748 | 0.78404
25 | -0.0025432 | -0.00063641 | 0.0025435 | 0.00063588 | 2.9885e-07 | -5.2975e-07 | 0.0037961 | 0.0037959 | 0.0037961 | 0.99679 | -0.061748 | 0.99692 | -0.059278 | 1.0429
26 | 0.0026565 | 0.00066516 | -0.0026563 | -0.00066548 | 2.0066e-07 | -3.1534e-07 | 0.0039649 | 0.0039651 | 0.0039651 | 0.99692 | -0.059278 | 0.99684 | -0.060864 | 1.0893
27 | -0.0052 | -0.001301 | 0.0052054 | 0.0013014 | 5.4319e-06 | 3.3664e-07 | 0.0077608 | 0.0077597 | 0.0077608 | 0.99692 | -0.059278 | 0.99806 | -0.037327 | 2.1321
28 | 0.0016966 | 0.00042495 | -0.0016965 | -0.00042518 | 4.9141e-08 | -2.3491e-07 | 0.0025324 | 0.0025325 | 0.0025325 | 0.99684 | -0.060864 | 0.99681 | -0.061472 | 0.69575
29 | -0.015328 | -0.0038383 | 0.015332 | 0.0038404 | 3.7191e-06 | 2.132e-06 | 0.022851 | 0.022851 | 0.022851 | 0.99806 | -0.037327 | 0.99832 | -0.032232 | 6.2778
30 | 0.0006664 | 0.00016701 | -0.0006664 | -0.00016702 | 1.854e-10 | -6.4005e-09 | 0.00099479 | 0.0009948 | 0.0009948 | 0.99681 | -0.061472 | 0.99681 | -0.061478 | 0.2733
31 | 0.06102 | 0.015336 | -0.060978 | -0.015309 | 4.2745e-05 | 2.7176e-05 | 0.090814 | 0.090815 | 0.090815 | 1 | 0 | 0.99924 | -0.014684 | 24.949
32 | 0.025518 | 0.0064009 | -0.025506 | -0.0063934 | 1.2096e-05 | 7.449e-06 | 0.038003 | 0.038003 | 0.038003 | 0.99924 | -0.014684 | 0.99872 | -0.024632 | 10.4403
33 | 0.035459 | 0.0089084 | -0.035428 | -0.0088891 | 3.0735e-05 | 1.9286e-05 | 0.052812 | 0.052812 | 0.052812 | 0.99924 | -0.014684 | 0.99829 | -0.032862 | 14.5088
34 | 0.022771 | 0.005708 | -0.022763 | -0.0057029 | 8.2419e-06 | 5.0251e-06 | 0.033928 | 0.033928 | 0.033928 | 0.99872 | -0.024632 | 0.99832 | -0.032232 | 9.3209
35 | 0.027517 | 0.0069062 | -0.027492 | -0.006891 | 2.4548e-05 | 1.5203e-05 | 0.041019 | 0.041019 | 0.041019 | 0.99829 | -0.032862 | 0.99732 | -0.051586 | 11.269
36 | 0.0079806 | 0.0019954 | -0.007979 | -0.0019947 | 1.6433e-06 | 6.5064e-07 | 0.011922 | 0.011922 | 0.011922 | 0.99592 | -0.078536 | 0.9957 | -0.082867 | 3.2754
37 | 0.007979 | 0.0019947 | -0.0079784 | -0.0019945 | 5.6534e-07 | 2.2388e-07 | 0.011922 | 0.011922 | 0.011922 | 0.9957 | -0.082867 | 0.99562 | -0.084357 | 3.2754
38 | 0.00034592 | 8.6449e-05 | -0.00034592 | -8.6695e-05 | 1.9007e-09 | -2.4543e-07 | 0.00051691 | 0.00051699 | 0.00051699 | 0.99562 | -0.084357 | 0.99561 | -0.084472 | 0.14203
39 | 0.0076325 | 0.001908 | -0.0076318 | -0.0019078 | 6.9274e-07 | 2.587e-07 | 0.011406 | 0.011406 | 0.011406 | 0.99562 | -0.084357 | 0.99552 | -0.086266 | 3.1334
40 | 0.0069717 | 0.0017423 | -0.0069711 | -0.0017422 | 6.0222e-07 | 1.9309e-07 | 0.010419 | 0.010419 | 0.010419 | 0.99552 | -0.086266 | 0.99543 | -0.088083 | 2.8624
41 | -0.0059516 | -0.0014866 | 0.0059516 | 0.0014866 | 5.0464e-08 | 1.0187e-08 | 0.008895 | 0.008895 | 0.008895 | 0.99542 | -0.088261 | 0.99543 | -0.088083 | 2.4437
42 | 0.0031835 | 0.00079771 | -0.0031834 | -0.00079783 | 1.3655e-07 | -1.2246e-07 | 0.0047541 | 0.0047542 | 0.0047542 | 0.99643 | -0.068558 | 0.99638 | -0.069458 | 1.3061
43 | 0.0015656 | 0.0003915 | -0.0015655 | -0.00039214 | 1.1472e-07 | -6.4344e-07 | 0.0023476 | 0.0023478 | 0.0023478 | 0.99223 | -0.14955 | 0.99215 | -0.15109 | 0.64501
44 | -0.0046889 | -0.0011743 | 0.0046891 | 0.0011743 | 1.3267e-07 | -7.5174e-09 | 0.0070315 | 0.0070315 | 0.0070315 | 0.99223 | -0.14955 | 0.99226 | -0.14896 | 1.9317
45 | 0.0015655 | 0.00039214 | -0.0015655 | -0.00039234 | 3.5234e-08 | -1.9756e-07 | 0.0023478 | 0.0023479 | 0.0023479 | 0.99215 | -0.15109 | 0.99213 | -0.15157 | 0.64503
46 | -0.011049 | -0.0027682 | 0.011055 | 0.0027713 | 6.0197e-06 | 3.0969e-06 | 0.016569 | 0.016569 | 0.016569 | 0.99226 | -0.14896 | 0.99285 | -0.13753 | 4.5519
47 | -0.0010199 | -0.00025562 | 0.00102 | 0.00025499 | 4.4562e-08 | -6.2886e-07 | 0.0015289 | 0.0015286 | 0.0015289 | 0.99269 | -0.14079 | 0.99273 | -0.13988 | 0.42002
48 | 0.0020915 | 0.00052262 | -0.0020913 | -0.00052331 | 2.421e-07 | -6.9448e-07 | 0.0031344 | 0.0031347 | 0.0031347 | 0.99273 | -0.13988 | 0.99261 | -0.14231 | 0.86119
49 | -0.0036238 | -0.00090602 | 0.0036241 | 0.00090586 | 3.0247e-07 | -1.6002e-07 | 0.005431 | 0.0054309 | 0.005431 | 0.99273 | -0.13988 | 0.99282 | -0.13812 | 1.492
50 | 0.0047696 | 0.0011922 | -0.0047692 | -0.0011923 | 3.4196e-07 | -1.2124e-08 | 0.0071461 | 0.0071462 | 0.0071462 | 0.993 | -0.1347 | 0.99292 | -0.13621 | 1.9632
51 | 0.0039551 | 0.00098858 | -0.0039547 | -0.0009887 | 3.5892e-07 | -1.2274e-07 | 0.0059262 | 0.0059263 | 0.0059263 | 0.99292 | -0.13621 | 0.99282 | -0.13812 | 1.6281
52 | 0.00081417 | 0.00020368 | -0.00081417 | -0.00020372 | 1.7845e-09 | -4.0209e-08 | 0.00122 | 0.00122 | 0.00122 | 0.99292 | -0.13621 | 0.99292 | -0.13626 | 0.33517
53 | 0.00045957 | 0.00011485 | -0.00045956 | -0.00011518 | 4.5334e-09 | -3.2679e-07 | 0.00068861 | 0.00068872 | 0.00068872 | 0.99292 | -0.13626 | 0.99291 | -0.13647 | 0.18921
54 | 0.0013438 | 0.00033599 | -0.0013438 | -0.00033662 | 8.0507e-08 | -6.3231e-07 | 0.0020143 | 0.0020145 | 0.0020145 | 0.99261 | -0.14231 | 0.99254 | -0.14357 | 0.55344
55 | 0.0013438 | 0.00033662 | -0.0013437 | -0.00033677 | 1.905e-08 | -1.4958e-07 | 0.0020145 | 0.0020146 | 0.0020146 | 0.99254 | -0.14357 | 0.99253 | -0.14387 | 0.55345

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.091827 | 0.022698

## res_load
| p_mw | q_mvar
0 | 0.00048187 | 0.00012077
1 | 0.00361 | 0.00090475
2 | 0.0025459 | 0.00063805
3 | 0.00069918 | 0.00017523
4 | 0.00074923 | 0.00018778
5 | 0.0026924 | 0.00067478
6 | 0.00021562 | 5.404e-05
7 | 0.00078933 | 0.00019782
8 | 0.00087327 | 0.00021886
9 | 0.00041118 | 0.00010305
10 | 0.00073146 | 0.00018332
11 | 0.00052361 | 0.00013123
12 | 0.0004195 | 0.00010514
13 | 0.00045659 | 0.00011443
14 | 0.00051204 | 0.00012833
15 | 0.0006313 | 0.00015822
16 | 0.00095974 | 0.00024053
17 | 0.010122 | 0.0025369
18 | 0.0010301 | 0.00025817
19 | 0.0012393 | 0.00031059
20 | 0.0027349 | 0.00068544
21 | 0.0079117 | 0.0019829
22 | 0.0045574 | 0.0011422
23 | 0.0075864 | 0.0019013
24 | 0.00034592 | 8.6695e-05
25 | 0.00066012 | 0.00016544
26 | 0.0006664 | 0.00016702
27 | 0.0074315 | 0.0018625
28 | 0.0015018 | 0.00037639
29 | 0.0010195 | 0.00025551
30 | 0.0015378 | 0.0003854
31 | 0.0031834 | 0.00079783
32 | 0.0031233 | 0.00078278
33 | 0.00636 | 0.001594
34 | 0.0015655 | 0.00039234
35 | 0.0047485 | 0.0011901
36 | 0.0010199 | 0.00025562
37 | 0.00051235 | 0.00012841
38 | 0.00044821 | 0.00011233
39 | 0.00033055 | 8.2843e-05
40 | 0.0003546 | 8.8872e-05
41 | 0.00045956 | 0.00011518
42 | 0.00074742 | 0.00018732
43 | 0.0013437 | 0.00033677

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1