## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1372-49_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1372-49_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1372-49_0_4_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_1372-49_0_4_node_59 | 0.4 | n |  | TRUE
4 | bus_LV_1372-49_0_4_node_84 | 0.4 | n |  | TRUE
5 | bus_LV_1372-49_0_4_node_2 | 0.4 | n |  | TRUE
6 | bus_LV_1372-49_0_4_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1372-49_0_4_node_51 | 0.4 | n |  | TRUE
8 | bus_LV_1372-49_0_4_node_50 | 0.4 | n |  | TRUE
9 | bus_LV_1372-49_0_4_node_58 | 0.4 | n |  | TRUE
10 | bus_LV_1372-49_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1372-49_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1372-49_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1372-49_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1372-49_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1372-49_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1372-49_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1372-49_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1372-49_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1372-49_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1372-49_0_4_node_124 | 0.4 | n |  | TRUE
21 | bus_LV_1372-49_0_4_node_123 | 0.4 | n |  | TRUE
22 | bus_LV_1372-49_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1372-49_0_4_node_101 | 0.4 | n |  | TRUE
24 | bus_LV_1372-49_0_4_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_1372-49_0_4_node_120 | 0.4 | n |  | TRUE
26 | bus_LV_1372-49_0_4_node_121 | 0.4 | n |  | TRUE
27 | bus_LV_1372-49_0_4_node_119 | 0.4 | n |  | TRUE
28 | bus_LV_1372-49_0_4_node_122 | 0.4 | n |  | TRUE
29 | bus_LV_1372-49_0_4_node_102 | 0.4 | n |  | TRUE
30 | bus_LV_1372-49_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1372-49_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1372-49_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1372-49_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1372-49_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1372-49_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1372-49_0_4_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_1372-49_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_1372-49_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_1372-49_0_4_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1372-49_0_4_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_1372-49_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_1372-49_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_1372-49_0_4_node_114 | 0.4 | n |  | TRUE
44 | bus_LV_1372-49_0_4_node_118 | 0.4 | n |  | TRUE
45 | bus_LV_1372-49_0_4_node_111 | 0.4 | n |  | TRUE
46 | bus_LV_1372-49_0_4_node_72 | 0.4 | n |  | TRUE
47 | bus_LV_1372-49_0_4_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_1372-49_0_4_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_1372-49_0_4_node_117 | 0.4 | n |  | TRUE
50 | bus_LV_1372-49_0_4_node_103 | 0.4 | n |  | TRUE
51 | bus_LV_1372-49_0_4_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_1372-49_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_1372-49_0_4_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_1372-49_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_1372-49_0_4_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_1372-49_0_4_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_1372-49_0_4_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_1372-49_0_4_node_39 | 0.4 | n |  | TRUE
59 | bus_LV_1372-49_0_4_node_37 | 0.4 | n |  | TRUE
60 | bus_LV_1372-49_0_4_node_40 | 0.4 | n |  | TRUE
61 | bus_LV_1372-49_0_4_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_1372-49_0_4_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_1372-49_0_4_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_1372-49_0_4_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_1372-49_0_4_node_43 | 0.4 | n |  | TRUE
66 | bus_LV_1372-49_0_4_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_1372-49_0_4_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_1372-49_0_4_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_1372-49_0_4_node_47 | 0.4 | n |  | TRUE
70 | bus_LV_1372-49_0_4_node_109 | 0.4 | n |  | TRUE
71 | bus_LV_1372-49_0_4_node_108 | 0.4 | n |  | TRUE
72 | bus_LV_1372-49_0_4_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_1372-49_0_4_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_1372-49_0_4_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_1372-49_0_4_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_1372-49_0_4_node_60 | 0.4 | n |  | TRUE
77 | bus_LV_1372-49_0_4_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_1372-49_0_4_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_1372-49_0_4_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_1372-49_0_4_node_110 | 0.4 | n |  | TRUE
81 | bus_LV_1372-49_0_4_node_64 | 0.4 | n |  | TRUE
82 | bus_LV_1372-49_0_4_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_1372-49_0_4_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_1372-49_0_4_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_1372-49_0_4_node_71 | 0.4 | n |  | TRUE
86 | bus_LV_1372-49_0_4_node_68 | 0.4 | n |  | TRUE
87 | bus_LV_1372-49_0_4_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_1372-49_0_4_node_69 | 0.4 | n |  | TRUE
89 | bus_LV_1372-49_0_4_node_70 | 0.4 | n |  | TRUE
90 | bus_LV_1372-49_0_4_node_74 | 0.4 | n |  | TRUE
91 | bus_LV_1372-49_0_4_node_75 | 0.4 | n |  | TRUE
92 | bus_LV_1372-49_0_4_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_1372-49_0_4_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_1372-49_0_4_node_125 | 0.4 | n |  | TRUE
95 | bus_LV_1372-49_0_4_node_78 | 0.4 | n |  | TRUE
96 | bus_LV_1372-49_0_4_node_112 | 0.4 | n |  | TRUE
97 | bus_LV_1372-49_0_4_node_113 | 0.4 | n |  | TRUE
98 | bus_LV_1372-49_0_4_node_115 | 0.4 | n |  | TRUE
99 | bus_LV_1372-49_0_4_node_79 | 0.4 | n |  | TRUE
100 | bus_LV_1372-49_0_4_node_94 | 0.4 | n |  | TRUE
101 | bus_LV_1372-49_0_4_node_95 | 0.4 | n |  | TRUE
102 | bus_LV_1372-49_0_4_node_93 | 0.4 | n |  | TRUE
103 | bus_LV_1372-49_0_4_node_80 | 0.4 | n |  | TRUE
104 | bus_LV_1372-49_0_4_node_81 | 0.4 | n |  | TRUE
105 | bus_LV_1372-49_0_4_node_82 | 0.4 | n |  | TRUE
106 | bus_LV_1372-49_0_4_node_97 | 0.4 | n |  | TRUE
107 | bus_LV_1372-49_0_4_node_83 | 0.4 | n |  | TRUE
108 | bus_LV_1372-49_0_4_node_116 | 0.4 | n |  | TRUE
109 | bus_LV_1372-49_0_4_node_85 | 0.4 | n |  | TRUE
110 | bus_LV_1372-49_0_4_node_86 | 0.4 | n |  | TRUE
111 | bus_LV_1372-49_0_4_node_87 | 0.4 | n |  | TRUE
112 | bus_LV_1372-49_0_4_node_88 | 0.4 | n |  | TRUE
113 | bus_LV_1372-49_0_4_node_89 | 0.4 | n |  | TRUE
114 | bus_LV_1372-49_0_4_node_90 | 0.4 | n |  | TRUE
115 | bus_LV_1372-49_0_4_node_91 | 0.4 | n |  | TRUE
116 | bus_LV_1372-49_0_4_node_92 | 0.4 | n |  | TRUE
117 | bus_LV_1372-49_0_4_node_104 | 0.4 | n |  | TRUE
118 | bus_LV_1372-49_0_4_node_96 | 0.4 | n |  | TRUE
119 | bus_LV_1372-49_0_4_node_98 | 0.4 | n |  | TRUE
120 | bus_LV_1372-49_0_4_node_99 | 0.4 | n |  | TRUE
121 | bus_LV_1372-49_0_4_node_100 | 0.4 | n |  | TRUE
122 | bus_LV_1372-49_0_4_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_1372-49_0_4_node_106 | 0.4 | n |  | TRUE
124 | bus_LV_1372-49_0_4_node_107 | 0.4 | n |  | TRUE
125 | bus_MV_22_1_node_119 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1372-49_0_4_load_0 | 0 | 0.0013363 | 0.0003349 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1372-49_0_4_load_1 | 1 | 0.0015026 | 0.00037659 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1372-49_0_4_load_59 | 3 | 0.0041353 | 0.0010364 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1372-49_0_4_load_84 | 4 | 0.0028824 | 0.00072239 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1372-49_0_4_load_2 | 5 | 0.0032971 | 0.00082632 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1372-49_0_4_load_3 | 6 | 0.002098 | 0.0005258 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1372-49_0_4_load_51 | 7 | 0.0041243 | 0.0010336 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1372-49_0_4_load_50 | 8 | 0.0065998 | 0.0016541 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1372-49_0_4_load_58 | 9 | 0.0014318 | 0.00035883 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1372-49_0_4_load_5 | 10 | 0.0043606 | 0.0010929 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1372-49_0_4_load_7 | 12 | 0.0035402 | 0.00088726 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1372-49_0_4_load_8 | 13 | 0.0035383 | 0.00088678 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1372-49_0_4_load_12 | 14 | 0.0012622 | 0.00031633 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1372-49_0_4_load_14 | 16 | 0.0018279 | 0.00045811 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1372-49_0_4_load_15 | 19 | 0.001797 | 0.00045038 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1372-49_0_4_load_124 | 20 | 0.0039198 | 0.00098238 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1372-49_0_4_load_123 | 21 | 0.0011405 | 0.00028584 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1372-49_0_4_load_16 | 22 | 0.0015789 | 0.0003957 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1372-49_0_4_load_101 | 23 | 0.0016194 | 0.00040586 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1372-49_0_4_load_120 | 25 | 0.0031766 | 0.00079613 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1372-49_0_4_load_121 | 26 | 0.0030441 | 0.00076293 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1372-49_0_4_load_119 | 27 | 0.0023563 | 0.00059055 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1372-49_0_4_load_122 | 28 | 0.00072661 | 0.00018211 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1372-49_0_4_load_102 | 29 | 0.0047256 | 0.0011844 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1372-49_0_4_load_17 | 30 | 0.0039845 | 0.00099861 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1372-49_0_4_load_18 | 31 | 0.0052204 | 0.0013083 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1372-49_0_4_load_20 | 33 | 0.0038153 | 0.00095619 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1372-49_0_4_load_22 | 35 | 0.0027907 | 0.00069941 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1372-49_0_4_load_31 | 37 | 0.0031692 | 0.00079428 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1372-49_0_4_load_29 | 38 | 0.0054839 | 0.0013744 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1372-49_0_4_load_25 | 39 | 0.0028873 | 0.00072362 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1372-49_0_4_load_24 | 40 | 0.0039131 | 0.00098073 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1372-49_0_4_load_26 | 42 | 0.0033557 | 0.00084101 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1372-49_0_4_load_114 | 43 | 0.0048558 | 0.001217 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1372-49_0_4_load_118 | 44 | 0.0042137 | 0.001056 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1372-49_0_4_load_111 | 45 | 0.0046465 | 0.0011645 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1372-49_0_4_load_72 | 46 | 0.0042147 | 0.0010563 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1372-49_0_4_load_27 | 47 | 0.0051372 | 0.0012875 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1372-49_0_4_load_28 | 48 | 0.0046291 | 0.0011602 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1372-49_0_4_load_117 | 49 | 0.0041276 | 0.0010345 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1372-49_0_4_load_32 | 51 | 0.0040884 | 0.0010246 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1372-49_0_4_load_33 | 52 | 0.0077301 | 0.0019373 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1372-49_0_4_load_48 | 54 | 0.0025736 | 0.000645 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1372-49_0_4_load_36 | 56 | 0.0033837 | 0.00084803 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1372-49_0_4_load_49 | 57 | 0.0047679 | 0.0011949 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1372-49_0_4_load_39 | 58 | 0.0030341 | 0.00076043 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1372-49_0_4_load_37 | 59 | 0.006083 | 0.0015245 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1372-49_0_4_load_40 | 60 | 0.0011413 | 0.00028603 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1372-49_0_4_load_38 | 61 | 0.0016827 | 0.00042173 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1372-49_0_4_load_52 | 62 | 0.0010987 | 0.00027536 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1372-49_0_4_load_53 | 63 | 0.0046929 | 0.0011761 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1372-49_0_4_load_41 | 64 | 0.00335 | 0.00083958 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1372-49_0_4_load_43 | 65 | 0.0038436 | 0.00096328 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1372-49_0_4_load_44 | 66 | 0.0015535 | 0.00038934 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1372-49_0_4_load_45 | 67 | 0.0015178 | 0.0003804 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1372-49_0_4_load_46 | 68 | 0.00074258 | 0.00018611 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1372-49_0_4_load_47 | 69 | 0.00091955 | 0.00023046 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1372-49_0_4_load_109 | 70 | 0.0035481 | 0.00088923 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1372-49_0_4_load_108 | 71 | 0.0039594 | 0.00099233 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1372-49_0_4_load_54 | 72 | 0.0027912 | 0.00069955 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1372-49_0_4_load_55 | 73 | 0.0023467 | 0.00058814 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1372-49_0_4_load_56 | 74 | 0.0038645 | 0.00096852 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1372-49_0_4_load_57 | 75 | 0.0010236 | 0.00025653 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1372-49_0_4_load_60 | 76 | 0.0079822 | 0.0020005 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1372-49_0_4_load_61 | 77 | 0.00021477 | 5.3827e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1372-49_0_4_load_63 | 79 | 0.009255 | 0.0023195 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1372-49_0_4_load_110 | 80 | 0.0045957 | 0.0011518 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1372-49_0_4_load_65 | 82 | 0.0068046 | 0.0017054 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1372-49_0_4_load_66 | 83 | 0.013169 | 0.0033004 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1372-49_0_4_load_67 | 84 | 0.010191 | 0.0025542 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1372-49_0_4_load_68 | 86 | 0.0061102 | 0.0015313 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1372-49_0_4_load_73 | 87 | 0.0042134 | 0.001056 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1372-49_0_4_load_69 | 88 | 0.0051312 | 0.001286 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1372-49_0_4_load_74 | 90 | 0.0044546 | 0.0011164 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1372-49_0_4_load_75 | 91 | 0.0041892 | 0.0010499 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1372-49_0_4_load_76 | 92 | 0.0035967 | 0.00090141 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1372-49_0_4_load_77 | 93 | 0.0038371 | 0.00096166 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1372-49_0_4_load_125 | 94 | 0.0049512 | 0.0012409 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1372-49_0_4_load_78 | 95 | 0.0057058 | 0.00143 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1372-49_0_4_load_112 | 96 | 0.0054597 | 0.0013683 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1372-49_0_4_load_113 | 97 | 0.004873 | 0.0012213 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1372-49_0_4_load_115 | 98 | 0.011858 | 0.0029718 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1372-49_0_4_load_94 | 100 | 0.0010327 | 0.00025883 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1372-49_0_4_load_95 | 101 | 0.0010262 | 0.0002572 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1372-49_0_4_load_93 | 102 | 0.001946 | 0.00048771 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1372-49_0_4_load_80 | 103 | 0.0056809 | 0.0014238 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1372-49_0_4_load_81 | 104 | 0.004274 | 0.0010712 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1372-49_0_4_load_82 | 105 | 0.0046141 | 0.0011564 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1372-49_0_4_load_97 | 106 | 0.0049187 | 0.0012327 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1372-49_0_4_load_83 | 107 | 0.0042139 | 0.0010561 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1372-49_0_4_load_116 | 108 | 0.0065731 | 0.0016474 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1372-49_0_4_load_85 | 109 | 0.0016471 | 0.0004128 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1372-49_0_4_load_86 | 110 | 0.0038379 | 0.00096188 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1372-49_0_4_load_87 | 111 | 0.0022594 | 0.00056626 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1372-49_0_4_load_88 | 112 | 0.001336 | 0.00033483 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1372-49_0_4_load_89 | 113 | 0.0018442 | 0.0004622 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1372-49_0_4_load_91 | 115 | 0.0018271 | 0.00045792 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1372-49_0_4_load_92 | 116 | 0.0012534 | 0.00031414 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1372-49_0_4_load_104 | 117 | 0.0062681 | 0.0015709 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1372-49_0_4_load_96 | 118 | 0.0021905 | 0.00054899 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1372-49_0_4_load_98 | 119 | 0.0070395 | 0.0017643 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1372-49_0_4_load_99 | 120 | 0.010457 | 0.0026207 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1372-49_0_4_load_100 | 121 | 0.0034204 | 0.00085724 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1372-49_0_4_load_105 | 122 | 0.010466 | 0.0026231 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1372-49_0_4_load_106 | 123 | 0.0065973 | 0.0016534 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1372-49_0_4_load_107 | 124 | 0.0053593 | 0.0013432 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1372-49_0_4_line_0 |  | 0 | 1 | 0.014692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1372-49_0_4_line_1 |  | 1 | 2 | 0.009909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1372-49_0_4_line_2 |  | 2 | 3 | 0.015325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1372-49_0_4_line_3 |  | 2 | 4 | 0.028961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1372-49_0_4_line_4 |  | 3 | 9 | 0.015077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1372-49_0_4_line_5 |  | 5 | 6 | 0.023199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1372-49_0_4_line_6 |  | 6 | 7 | 0.015529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1372-49_0_4_line_7 |  | 7 | 8 | 0.023601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1372-49_0_4_line_8 |  | 8 | 37 | 0.0052144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1372-49_0_4_line_9 |  | 9 | 75 | 0.00067931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1372-49_0_4_line_10 |  | 10 | 11 | 0.029002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1372-49_0_4_line_11 |  | 11 | 12 | 0.024371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1372-49_0_4_line_12 |  | 11 | 13 | 0.054529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1372-49_0_4_line_13 |  | 13 | 17 | 0.054596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1372-49_0_4_line_14 |  | 14 | 15 | 0.045394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1372-49_0_4_line_15 |  | 14 | 16 | 0.093059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1372-49_0_4_line_16 |  | 15 | 22 | 0.041361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1372-49_0_4_line_17 |  | 16 | 19 | 0.034555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1372-49_0_4_line_18 |  | 17 | 18 | 0.005428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1372-49_0_4_line_19 |  | 18 | 19 | 0.017449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1372-49_0_4_line_20 |  | 18 | 20 | 0.037492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1372-49_0_4_line_21 |  | 20 | 21 | 0.00085435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1372-49_0_4_line_22 |  | 21 | 28 | 0.018047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1372-49_0_4_line_23 |  | 22 | 29 | 0.021851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1372-49_0_4_line_24 |  | 22 | 23 | 0.040645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1372-49_0_4_line_25 |  | 23 | 24 | 0.055043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1372-49_0_4_line_26 |  | 24 | 55 | 0.032142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1372-49_0_4_line_27 |  | 25 | 26 | 0.016459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1372-49_0_4_line_28 |  | 25 | 27 | 0.028125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1372-49_0_4_line_29 |  | 26 | 28 | 0.011658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1372-49_0_4_line_30 |  | 30 | 31 | 0.025915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1372-49_0_4_line_31 |  | 30 | 32 | 0.024476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1372-49_0_4_line_32 |  | 31 | 33 | 0.0063416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1372-49_0_4_line_33 |  | 32 | 34 | 0.018465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1372-49_0_4_line_34 |  | 32 | 35 | 0.029992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1372-49_0_4_line_35 |  | 33 | 36 | 0.015373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1372-49_0_4_line_36 |  | 34 | 37 | 0.035121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1372-49_0_4_line_37 |  | 34 | 38 | 0.030299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1372-49_0_4_line_38 |  | 35 | 39 | 0.00039895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1372-49_0_4_line_39 |  | 36 | 40 | 0.018633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1372-49_0_4_line_40 |  | 38 | 41 | 0.01115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1372-49_0_4_line_41 |  | 39 | 42 | 0.027414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1372-49_0_4_line_42 |  | 40 | 43 | 0.021184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1372-49_0_4_line_43 |  | 40 | 44 | 0.043574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_1372-49_0_4_line_44 |  | 41 | 51 | 0.016096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1372-49_0_4_line_45 |  | 41 | 52 | 0.02543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1372-49_0_4_line_46 |  | 42 | 47 | 0.02553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_1372-49_0_4_line_47 |  | 43 | 45 | 0.021156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1372-49_0_4_line_48 |  | 44 | 46 | 0.019951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_1372-49_0_4_line_49 |  | 45 | 80 | 0.00062475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1372-49_0_4_line_50 |  | 46 | 85 | 0.0062567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_1372-49_0_4_line_51 |  | 47 | 48 | 0.04 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1372-49_0_4_line_52 |  | 48 | 49 | 0.029757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1372-49_0_4_line_53 |  | 49 | 50 | 0.010282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1372-49_0_4_line_54 |  | 50 | 117 | 0.015206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1372-49_0_4_line_55 |  | 50 | 121 | 0.029844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1372-49_0_4_line_56 |  | 51 | 53 | 0.024321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1372-49_0_4_line_57 |  | 52 | 54 | 0.026943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1372-49_0_4_line_58 |  | 53 | 55 | 0.005604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1372-49_0_4_line_59 |  | 53 | 56 | 0.014613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1372-49_0_4_line_60 |  | 54 | 57 | 0.029636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1372-49_0_4_line_61 |  | 55 | 58 | 0.021237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1372-49_0_4_line_62 |  | 56 | 59 | 0.047333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1372-49_0_4_line_63 |  | 57 | 70 | 0.030354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1372-49_0_4_line_64 |  | 58 | 60 | 0.0038282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1372-49_0_4_line_65 |  | 59 | 61 | 0.026207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1372-49_0_4_line_66 |  | 60 | 64 | 0.025954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1372-49_0_4_line_67 |  | 61 | 62 | 0.0016336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1372-49_0_4_line_68 |  | 62 | 63 | 0.0096458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1372-49_0_4_line_69 |  | 63 | 72 | 0.013333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1372-49_0_4_line_70 |  | 64 | 65 | 0.0069218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1372-49_0_4_line_71 |  | 65 | 66 | 0.017457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1372-49_0_4_line_72 |  | 66 | 67 | 0.022169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1372-49_0_4_line_73 |  | 67 | 68 | 0.000693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1372-49_0_4_line_74 |  | 68 | 69 | 0.009187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1372-49_0_4_line_75 |  | 70 | 71 | 0.0084291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1372-49_0_4_line_76 |  | 71 | 124 | 0.017475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1372-49_0_4_line_77 |  | 72 | 73 | 0.024663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1372-49_0_4_line_78 |  | 73 | 74 | 0.0069516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1372-49_0_4_line_79 |  | 74 | 75 | 0.0082098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1372-49_0_4_line_80 |  | 76 | 77 | 0.021078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1372-49_0_4_line_81 |  | 76 | 78 | 0.068045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1372-49_0_4_line_82 |  | 78 | 79 | 0.020441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1372-49_0_4_line_83 |  | 79 | 81 | 0.0032498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1372-49_0_4_line_84 |  | 81 | 82 | 0.022621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_1372-49_0_4_line_85 |  | 81 | 83 | 0.02968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_1372-49_0_4_line_86 |  | 82 | 84 | 0.00040097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1372-49_0_4_line_87 |  | 83 | 85 | 0.017724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1372-49_0_4_line_88 |  | 84 | 86 | 0.020119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1372-49_0_4_line_89 |  | 85 | 87 | 0.013908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1372-49_0_4_line_90 |  | 86 | 88 | 0.011333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1372-49_0_4_line_91 |  | 87 | 94 | 0.020171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1372-49_0_4_line_92 |  | 88 | 89 | 0.030049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1372-49_0_4_line_93 |  | 89 | 90 | 0.01358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1372-49_0_4_line_94 |  | 89 | 91 | 0.0021694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1372-49_0_4_line_95 |  | 90 | 92 | 0.00011144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1372-49_0_4_line_96 |  | 91 | 93 | 0.013346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1372-49_0_4_line_97 |  | 93 | 95 | 0.020508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1372-49_0_4_line_98 |  | 95 | 99 | 0.0091856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1372-49_0_4_line_99 |  | 96 | 97 | 0.0016443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1372-49_0_4_line_100 |  | 97 | 98 | 0.03216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1372-49_0_4_line_101 |  | 98 | 108 | 0.0063073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1372-49_0_4_line_102 |  | 99 | 103 | 0.0099466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1372-49_0_4_line_103 |  | 99 | 104 | 0.012823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1372-49_0_4_line_104 |  | 100 | 101 | 0.019576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1372-49_0_4_line_105 |  | 100 | 102 | 0.01709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1372-49_0_4_line_106 |  | 101 | 106 | 0.038033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1372-49_0_4_line_107 |  | 102 | 115 | 0.024444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1372-49_0_4_line_108 |  | 104 | 105 | 0.0014158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1372-49_0_4_line_109 |  | 105 | 107 | 0.011088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1372-49_0_4_line_110 |  | 106 | 118 | 0.025482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1372-49_0_4_line_111 |  | 107 | 108 | 0.038118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1372-49_0_4_line_112 |  | 109 | 110 | 0.031883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1372-49_0_4_line_113 |  | 110 | 111 | 0.023893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1372-49_0_4_line_114 |  | 111 | 112 | 0.021129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1372-49_0_4_line_115 |  | 112 | 113 | 0.02687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1372-49_0_4_line_116 |  | 113 | 114 | 0.050635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1372-49_0_4_line_117 |  | 114 | 115 | 0.0078609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1372-49_0_4_line_118 |  | 114 | 116 | 0.0057219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1372-49_0_4_line_119 |  | 116 | 117 | 0.031629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1372-49_0_4_line_120 |  | 119 | 120 | 0.034983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1372-49_0_4_line_121 |  | 120 | 121 | 0.022033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1372-49_0_4_line_122 |  | 122 | 123 | 0.017573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1372-49_0_4_line_123 |  | 122 | 124 | 0.010694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1372-49_0_4_trafo_27 | 0.63 MVA 20/0.4 kV | 125 | 47 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2691785.039 | 1208882.5138 | 2691799.3913 | 1208879.3716
1 | 2691808.7381 | 1208882.662 | 2691799.3913 | 1208879.3716
2 | 2691808.7381 | 1208882.662 | 2691798.8022 | 1208894.33
3 | 2691808.7381 | 1208882.662 | 2691827.6723 | 1208860.7478
4 | 2691789.0275 | 1208905.8089 | 2691798.8022 | 1208894.33
5 | 2691737.5615 | 1208918.3984 | 2691719.7258 | 1208933.233
6 | 2691707.7345 | 1208943.0999 | 2691714.9288 | 1208937.2229 | 2691719.7258 | 1208933.233
7 | 2691689.3941 | 1208957.9544 | 2691701.3157 | 1208948.3433 | 2691707.7345 | 1208943.0999
8 | 2691685.3347 | 1208961.2271 | 2691689.3941 | 1208957.9544
9 | 2691789.0275 | 1208905.8089 | 2691788.5871 | 1208906.3261
10 | 2691735.6528 | 1209290.2663 | 2691742.4725 | 1209287.2914 | 2691757.6068 | 1209271.9338
11 | 2691735.6528 | 1209290.2663 | 2691757.9705 | 1209300.0584
12 | 2691735.6528 | 1209290.2663 | 2691710.9997 | 1209301.0169 | 2691684.7486 | 1209309.6484
13 | 2691632.6882 | 1209325.6193 | 2691636.6668 | 1209325.4581 | 2691684.7486 | 1209309.6484
14 | 2691684.483 | 1209144.1823 | 2691670.7595 | 1209187.4525
15 | 2691670.7595 | 1209187.4525 | 2691642.6759 | 1209276.1729
16 | 2691684.483 | 1209144.1823 | 2691680.9387 | 1209143.2828 | 2691656.9552 | 1209134.175 | 2691645.1552 | 1209131.7367
17 | 2691632.4253 | 1209309.1722 | 2691642.6759 | 1209276.1729
18 | 2691632.6882 | 1209325.6193 | 2691627.2491 | 1209325.836
19 | 2691627.2491 | 1209325.836 | 2691632.4253 | 1209309.1722
20 | 2691627.2491 | 1209325.836 | 2691620.461 | 1209324.7866 | 2691612.1604 | 1209325.1928 | 2691605.5986 | 1209329.2059 | 2691596.9819 | 1209341.0182
21 | 2691596.9819 | 1209341.0182 | 2691596.4784 | 1209341.7084
22 | 2691587.5947 | 1209357.3623 | 2691593.3749 | 1209345.9628 | 2691596.4784 | 1209341.7084
23 | 2691624.4904 | 1209137.7123 | 2691633.7157 | 1209133.0508 | 2691645.1552 | 1209131.7367
24 | 2691672.5348 | 1209101.6965 | 2691645.1552 | 1209131.7367
25 | 2691706.8739 | 1209074.9022 | 2691702.2725 | 1209073.5306 | 2691699.0736 | 1209075.3827 | 2691696.2834 | 1209082.8004 | 2691691.5759 | 1209097.2266 | 2691688.0792 | 1209100.6529 | 2691680.9829 | 1209103.8127 | 2691675.5526 | 1209105.4192 | 2691673.4419 | 1209104.2416 | 2691672.5348 | 1209101.6965
26 | 2691716.8547 | 1209044.3574 | 2691712.3419 | 1209056.9965 | 2691709.3804 | 1209067.1467 | 2691706.8739 | 1209074.9022
27 | 2691574.8786 | 1209382.4401 | 2691582.3223 | 1209367.7602
28 | 2691564.5696 | 1209408.5735 | 2691572.2622 | 1209387.6 | 2691574.8786 | 1209382.4401
29 | 2691587.5947 | 1209357.3623 | 2691582.3223 | 1209367.7602
30 | 2691622.2657 | 1208987.2648 | 2691614.1454 | 1208984.6178 | 2691600.6775 | 1208976.4056 | 2691599.4824 | 1208975.342
31 | 2691644.5123 | 1208995.9471 | 2691639.8565 | 1208991.6728 | 2691627.8911 | 1208989.0985 | 2691622.2657 | 1208987.2648
32 | 2691594.7451 | 1208971.1259 | 2691599.4824 | 1208975.342
33 | 2691644.5123 | 1208995.9471 | 2691651.0893 | 1208989.9775 | 2691658.2733 | 1208983.5946
34 | 2691644.5123 | 1208995.9471 | 2691621.523 | 1209015.2087
35 | 2691583.2614 | 1208960.9057 | 2691594.7451 | 1208971.1259
36 | 2691658.2733 | 1208983.5946 | 2691666.5065 | 1208976.2273 | 2691677.9434 | 1208967.1858 | 2691685.3347 | 1208961.2271
37 | 2691658.2733 | 1208983.5946 | 2691680.0411 | 1209004.6708
38 | 2691621.523 | 1209015.2087 | 2691621.2172 | 1209015.465
39 | 2691583.2614 | 1208960.9057 | 2691575.529 | 1208967.3581 | 2691569.2317 | 1208973.1595
40 | 2691688.0518 | 1209012.4268 | 2691680.0411 | 1209004.6708
41 | 2691621.2172 | 1209015.465 | 2691612.0251 | 1209023.1666 | 2691599.8011 | 1209032.5692
42 | 2691553.4156 | 1208987.2416 | 2691558.3158 | 1208983.2157 | 2691569.2317 | 1208973.1595
43 | 2691569.2317 | 1208973.1595 | 2691533.973 | 1208947.5563
44 | 2691688.0518 | 1209012.4268 | 2691700.1789 | 1209023.01
45 | 2691688.0518 | 1209012.4268 | 2691668.0012 | 1209028.0686
46 | 2691579.5652 | 1209048.1345 | 2691599.8011 | 1209032.5692
47 | 2691553.4156 | 1208987.2416 | 2691537.0695 | 1209000.6715
48 | 2691518.0724 | 1208959.6074 | 2691533.973 | 1208947.5563
49 | 2691536.5868 | 1209001.0681 | 2691537.0695 | 1209000.6715
50 | 2691513.0861 | 1208963.3866 | 2691518.0724 | 1208959.6074
51 | 2691547.8599 | 1209072.5219 | 2691579.5652 | 1209048.1345
52 | 2691524.2735 | 1209090.6644 | 2691547.8599 | 1209072.5219
53 | 2691516.1233 | 1209096.9335 | 2691524.2735 | 1209090.6644
54 | 2691516.1233 | 1209096.9335 | 2691504.6699 | 1209106.9361
55 | 2691516.1233 | 1209096.9335 | 2691518.4581 | 1209099.8601 | 2691519.6304 | 1209104.2254 | 2691518.5253 | 1209112.325 | 2691515.8278 | 1209122.635 | 2691514.5774 | 1209125.0832
56 | 2691718.5033 | 1209039.0014 | 2691700.1789 | 1209023.01
57 | 2691668.0012 | 1209028.0686 | 2691646.758 | 1209044.6407
58 | 2691718.5033 | 1209039.0014 | 2691716.8547 | 1209044.3574
59 | 2691718.5033 | 1209039.0014 | 2691722.5786 | 1209024.9687
60 | 2691623.3708 | 1209062.8418 | 2691624.4978 | 1209062.0062 | 2691646.758 | 1209044.6407
61 | 2691716.8547 | 1209044.3574 | 2691735.1675 | 1209049.4645 | 2691737.3389 | 1209049.9512
62 | 2691722.5786 | 1209024.9687 | 2691727.4465 | 1209008.2071 | 2691732.3367 | 1208991.7935 | 2691736.8628 | 1208979.8713
63 | 2691598.9886 | 1209080.9209 | 2691623.3708 | 1209062.8418
64 | 2691737.3389 | 1209049.9512 | 2691741.0744 | 1209050.7885
65 | 2691736.8628 | 1208979.8713 | 2691743.042 | 1208963.5948 | 2691748.1563 | 1208956.4366
66 | 2691766.7953 | 1209051.9309 | 2691763.0725 | 1209052.262 | 2691749.6012 | 1209052.6996 | 2691741.0744 | 1209050.7885
67 | 2691748.1563 | 1208956.4366 | 2691749.106 | 1208955.1074
68 | 2691754.7134 | 1208947.259 | 2691749.106 | 1208955.1074
69 | 2691762.7676 | 1208936.6471 | 2691759.8335 | 1208940.0928 | 2691754.7134 | 1208947.259
70 | 2691773.6899 | 1209051.3178 | 2691766.7953 | 1209051.9309
71 | 2691773.6899 | 1209051.3178 | 2691783.2173 | 1209050.4706 | 2691790.9596 | 1209052.0004
72 | 2691812.1892 | 1209058.17 | 2691800.0596 | 1209053.7985 | 2691790.9596 | 1209052.0004
73 | 2691812.1892 | 1209058.17 | 2691812.8412 | 1209058.4049
74 | 2691821.484 | 1209061.5198 | 2691812.8412 | 1209058.4049
75 | 2691592.2177 | 1209085.9414 | 2691598.9886 | 1209080.9209
76 | 2691592.2177 | 1209085.9414 | 2691578.1807 | 1209096.3497
77 | 2691762.7676 | 1208936.6471 | 2691778.7576 | 1208917.8694
78 | 2691778.7576 | 1208917.8694 | 2691783.2645 | 1208912.5767
79 | 2691788.5871 | 1208906.3261 | 2691783.2645 | 1208912.5767
80 | 2691412.4389 | 1208868.7265 | 2691415.6692 | 1208871.6324 | 2691428.76 | 1208882.0549
81 | 2691488.1646 | 1208915.239 | 2691428.76 | 1208882.0549
82 | 2691488.1646 | 1208915.239 | 2691477.6489 | 1208932.7679
83 | 2691475.9771 | 1208935.5547 | 2691477.6489 | 1208932.7679
84 | 2691475.9771 | 1208935.5547 | 2691464.2803 | 1208954.917
85 | 2691475.9771 | 1208935.5547 | 2691481.9417 | 1208940.2603 | 2691487.1651 | 1208946.1999 | 2691500.0917 | 1208952.0112
86 | 2691464.2803 | 1208954.917 | 2691464.0729 | 1208955.2603
87 | 2691513.0861 | 1208963.3866 | 2691506.0877 | 1208954.7068 | 2691500.0917 | 1208952.0112
88 | 2691453.6699 | 1208972.4809 | 2691464.0729 | 1208955.2603
89 | 2691513.0861 | 1208963.3866 | 2691502.0942 | 1208971.9079
90 | 2691453.6699 | 1208972.4809 | 2691447.8097 | 1208982.1816
91 | 2691502.0942 | 1208971.9079 | 2691486.1525 | 1208984.2665
92 | 2691427.9698 | 1209004.6319 | 2691441.2946 | 1208990.9491 | 2691445.803 | 1208985.5034 | 2691447.8097 | 1208982.1816
93 | 2691427.9698 | 1209004.6319 | 2691437.6219 | 1209014.1842
94 | 2691427.9698 | 1209004.6319 | 2691426.456 | 1209006.1858
95 | 2691437.7011 | 1209014.2626 | 2691437.6219 | 1209014.1842
96 | 2691426.456 | 1209006.1858 | 2691417.1433 | 1209015.7454
97 | 2691417.1433 | 1209015.7454 | 2691402.833 | 1209030.4352
98 | 2691396.4234 | 1209037.0148 | 2691402.833 | 1209030.4352
99 | 2691473.571 | 1209052.8414 | 2691472.3005 | 1209053.8853
100 | 2691447.4517 | 1209074.3009 | 2691472.3005 | 1209053.8853
101 | 2691442.5783 | 1209078.3049 | 2691447.4517 | 1209074.3009
102 | 2691396.4234 | 1209037.0148 | 2691389.4518 | 1209044.1092
103 | 2691396.4234 | 1209037.0148 | 2691405.9926 | 1209045.5503
104 | 2691410.9185 | 1209127.4258 | 2691429.7287 | 1209122.0039
105 | 2691446.7587 | 1209122.9229 | 2691438.7845 | 1209121.9426 | 2691429.7287 | 1209122.0039 | 2691429.7287 | 1209122.0039
106 | 2691375.1371 | 1209140.0884 | 2691391.4547 | 1209133.0361 | 2691410.9185 | 1209127.4258
107 | 2691446.7587 | 1209122.9229 | 2691471.0202 | 1209125.9058
108 | 2691407.0491 | 1209046.4927 | 2691405.9926 | 1209045.5503
109 | 2691412.4101 | 1209055.0049 | 2691412.7591 | 1209051.5858 | 2691407.0491 | 1209046.4927
110 | 2691351.4409 | 1209149.4309 | 2691364.5224 | 1209144.676 | 2691375.1371 | 1209140.0884
111 | 2691412.4101 | 1209055.0049 | 2691442.5783 | 1209078.3049
112 | 2691357.4873 | 1209229.8032 | 2691382.26 | 1209209.7318
113 | 2691382.26 | 1209209.7318 | 2691400.8242 | 1209194.6907
114 | 2691400.8242 | 1209194.6907 | 2691417.2412 | 1209181.3892
115 | 2691417.2412 | 1209181.3892 | 2691438.1188 | 1209164.4737
116 | 2691476.5376 | 1209131.5052 | 2691470.2171 | 1209136.634 | 2691444.4915 | 1209159.3105 | 2691438.1188 | 1209164.4737
117 | 2691476.5376 | 1209131.5052 | 2691471.0202 | 1209125.9058
118 | 2691476.5376 | 1209131.5052 | 2691480.8473 | 1209127.7414
119 | 2691480.8473 | 1209127.7414 | 2691504.6699 | 1209106.9361
120 | 2691508.3036 | 1209173.1143 | 2691496.3258 | 1209158.8713 | 2691504.2058 | 1209144.5193
121 | 2691504.2058 | 1209144.5193 | 2691510.5762 | 1209132.9169 | 2691514.5774 | 1209125.0832
122 | 2691569.5903 | 1209102.7194 | 2691568.8348 | 1209103.2795 | 2691554.9731 | 1209112.471
123 | 2691569.5903 | 1209102.7194 | 2691578.1807 | 1209096.3497

## bus_geodata
| x | y | coords
0 | 2691785.039 | 1208882.5138
1 | 2691799.3913 | 1208879.3716
2 | 2691808.7381 | 1208882.662
3 | 2691798.8022 | 1208894.33
4 | 2691827.6723 | 1208860.7478
5 | 2691737.5615 | 1208918.3984
6 | 2691719.7258 | 1208933.233
7 | 2691707.7345 | 1208943.0999
8 | 2691689.3941 | 1208957.9544
9 | 2691789.0275 | 1208905.8089
10 | 2691757.6068 | 1209271.9338
11 | 2691735.6528 | 1209290.2663
12 | 2691757.9705 | 1209300.0584
13 | 2691684.7486 | 1209309.6484
14 | 2691670.7595 | 1209187.4525
15 | 2691684.483 | 1209144.1823
16 | 2691642.6759 | 1209276.1729
17 | 2691632.6882 | 1209325.6193
18 | 2691627.2491 | 1209325.836
19 | 2691632.4253 | 1209309.1722
20 | 2691596.9819 | 1209341.0182
21 | 2691596.4784 | 1209341.7084
22 | 2691645.1552 | 1209131.7367
23 | 2691672.5348 | 1209101.6965
24 | 2691706.8739 | 1209074.9022
25 | 2691574.8786 | 1209382.4401
26 | 2691582.3223 | 1209367.7602
27 | 2691564.5696 | 1209408.5735
28 | 2691587.5947 | 1209357.3623
29 | 2691624.4904 | 1209137.7123
30 | 2691622.2657 | 1208987.2648
31 | 2691599.4824 | 1208975.342
32 | 2691644.5123 | 1208995.9471
33 | 2691594.7451 | 1208971.1259
34 | 2691658.2733 | 1208983.5946
35 | 2691621.523 | 1209015.2087
36 | 2691583.2614 | 1208960.9057
37 | 2691685.3347 | 1208961.2271
38 | 2691680.0411 | 1209004.6708
39 | 2691621.2172 | 1209015.465
40 | 2691569.2317 | 1208973.1595
41 | 2691688.0518 | 1209012.4268
42 | 2691599.8011 | 1209032.5692
43 | 2691553.4156 | 1208987.2416
44 | 2691533.973 | 1208947.5563
45 | 2691537.0695 | 1209000.6715
46 | 2691518.0724 | 1208959.6074
47 | 2691579.5652 | 1209048.1345
48 | 2691547.8599 | 1209072.5219
49 | 2691524.2735 | 1209090.6644
50 | 2691516.1233 | 1209096.9335
51 | 2691700.1789 | 1209023.01
52 | 2691668.0012 | 1209028.0686
53 | 2691718.5033 | 1209039.0014
54 | 2691646.758 | 1209044.6407
55 | 2691716.8547 | 1209044.3574
56 | 2691722.5786 | 1209024.9687
57 | 2691623.3708 | 1209062.8418
58 | 2691737.3389 | 1209049.9512
59 | 2691736.8628 | 1208979.8713
60 | 2691741.0744 | 1209050.7885
61 | 2691748.1563 | 1208956.4366
62 | 2691749.106 | 1208955.1074
63 | 2691754.7134 | 1208947.259
64 | 2691766.7953 | 1209051.9309
65 | 2691773.6899 | 1209051.3178
66 | 2691790.9596 | 1209052.0004
67 | 2691812.1892 | 1209058.17
68 | 2691812.8412 | 1209058.4049
69 | 2691821.484 | 1209061.5198
70 | 2691598.9886 | 1209080.9209
71 | 2691592.2177 | 1209085.9414
72 | 2691762.7676 | 1208936.6471
73 | 2691778.7576 | 1208917.8694
74 | 2691783.2645 | 1208912.5767
75 | 2691788.5871 | 1208906.3261
76 | 2691428.76 | 1208882.0549
77 | 2691412.4389 | 1208868.7265
78 | 2691488.1646 | 1208915.239
79 | 2691477.6489 | 1208932.7679
80 | 2691536.5868 | 1209001.0681
81 | 2691475.9771 | 1208935.5547
82 | 2691464.2803 | 1208954.917
83 | 2691500.0917 | 1208952.0112
84 | 2691464.0729 | 1208955.2603
85 | 2691513.0861 | 1208963.3866
86 | 2691453.6699 | 1208972.4809
87 | 2691502.0942 | 1208971.9079
88 | 2691447.8097 | 1208982.1816
89 | 2691427.9698 | 1209004.6319
90 | 2691437.6219 | 1209014.1842
91 | 2691426.456 | 1209006.1858
92 | 2691437.7011 | 1209014.2626
93 | 2691417.1433 | 1209015.7454
94 | 2691486.1525 | 1208984.2665
95 | 2691402.833 | 1209030.4352
96 | 2691473.571 | 1209052.8414
97 | 2691472.3005 | 1209053.8853
98 | 2691447.4517 | 1209074.3009
99 | 2691396.4234 | 1209037.0148
100 | 2691429.7287 | 1209122.0039
101 | 2691410.9185 | 1209127.4258
102 | 2691446.7587 | 1209122.9229
103 | 2691389.4518 | 1209044.1092
104 | 2691405.9926 | 1209045.5503
105 | 2691407.0491 | 1209046.4927
106 | 2691375.1371 | 1209140.0884
107 | 2691412.4101 | 1209055.0049
108 | 2691442.5783 | 1209078.3049
109 | 2691357.4873 | 1209229.8032
110 | 2691382.26 | 1209209.7318
111 | 2691400.8242 | 1209194.6907
112 | 2691417.2412 | 1209181.3892
113 | 2691438.1188 | 1209164.4738
114 | 2691476.5376 | 1209131.5052
115 | 2691471.0202 | 1209125.9058
116 | 2691480.8473 | 1209127.7414
117 | 2691504.6699 | 1209106.9361
118 | 2691351.4409 | 1209149.4309
119 | 2691508.3036 | 1209173.1143
120 | 2691504.2058 | 1209144.5193
121 | 2691514.5774 | 1209125.0832
122 | 2691569.5903 | 1209102.7194
123 | 2691554.9731 | 1209112.471
124 | 2691578.1807 | 1209096.3497
125 | 2691516.1233 | 1209096.9335

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98027 | -0.37905 | 0.0013363 | 0.0003349
1 | 0.98029 | -0.37869 | 0.0015026 | 0.00037659
2 | 0.98032 | -0.37818 | 0 | 0
3 | 0.9804 | -0.37659 | 0.0041353 | 0.0010364
4 | 0.98024 | -0.3797 | 0.0028824 | 0.00072239
5 | 0.98904 | -0.20885 | 0.0032971 | 0.00082632
6 | 0.98911 | -0.20749 | 0.002098 | 0.0005258
7 | 0.98919 | -0.20599 | 0.0041243 | 0.0010336
8 | 0.9894 | -0.20199 | 0.0065998 | 0.0016541
9 | 0.98054 | -0.3739 | 0.0014318 | 0.00035883
10 | 0.97211 | -0.53864 | 0.0043606 | 0.0010929
11 | 0.97223 | -0.53631 | 0 | 0
12 | 0.97215 | -0.5379 | 0.0035402 | 0.00088726
13 | 0.97263 | -0.52837 | 0.0035383 | 0.00088678
14 | 0.97714 | -0.43977 | 0.0012622 | 0.00031633
15 | 0.97844 | -0.41436 | 0 | 0
16 | 0.97458 | -0.48991 | 0.0018279 | 0.00045811
17 | 0.97322 | -0.51686 | 0 | 0
18 | 0.97327 | -0.51572 | 0 | 0
19 | 0.97369 | -0.50744 | 0.001797 | 0.00045038
20 | 0.97277 | -0.52564 | 0.0039198 | 0.00098238
21 | 0.97276 | -0.5258 | 0.0011405 | 0.00028584
22 | 0.97962 | -0.39127 | 0.0015789 | 0.0003957
23 | 0.98102 | -0.36398 | 0.0016194 | 0.00040586
24 | 0.983 | -0.32555 | 0 | 0
25 | 0.97243 | -0.53242 | 0.0031766 | 0.00079613
26 | 0.97251 | -0.53074 | 0.0030441 | 0.00076293
27 | 0.97237 | -0.53364 | 0.0023563 | 0.00059055
28 | 0.97261 | -0.52889 | 0.00072661 | 0.00018211
29 | 0.97952 | -0.39314 | 0.0047256 | 0.0011844
30 | 0.98971 | -0.19584 | 0.0039845 | 0.00099861
31 | 0.98832 | -0.22244 | 0.0052204 | 0.0013083
32 | 0.99104 | -0.1702 | 0 | 0
33 | 0.98799 | -0.22877 | 0.0038153 | 0.00095619
34 | 0.99009 | -0.18844 | 0 | 0
35 | 0.99422 | -0.10941 | 0.0027907 | 0.00069941
36 | 0.98721 | -0.24377 | 0 | 0
37 | 0.98947 | -0.2005 | 0.0031692 | 0.00079428
38 | 0.98872 | -0.21498 | 0.0054839 | 0.0013744
39 | 0.99427 | -0.1086 | 0.0028873 | 0.00072362
40 | 0.98627 | -0.26198 | 0.0039131 | 0.00098073
41 | 0.98798 | -0.22912 | 0 | 0
42 | 0.99722 | -0.05247 | 0.0033557 | 0.00084101
43 | 0.986 | -0.26734 | 0.0048558 | 0.001217
44 | 0.98431 | -0.30001 | 0.0042137 | 0.001056
45 | 0.98582 | -0.27084 | 0.0046465 | 0.0011645
46 | 0.98343 | -0.31696 | 0.0042147 | 0.0010563
47 | 1 | 0 | -0.42196 | -0.10786
48 | 0.99777 | -0.042676 | 0.0046291 | 0.0011602
49 | 0.99624 | -0.072128 | 0.0041276 | 0.0010345
50 | 0.99575 | -0.08158 | 0 | 0
51 | 0.98654 | -0.25706 | 0.0040884 | 0.0010246
52 | 0.98693 | -0.24958 | 0.0077301 | 0.0019373
53 | 0.98444 | -0.29766 | 0 | 0
54 | 0.986 | -0.26756 | 0.0025736 | 0.000645
55 | 0.98415 | -0.30318 | 0 | 0
56 | 0.98392 | -0.30772 | 0.0033837 | 0.00084803
57 | 0.98506 | -0.28602 | 0.0047679 | 0.0011949
58 | 0.98384 | -0.30933 | 0.0030341 | 0.00076043
59 | 0.9824 | -0.33749 | 0.006083 | 0.0015245
60 | 0.98379 | -0.31023 | 0.0011413 | 0.00028603
61 | 0.9817 | -0.35112 | 0.0016827 | 0.00042173
62 | 0.98166 | -0.35193 | 0.0010987 | 0.00027536
63 | 0.98143 | -0.35646 | 0.0046929 | 0.0011761
64 | 0.98351 | -0.31581 | 0.00335 | 0.00083958
65 | 0.98345 | -0.31688 | 0.0038436 | 0.00096328
66 | 0.98338 | -0.31837 | 0.0015535 | 0.00038934
67 | 0.98331 | -0.31964 | 0.0015178 | 0.0003804
68 | 0.98331 | -0.31966 | 0.00074258 | 0.00018611
69 | 0.9833 | -0.31982 | 0.00091955 | 0.00023046
70 | 0.98422 | -0.30235 | 0.0035481 | 0.00088923
71 | 0.98401 | -0.30635 | 0.0039594 | 0.00099233
72 | 0.98116 | -0.36161 | 0.0027912 | 0.00069955
73 | 0.98074 | -0.36989 | 0.0023467 | 0.00058814
74 | 0.98064 | -0.37192 | 0.0038645 | 0.00096852
75 | 0.98054 | -0.37376 | 0.0010236 | 0.00025653
76 | 0.98068 | -0.37053 | 0.0079822 | 0.0020005
77 | 0.98068 | -0.37061 | 0.00021477 | 5.3827e-05
78 | 0.9812 | -0.36042 | 0 | 0
79 | 0.98135 | -0.35739 | 0.009255 | 0.0023195
80 | 0.98581 | -0.27089 | 0.0045957 | 0.0011518
81 | 0.9814 | -0.35636 | 0 | 0
82 | 0.98038 | -0.37636 | 0.0068046 | 0.0017054
83 | 0.98246 | -0.33579 | 0.013169 | 0.0033004
84 | 0.98034 | -0.37702 | 0.010191 | 0.0025542
85 | 0.98317 | -0.32212 | 0 | 0
86 | 0.97883 | -0.40646 | 0.0061102 | 0.0015313
87 | 0.98305 | -0.32442 | 0.0042134 | 0.001056
88 | 0.97805 | -0.42183 | 0.0051312 | 0.001286
89 | 0.97611 | -0.45986 | 0 | 0
90 | 0.97601 | -0.46186 | 0.0044546 | 0.0011164
91 | 0.97598 | -0.4623 | 0.0041892 | 0.0010499
92 | 0.976 | -0.46187 | 0.0035967 | 0.00090141
93 | 0.97527 | -0.47625 | 0.0038371 | 0.00096166
94 | 0.98296 | -0.32622 | 0.0049512 | 0.0012409
95 | 0.97425 | -0.49628 | 0.0057058 | 0.00143
96 | 0.97148 | -0.55098 | 0.0054597 | 0.0013683
97 | 0.97149 | -0.55082 | 0.004873 | 0.0012213
98 | 0.9718 | -0.54468 | 0.011858 | 0.0029718
99 | 0.97385 | -0.50431 | 0 | 0
100 | 0.99398 | -0.11573 | 0.0010327 | 0.00025883
101 | 0.99384 | -0.11854 | 0.0010262 | 0.0002572
102 | 0.99413 | -0.11296 | 0.001946 | 0.00048771
103 | 0.97379 | -0.50535 | 0.0056809 | 0.0014238
104 | 0.97335 | -0.51418 | 0.004274 | 0.0010712
105 | 0.9733 | -0.51516 | 0.0046141 | 0.0011564
106 | 0.99359 | -0.12331 | 0.0049187 | 0.0012327
107 | 0.97296 | -0.52189 | 0.0042139 | 0.0010561
108 | 0.97193 | -0.5421 | 0.0065731 | 0.0016474
109 | 0.99342 | -0.12657 | 0.0016471 | 0.0004128
110 | 0.99347 | -0.12565 | 0.0038379 | 0.00096188
111 | 0.99359 | -0.12333 | 0.0022594 | 0.00056626
112 | 0.99374 | -0.12044 | 0.001336 | 0.00033483
113 | 0.99396 | -0.11614 | 0.0018442 | 0.0004622
114 | 0.99447 | -0.10638 | 0 | 0
115 | 0.99437 | -0.10817 | 0.0018271 | 0.00045792
116 | 0.99459 | -0.10397 | 0.0012534 | 0.00031414
117 | 0.99532 | -0.089976 | 0.0062681 | 0.0015709
118 | 0.99354 | -0.1243 | 0.0021905 | 0.00054899
119 | 0.99461 | -0.10369 | 0.0070395 | 0.0017643
120 | 0.99483 | -0.099347 | 0.010457 | 0.0026207
121 | 0.99518 | -0.09256 | 0.0034204 | 0.00085724
122 | 0.98348 | -0.3167 | 0.010466 | 0.0026231
123 | 0.98338 | -0.31879 | 0.0065973 | 0.0016534
124 | 0.98365 | -0.31341 | 0.0053593 | 0.0013432
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0013363 | -0.0003349 | 0.0013363 | 0.00033473 | 2.2668e-08 | -1.7072e-07 | 0.0020284 | 0.0020283 | 0.0020284 | 0.98027 | -0.37905 | 0.98029 | -0.37869 | 0.55725
1 | -0.0028389 | -0.00071132 | 0.002839 | 0.00071124 | 6.9001e-08 | -8.0769e-08 | 0.0043092 | 0.0043092 | 0.0043092 | 0.98029 | -0.37869 | 0.98032 | -0.37818 | 1.1839
2 | -0.0057216 | -0.0014334 | 0.005722 | 0.0014335 | 4.3344e-07 | 8.4162e-08 | 0.0086845 | 0.0086844 | 0.0086845 | 0.98032 | -0.37818 | 0.9804 | -0.37659 | 2.3858
3 | 0.0028826 | 0.00072215 | -0.0028824 | -0.00072239 | 2.0791e-07 | -2.3205e-07 | 0.0043753 | 0.0043754 | 0.0043754 | 0.98032 | -0.37818 | 0.98024 | -0.3797 | 1.202
4 | -0.0098573 | -0.0024699 | 0.0098586 | 0.0024705 | 1.2655e-06 | 6.1976e-07 | 0.014961 | 0.014961 | 0.014961 | 0.9804 | -0.37659 | 0.98054 | -0.3739 | 4.1101
5 | -0.0032971 | -0.00082632 | 0.0032973 | 0.00082616 | 2.1405e-07 | -1.6074e-07 | 0.0049604 | 0.0049603 | 0.0049604 | 0.98904 | -0.20885 | 0.98911 | -0.20749 | 1.3628
6 | -0.0053953 | -0.001352 | 0.0053956 | 0.001352 | 3.8363e-07 | 4.6189e-08 | 0.0081165 | 0.0081164 | 0.0081165 | 0.98911 | -0.20749 | 0.98919 | -0.20599 | 2.2298
7 | -0.0095199 | -0.0023856 | 0.0095217 | 0.0023865 | 1.815e-06 | 8.5858e-07 | 0.01432 | 0.01432 | 0.01432 | 0.98919 | -0.20599 | 0.9894 | -0.20199 | 3.9342
8 | -0.016121 | -0.0040406 | 0.016123 | 0.0040412 | 1.1495e-06 | 6.6873e-07 | 0.024246 | 0.024246 | 0.024246 | 0.9894 | -0.20199 | 0.98947 | -0.2005 | 6.661
9 | -0.01129 | -0.0028293 | 0.01129 | 0.0028294 | 7.4782e-08 | 3.9292e-08 | 0.017134 | 0.017134 | 0.017134 | 0.98054 | -0.3739 | 0.98054 | -0.37376 | 4.707
10 | -0.0043606 | -0.0010929 | 0.0043611 | 0.0010928 | 4.8454e-07 | -4.9498e-08 | 0.0066748 | 0.0066747 | 0.0066748 | 0.97211 | -0.53864 | 0.97223 | -0.53631 | 1.8337
11 | 0.0035405 | 0.00088713 | -0.0035402 | -0.00088726 | 2.6835e-07 | -1.3045e-07 | 0.0054187 | 0.0054188 | 0.0054188 | 0.97223 | -0.53631 | 0.97215 | -0.5379 | 1.4887
12 | -0.0079016 | -0.00198 | 0.0079046 | 0.0019812 | 2.9905e-06 | 1.2374e-06 | 0.012093 | 0.012093 | 0.012093 | 0.97223 | -0.53631 | 0.97263 | -0.52837 | 3.3224
13 | -0.011443 | -0.002868 | 0.011449 | 0.0028713 | 6.2744e-06 | 3.3376e-06 | 0.017506 | 0.017506 | 0.017506 | 0.97263 | -0.52837 | 0.97322 | -0.51686 | 4.8094
14 | -0.030814 | -0.0077659 | 0.030852 | 0.0077893 | 3.7509e-05 | 2.3436e-05 | 0.046941 | 0.046941 | 0.046941 | 0.97714 | -0.43977 | 0.97844 | -0.41436 | 12.8958
15 | 0.029552 | 0.0074496 | -0.029481 | -0.0074055 | 7.0726e-05 | 4.4102e-05 | 0.045019 | 0.045019 | 0.045019 | 0.97714 | -0.43977 | 0.97458 | -0.48991 | 12.3679
16 | -0.030852 | -0.0077893 | 0.030886 | 0.0078107 | 3.4175e-05 | 2.1352e-05 | 0.046941 | 0.04694 | 0.046941 | 0.97844 | -0.41436 | 0.97962 | -0.39127 | 12.8957
17 | 0.027654 | 0.0069474 | -0.02763 | -0.006933 | 2.3107e-05 | 1.4358e-05 | 0.042228 | 0.042228 | 0.042228 | 0.97458 | -0.48991 | 0.97369 | -0.50744 | 11.6012
18 | -0.011449 | -0.0028713 | 0.01145 | 0.0028716 | 6.238e-07 | 3.3178e-07 | 0.017506 | 0.017506 | 0.017506 | 0.97322 | -0.51686 | 0.97327 | -0.51572 | 4.8094
19 | -0.025823 | -0.0064763 | 0.025833 | 0.0064826 | 1.02e-05 | 6.3112e-06 | 0.039482 | 0.039482 | 0.039482 | 0.97327 | -0.51572 | 0.97369 | -0.50744 | 10.8468
20 | 0.014374 | 0.0036047 | -0.014367 | -0.0036008 | 6.7901e-06 | 3.88e-06 | 0.021976 | 0.021976 | 0.021976 | 0.97327 | -0.51572 | 0.97277 | -0.52564 | 6.0375
21 | 0.010447 | 0.0026184 | -0.010447 | -0.0026184 | 8.1817e-08 | 4.1756e-08 | 0.01598 | 0.01598 | 0.01598 | 0.97277 | -0.52564 | 0.97276 | -0.5258 | 4.3902
22 | 0.0093063 | 0.0023325 | -0.009305 | -0.0023319 | 1.3715e-06 | 6.5377e-07 | 0.014236 | 0.014236 | 0.014236 | 0.97276 | -0.5258 | 0.97261 | -0.52889 | 3.9109
23 | 0.004726 | 0.0011843 | -0.0047256 | -0.0011844 | 4.2228e-07 | -4.8179e-09 | 0.0071787 | 0.0071788 | 0.0071788 | 0.97962 | -0.39127 | 0.97952 | -0.39314 | 1.9722
24 | -0.037191 | -0.0093907 | 0.03724 | 0.0094214 | 4.8686e-05 | 3.0647e-05 | 0.056517 | 0.056517 | 0.056517 | 0.97962 | -0.39127 | 0.98102 | -0.36398 | 15.5267
25 | -0.038859 | -0.0098273 | 0.038931 | 0.0098725 | 7.1787e-05 | 4.5247e-05 | 0.058973 | 0.058973 | 0.058973 | 0.98102 | -0.36398 | 0.983 | -0.32555 | 16.2015
26 | -0.038931 | -0.0098725 | 0.038973 | 0.0098989 | 4.1919e-05 | 2.642e-05 | 0.058973 | 0.058973 | 0.058973 | 0.983 | -0.32555 | 0.98415 | -0.30318 | 16.2014
27 | -0.005533 | -0.0013864 | 0.0055335 | 0.0013865 | 4.4244e-07 | 7.8953e-08 | 0.0084666 | 0.0084665 | 0.0084666 | 0.97243 | -0.53242 | 0.97251 | -0.53074 | 2.326
28 | 0.0023564 | 0.00059029 | -0.0023563 | -0.00059055 | 1.3713e-07 | -2.6113e-07 | 0.0036057 | 0.0036059 | 0.0036059 | 0.97243 | -0.53242 | 0.97237 | -0.53364 | 0.99062
29 | -0.0085776 | -0.0021494 | 0.0085784 | 0.0021498 | 7.5303e-07 | 3.3727e-07 | 0.013124 | 0.013124 | 0.013124 | 0.97251 | -0.53074 | 0.97261 | -0.52889 | 3.6056
30 | 0.17457 | 0.044417 | -0.17435 | -0.044275 | 0.00022356 | 0.00014208 | 0.2627 | 0.2627 | 0.2627 | 0.98971 | -0.19584 | 0.98832 | -0.22244 | 24.057
31 | -0.17855 | -0.045415 | 0.17878 | 0.045556 | 0.00022089 | 0.00014042 | 0.26869 | 0.26869 | 0.26869 | 0.98971 | -0.19584 | 0.99104 | -0.1702 | 24.6056
32 | 0.16913 | 0.042966 | -0.16907 | -0.042934 | 5.1482e-05 | 3.2705e-05 | 0.25484 | 0.25484 | 0.25484 | 0.98832 | -0.22244 | 0.98799 | -0.22877 | 23.3373
33 | 0.16824 | 0.042691 | -0.16809 | -0.042597 | 0.00014749 | 9.3683e-05 | 0.25279 | 0.25279 | 0.25279 | 0.99104 | -0.1702 | 0.99009 | -0.18844 | 23.1491
34 | -0.34701 | -0.088247 | 0.34803 | 0.088898 | 0.0010195 | 0.00065132 | 0.52148 | 0.52148 | 0.52148 | 0.99104 | -0.1702 | 0.99422 | -0.10941 | 47.7547
35 | 0.16526 | 0.041978 | -0.16514 | -0.041902 | 0.00011924 | 7.572e-05 | 0.2491 | 0.2491 | 0.2491 | 0.98799 | -0.22877 | 0.98721 | -0.24377 | 22.8111
36 | 0.019303 | 0.0048422 | -0.019292 | -0.0048355 | 1.1086e-05 | 6.6434e-06 | 0.029012 | 0.029012 | 0.029012 | 0.99009 | -0.18844 | 0.98947 | -0.2005 | 7.9704
37 | 0.14879 | 0.037755 | -0.1486 | -0.037635 | 0.00018966 | 0.00012021 | 0.22378 | 0.22378 | 0.22378 | 0.99009 | -0.18844 | 0.98872 | -0.21498 | 20.4924
38 | -0.35082 | -0.089598 | 0.35084 | 0.089606 | 1.378e-05 | 8.8035e-06 | 0.52566 | 0.52566 | 0.52566 | 0.99422 | -0.10941 | 0.99427 | -0.1086 | 48.1371
39 | 0.16514 | 0.041902 | -0.165 | -0.04181 | 0.00014452 | 9.178e-05 | 0.2491 | 0.2491 | 0.2491 | 0.98721 | -0.24377 | 0.98627 | -0.26198 | 22.8111
40 | 0.14311 | 0.036261 | -0.14301 | -0.036199 | 9.7113e-05 | 6.1866e-05 | 0.21552 | 0.21552 | 0.21552 | 0.98872 | -0.21498 | 0.98798 | -0.22912 | 29.6049
41 | -0.35372 | -0.09033 | 0.35468 | 0.090945 | 0.00096249 | 0.00061492 | 0.52998 | 0.52998 | 0.52998 | 0.99427 | -0.1086 | 0.99722 | -0.05247 | 48.5328
42 | 0.014103 | 0.003536 | -0.014099 | -0.003534 | 3.5968e-06 | 2.0317e-06 | 0.021278 | 0.021278 | 0.021278 | 0.98627 | -0.26198 | 0.986 | -0.26734 | 5.8457
43 | 0.14698 | 0.037293 | -0.14671 | -0.037123 | 0.00026823 | 0.00017 | 0.22192 | 0.22192 | 0.22192 | 0.98627 | -0.26198 | 0.98431 | -0.30001 | 20.322
44 | 0.097867 | 0.024829 | -0.097736 | -0.024745 | 0.00013133 | 8.3845e-05 | 0.14751 | 0.14751 | 0.14751 | 0.98798 | -0.22912 | 0.98654 | -0.25706 | 40.5238
45 | 0.045148 | 0.01137 | -0.045104 | -0.011342 | 4.4118e-05 | 2.791e-05 | 0.068017 | 0.068018 | 0.068018 | 0.98798 | -0.22912 | 0.98693 | -0.24958 | 18.6861
46 | -0.35804 | -0.091786 | 0.35895 | 0.09237 | 0.00091336 | 0.00058355 | 0.53498 | 0.53498 | 0.53498 | 0.99722 | -0.05247 | 1 | 0 | 48.9913
47 | 0.0092437 | 0.002317 | -0.0092422 | -0.0023163 | 1.5439e-06 | 7.1833e-07 | 0.01395 | 0.01395 | 0.01395 | 0.986 | -0.26734 | 0.98582 | -0.27084 | 3.8325
48 | 0.1425 | 0.036067 | -0.14238 | -0.035994 | 0.00011587 | 7.3395e-05 | 0.21555 | 0.21555 | 0.21555 | 0.98431 | -0.30001 | 0.98343 | -0.31696 | 19.7387
49 | 0.0045957 | 0.0011518 | -0.0045957 | -0.0011518 | 1.1274e-08 | -7.502e-10 | 0.0069369 | 0.0069369 | 0.0069369 | 0.98582 | -0.27084 | 0.98581 | -0.27089 | 1.9057
50 | 0.13817 | 0.034938 | -0.13813 | -0.034916 | 3.4217e-05 | 2.1661e-05 | 0.20917 | 0.20917 | 0.20917 | 0.98343 | -0.31696 | 0.98317 | -0.32212 | 19.1547
51 | 0.061356 | 0.015485 | -0.06123 | -0.015406 | 0.00012513 | 7.9562e-05 | 0.091336 | 0.091336 | 0.091336 | 1 | 0 | 0.99777 | -0.042676 | 25.0924
52 | 0.056601 | 0.014246 | -0.056522 | -0.014195 | 7.955e-05 | 5.0524e-05 | 0.084433 | 0.084433 | 0.084433 | 0.99777 | -0.042676 | 0.99624 | -0.072128 | 23.1959
53 | 0.052394 | 0.013161 | -0.052371 | -0.013146 | 2.3621e-05 | 1.4983e-05 | 0.078268 | 0.078268 | 0.078268 | 0.99624 | -0.072128 | 0.99575 | -0.08158 | 21.5022
54 | 0.031436 | 0.007893 | -0.031423 | -0.0078852 | 1.2587e-05 | 7.8578e-06 | 0.046982 | 0.046982 | 0.046982 | 0.99575 | -0.08158 | 0.99532 | -0.089976 | 12.9071
55 | 0.020935 | 0.0052526 | -0.020924 | -0.005246 | 1.0955e-05 | 6.6231e-06 | 0.031286 | 0.031286 | 0.031286 | 0.99575 | -0.08158 | 0.99518 | -0.09256 | 8.5951
56 | 0.093647 | 0.02372 | -0.093465 | -0.023604 | 0.0001822 | 0.0001163 | 0.14134 | 0.14134 | 0.14134 | 0.98654 | -0.25706 | 0.98444 | -0.29766 | 38.8297
57 | 0.037374 | 0.0094046 | -0.037342 | -0.0093844 | 3.2096e-05 | 2.0198e-05 | 0.056363 | 0.056363 | 0.056363 | 0.98693 | -0.24958 | 0.986 | -0.26756 | 15.4843
58 | 0.055099 | 0.013948 | -0.055085 | -0.013939 | 1.4594e-05 | 9.269e-06 | 0.083334 | 0.083334 | 0.083334 | 0.98444 | -0.29766 | 0.98415 | -0.30318 | 22.894
59 | 0.038366 | 0.0096556 | -0.038348 | -0.009644 | 1.8438e-05 | 1.1614e-05 | 0.058006 | 0.058006 | 0.058006 | 0.98444 | -0.29766 | 0.98392 | -0.30772 | 15.9357
60 | 0.034768 | 0.0087394 | -0.034737 | -0.0087202 | 3.0607e-05 | 1.9211e-05 | 0.052479 | 0.052479 | 0.052479 | 0.986 | -0.26756 | 0.98506 | -0.28602 | 14.4173
61 | 0.016112 | 0.0040403 | -0.016107 | -0.0040375 | 4.7264e-06 | 2.7551e-06 | 0.024361 | 0.024361 | 0.024361 | 0.98415 | -0.30318 | 0.98384 | -0.30933 | 6.6927
62 | 0.034964 | 0.0087959 | -0.034914 | -0.0087647 | 4.9651e-05 | 3.1176e-05 | 0.052889 | 0.052889 | 0.052889 | 0.98392 | -0.30772 | 0.9824 | -0.33749 | 14.53
63 | 0.02997 | 0.0075253 | -0.029946 | -0.0075107 | 2.3334e-05 | 1.4548e-05 | 0.045277 | 0.045277 | 0.045277 | 0.98506 | -0.28602 | 0.98422 | -0.30235 | 12.4387
64 | 0.013073 | 0.0032771 | -0.013072 | -0.0032768 | 5.6124e-07 | 3.1058e-07 | 0.019772 | 0.019772 | 0.019772 | 0.98384 | -0.30933 | 0.98379 | -0.31023 | 5.432
65 | 0.028831 | 0.0072402 | -0.028813 | -0.0072285 | 1.8747e-05 | 1.1666e-05 | 0.043675 | 0.043675 | 0.043675 | 0.9824 | -0.33749 | 0.9817 | -0.35112 | 11.9987
66 | 0.011931 | 0.0029908 | -0.011928 | -0.0029891 | 3.1697e-06 | 1.6991e-06 | 0.018046 | 0.018046 | 0.018046 | 0.98379 | -0.31023 | 0.98351 | -0.31581 | 4.9578
67 | 0.02713 | 0.0068068 | -0.027129 | -0.0068062 | 1.0361e-06 | 6.4244e-07 | 0.041125 | 0.041125 | 0.041125 | 0.9817 | -0.35112 | 0.98166 | -0.35193 | 11.298
68 | 0.02603 | 0.0065308 | -0.026024 | -0.0065273 | 5.6321e-06 | 3.4826e-06 | 0.039459 | 0.039459 | 0.039459 | 0.98166 | -0.35193 | 0.98143 | -0.35646 | 10.8405
69 | 0.021332 | 0.0053512 | -0.021326 | -0.005348 | 5.2306e-06 | 3.1792e-06 | 0.032344 | 0.032344 | 0.032344 | 0.98143 | -0.35646 | 0.98116 | -0.36161 | 8.8858
70 | 0.0085779 | 0.0021495 | -0.0085775 | -0.0021493 | 4.3718e-07 | 1.9196e-07 | 0.012978 | 0.012978 | 0.012978 | 0.98351 | -0.31581 | 0.98345 | -0.31688 | 3.5654
71 | 0.0047339 | 0.001186 | -0.0047336 | -0.001186 | 3.3585e-07 | -6.5483e-09 | 0.0071625 | 0.0071626 | 0.0071626 | 0.98345 | -0.31688 | 0.98338 | -0.31837 | 1.9678
72 | 0.0031801 | 0.00079669 | -0.0031799 | -0.00079685 | 1.925e-07 | -1.5804e-07 | 0.004812 | 0.0048121 | 0.0048121 | 0.98338 | -0.31837 | 0.98331 | -0.31964 | 1.322
73 | 0.0016621 | 0.00041645 | -0.0016621 | -0.00041646 | 1.6442e-09 | -7.7386e-09 | 0.0025152 | 0.0025152 | 0.0025152 | 0.98331 | -0.31964 | 0.98331 | -0.31966 | 0.69099
74 | 0.00091955 | 0.00023035 | -0.00091955 | -0.00023046 | 6.6708e-09 | -1.1227e-07 | 0.0013915 | 0.0013915 | 0.0013915 | 0.98331 | -0.31966 | 0.9833 | -0.31982 | 0.38229
75 | 0.026398 | 0.0066215 | -0.026393 | -0.0066184 | 5.0354e-06 | 3.1156e-06 | 0.039913 | 0.039913 | 0.039913 | 0.98422 | -0.30235 | 0.98401 | -0.30635 | 10.965
76 | 0.022434 | 0.0056261 | -0.022426 | -0.0056215 | 7.5421e-06 | 4.605e-06 | 0.033925 | 0.033925 | 0.033925 | 0.98401 | -0.30635 | 0.98365 | -0.31341 | 9.3202
77 | 0.018535 | 0.0046484 | -0.018528 | -0.0046441 | 7.3087e-06 | 4.3662e-06 | 0.028111 | 0.028111 | 0.028111 | 0.98116 | -0.36161 | 0.98074 | -0.36989 | 7.7229
78 | 0.016181 | 0.0040559 | -0.01618 | -0.004055 | 1.5713e-06 | 9.1789e-07 | 0.024551 | 0.024551 | 0.024551 | 0.98074 | -0.36989 | 0.98064 | -0.37192 | 6.7447
79 | 0.012315 | 0.0030865 | -0.012314 | -0.0030859 | 1.0751e-06 | 5.8448e-07 | 0.018687 | 0.018687 | 0.018687 | 0.98064 | -0.37192 | 0.98054 | -0.37376 | 5.1338
80 | 0.00021477 | 5.3562e-05 | -0.00021477 | -5.3827e-05 | 8.3919e-10 | -2.6541e-07 | 0.00032579 | 0.00032588 | 0.00032588 | 0.98068 | -0.37053 | 0.98068 | -0.37061 | 0.089529
81 | -0.008197 | -0.0020541 | 0.008201 | 0.0020558 | 3.9471e-06 | 1.6672e-06 | 0.012437 | 0.012437 | 0.012437 | 0.98068 | -0.37053 | 0.9812 | -0.36042 | 3.4169
82 | -0.008201 | -0.0020558 | 0.0082021 | 0.0020563 | 1.1857e-06 | 5.0063e-07 | 0.012437 | 0.012437 | 0.012437 | 0.9812 | -0.36042 | 0.98135 | -0.35739 | 3.4168
83 | -0.017457 | -0.0043758 | 0.017458 | 0.0043763 | 8.5389e-07 | 5.0543e-07 | 0.02647 | 0.02647 | 0.02647 | 0.98135 | -0.35739 | 0.9814 | -0.35636 | 7.2721
84 | 0.098141 | 0.024816 | -0.098047 | -0.024757 | 9.4015e-05 | 5.9599e-05 | 0.14888 | 0.14888 | 0.14888 | 0.9814 | -0.35636 | 0.98038 | -0.37636 | 20.4508
85 | -0.1156 | -0.029193 | 0.11571 | 0.029265 | 0.00011407 | 7.1882e-05 | 0.17535 | 0.17535 | 0.17535 | 0.9814 | -0.35636 | 0.98246 | -0.33579 | 16.0578
86 | 0.091242 | 0.023051 | -0.091239 | -0.02305 | 2.8866e-06 | 1.8423e-06 | 0.13855 | 0.13855 | 0.13855 | 0.98038 | -0.37636 | 0.98034 | -0.37702 | 38.0642
87 | -0.12888 | -0.032565 | 0.12897 | 0.032618 | 8.4499e-05 | 5.3406e-05 | 0.1953 | 0.1953 | 0.1953 | 0.98246 | -0.33579 | 0.98317 | -0.32212 | 17.8843
88 | 0.081048 | 0.020496 | -0.080934 | -0.020423 | 0.0001143 | 7.2899e-05 | 0.12308 | 0.12309 | 0.12309 | 0.98034 | -0.37702 | 0.97883 | -0.40646 | 33.8146
89 | 0.0091661 | 0.0022974 | -0.0091651 | -0.0022969 | 1.0038e-06 | 4.6605e-07 | 0.013873 | 0.013873 | 0.013873 | 0.98317 | -0.32212 | 0.98305 | -0.32442 | 3.8112
90 | 0.074824 | 0.018891 | -0.074769 | -0.018856 | 5.5036e-05 | 3.5081e-05 | 0.1138 | 0.1138 | 0.1138 | 0.97883 | -0.40646 | 0.97805 | -0.42183 | 31.2628
91 | 0.0049516 | 0.0012409 | -0.0049512 | -0.0012409 | 4.2494e-07 | 1.6249e-08 | 0.0074951 | 0.0074952 | 0.0074952 | 0.98305 | -0.32442 | 0.98296 | -0.32622 | 2.0591
92 | 0.069638 | 0.01757 | -0.069511 | -0.01749 | 0.00012659 | 8.0641e-05 | 0.10599 | 0.10599 | 0.10599 | 0.97805 | -0.42183 | 0.97611 | -0.45986 | 29.1181
93 | 0.008052 | 0.0020182 | -0.0080512 | -0.0020178 | 7.6729e-07 | 3.2134e-07 | 0.012275 | 0.012275 | 0.012275 | 0.97611 | -0.45986 | 0.97601 | -0.46186 | 3.3722
94 | 0.061459 | 0.015471 | -0.061452 | -0.015467 | 7.1448e-06 | 4.5456e-06 | 0.093715 | 0.093715 | 0.093715 | 0.97611 | -0.45986 | 0.97598 | -0.4623 | 25.7459
95 | 0.0035967 | 0.00090141 | -0.0035967 | -0.00090141 | 1.256e-09 | -5.8946e-10 | 0.0054835 | 0.0054835 | 0.0054835 | 0.97601 | -0.46186 | 0.976 | -0.46187 | 1.5065
96 | 0.057263 | 0.014417 | -0.057224 | -0.014393 | 3.8167e-05 | 2.426e-05 | 0.087328 | 0.087328 | 0.087328 | 0.97598 | -0.4623 | 0.97527 | -0.47625 | 23.9913
97 | 0.053387 | 0.013431 | -0.053336 | -0.013399 | 5.1049e-05 | 3.2416e-05 | 0.081474 | 0.081474 | 0.081474 | 0.97527 | -0.47625 | 0.97425 | -0.49628 | 22.3829
98 | 0.047631 | 0.011969 | -0.047612 | -0.011957 | 1.8235e-05 | 1.1556e-05 | 0.072759 | 0.072759 | 0.072759 | 0.97425 | -0.49628 | 0.97385 | -0.50431 | 19.9888
99 | -0.0054597 | -0.0013683 | 0.0054598 | 0.0013683 | 4.3122e-08 | 7.2385e-09 | 0.0083626 | 0.0083626 | 0.0083626 | 0.97148 | -0.55098 | 0.97149 | -0.55082 | 2.2974
100 | -0.010333 | -0.0025896 | 0.010336 | 0.0025912 | 3.0207e-06 | 1.5349e-06 | 0.015826 | 0.015826 | 0.015826 | 0.97149 | -0.55082 | 0.9718 | -0.54468 | 4.3479
101 | -0.022193 | -0.0055629 | 0.022196 | 0.0055646 | 2.7314e-06 | 1.6699e-06 | 0.033983 | 0.033983 | 0.033983 | 0.9718 | -0.54468 | 0.97193 | -0.5421 | 9.3359
102 | 0.0056812 | 0.0014238 | -0.0056809 | -0.0014238 | 2.8108e-07 | 5.614e-08 | 0.0086808 | 0.0086808 | 0.0086808 | 0.97385 | -0.50431 | 0.97379 | -0.50535 | 2.3848
103 | 0.041931 | 0.010533 | -0.041911 | -0.010521 | 1.9744e-05 | 1.2477e-05 | 0.064078 | 0.064079 | 0.064079 | 0.97385 | -0.50431 | 0.97335 | -0.51418 | 17.604
104 | 0.0081382 | 0.0020397 | -0.0081372 | -0.0020392 | 1.0896e-06 | 4.4366e-07 | 0.012183 | 0.012183 | 0.012183 | 0.99398 | -0.11573 | 0.99384 | -0.11854 | 3.347
105 | -0.009171 | -0.0022985 | 0.0091722 | 0.002299 | 1.208e-06 | 5.5156e-07 | 0.013729 | 0.013729 | 0.013729 | 0.99398 | -0.11573 | 0.99413 | -0.11296 | 3.7718
106 | 0.0071109 | 0.001782 | -0.0071093 | -0.0017815 | 1.6167e-06 | 5.4197e-07 | 0.010647 | 0.010647 | 0.010647 | 0.99384 | -0.11854 | 0.99359 | -0.12331 | 2.925
107 | -0.011118 | -0.0027867 | 0.011121 | 0.0027881 | 2.5387e-06 | 1.3078e-06 | 0.016642 | 0.016642 | 0.016642 | 0.99413 | -0.11296 | 0.99437 | -0.10817 | 4.5719
108 | 0.037637 | 0.0094495 | -0.037636 | -0.0094484 | 1.758e-06 | 1.1075e-06 | 0.057545 | 0.057545 | 0.057545 | 0.97335 | -0.51418 | 0.9733 | -0.51516 | 15.8089
109 | 0.033021 | 0.008292 | -0.033011 | -0.0082854 | 1.06e-05 | 6.6463e-06 | 0.05049 | 0.05049 | 0.05049 | 0.9733 | -0.51516 | 0.97296 | -0.52189 | 13.871
110 | 0.0021906 | 0.00054872 | -0.0021905 | -0.00054899 | 1.0284e-07 | -2.642e-07 | 0.0032805 | 0.0032807 | 0.0032807 | 0.99359 | -0.12331 | 0.99354 | -0.1243 | 0.90128
111 | 0.028797 | 0.0072293 | -0.028769 | -0.007212 | 2.7732e-05 | 1.7275e-05 | 0.044046 | 0.044046 | 0.044046 | 0.97296 | -0.52189 | 0.97193 | -0.5421 | 12.1005
112 | -0.0016471 | -0.0004128 | 0.0016472 | 0.00041243 | 7.2769e-08 | -3.6625e-07 | 0.0024671 | 0.002467 | 0.0024671 | 0.99342 | -0.12657 | 0.99347 | -0.12565 | 0.67778
113 | -0.0054851 | -0.0013743 | 0.0054857 | 0.0013744 | 6.0471e-07 | 7.7604e-08 | 0.0082154 | 0.0082153 | 0.0082154 | 0.99347 | -0.12565 | 0.99359 | -0.12333 | 2.257
114 | -0.0077451 | -0.0019406 | 0.0077462 | 0.0019411 | 1.066e-06 | 4.0853e-07 | 0.011599 | 0.011599 | 0.011599 | 0.99359 | -0.12333 | 0.99374 | -0.12044 | 3.1865
115 | -0.0090821 | -0.0022759 | 0.009084 | 0.0022767 | 1.8635e-06 | 8.4446e-07 | 0.013599 | 0.013599 | 0.013599 | 0.99374 | -0.12044 | 0.99396 | -0.11614 | 3.7361
116 | -0.010928 | -0.0027389 | 0.010933 | 0.0027415 | 5.0821e-06 | 2.5959e-06 | 0.01636 | 0.01636 | 0.01636 | 0.99396 | -0.11614 | 0.99447 | -0.10638 | 4.4945
117 | 0.012949 | 0.0032466 | -0.012948 | -0.003246 | 1.1067e-06 | 6.0631e-07 | 0.019376 | 0.019376 | 0.019376 | 0.99447 | -0.10638 | 0.99437 | -0.10817 | 5.3231
118 | -0.023882 | -0.0059881 | 0.023885 | 0.0059898 | 2.7402e-06 | 1.6795e-06 | 0.035736 | 0.035736 | 0.035736 | 0.99447 | -0.10638 | 0.99459 | -0.10397 | 9.8175
119 | -0.025138 | -0.0063039 | 0.025155 | 0.0063143 | 1.6778e-05 | 1.0327e-05 | 0.037611 | 0.037611 | 0.037611 | 0.99459 | -0.10397 | 0.99532 | -0.089976 | 10.3327
120 | -0.0070395 | -0.0017643 | 0.007041 | 0.0017647 | 1.4551e-06 | 4.7712e-07 | 0.010532 | 0.010532 | 0.010532 | 0.99461 | -0.10369 | 0.99483 | -0.099347 | 2.8933
121 | -0.017498 | -0.0043854 | 0.017503 | 0.0043888 | 5.6595e-06 | 3.3359e-06 | 0.026172 | 0.026172 | 0.026172 | 0.99483 | -0.099347 | 0.99518 | -0.09256 | 7.1901
122 | 0.0065979 | 0.0016536 | -0.0065973 | -0.0016534 | 6.567e-07 | 1.9733e-07 | 0.0099827 | 0.0099828 | 0.0099828 | 0.98348 | -0.3167 | 0.98338 | -0.31879 | 2.7425
123 | -0.017064 | -0.0042767 | 0.017067 | 0.0042783 | 2.6732e-06 | 1.5751e-06 | 0.025818 | 0.025818 | 0.025818 | 0.98348 | -0.3167 | 0.98365 | -0.31341 | 7.0929

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4271 | 0.10914

## res_load
| p_mw | q_mvar
0 | 0.0013363 | 0.0003349
1 | 0.0015026 | 0.00037659
2 | 0.0041353 | 0.0010364
3 | 0.0028824 | 0.00072239
4 | 0.0032971 | 0.00082632
5 | 0.002098 | 0.0005258
6 | 0.0041243 | 0.0010336
7 | 0.0065998 | 0.0016541
8 | 0.0014318 | 0.00035883
9 | 0.0043606 | 0.0010929
10 | 0.0035402 | 0.00088726
11 | 0.0035383 | 0.00088678
12 | 0.0012622 | 0.00031633
13 | 0.0018279 | 0.00045811
14 | 0.001797 | 0.00045038
15 | 0.0039198 | 0.00098238
16 | 0.0011405 | 0.00028584
17 | 0.0015789 | 0.0003957
18 | 0.0016194 | 0.00040586
19 | 0.0031766 | 0.00079613
20 | 0.0030441 | 0.00076293
21 | 0.0023563 | 0.00059055
22 | 0.00072661 | 0.00018211
23 | 0.0047256 | 0.0011844
24 | 0.0039845 | 0.00099861
25 | 0.0052204 | 0.0013083
26 | 0.0038153 | 0.00095619
27 | 0.0027907 | 0.00069941
28 | 0.0031692 | 0.00079428
29 | 0.0054839 | 0.0013744
30 | 0.0028873 | 0.00072362
31 | 0.0039131 | 0.00098073
32 | 0.0033557 | 0.00084101
33 | 0.0048558 | 0.001217
34 | 0.0042137 | 0.001056
35 | 0.0046465 | 0.0011645
36 | 0.0042147 | 0.0010563
37 | 0.0051372 | 0.0012875
38 | 0.0046291 | 0.0011602
39 | 0.0041276 | 0.0010345
40 | 0.0040884 | 0.0010246
41 | 0.0077301 | 0.0019373
42 | 0.0025736 | 0.000645
43 | 0.0033837 | 0.00084803
44 | 0.0047679 | 0.0011949
45 | 0.0030341 | 0.00076043
46 | 0.006083 | 0.0015245
47 | 0.0011413 | 0.00028603
48 | 0.0016827 | 0.00042173
49 | 0.0010987 | 0.00027536
50 | 0.0046929 | 0.0011761
51 | 0.00335 | 0.00083958
52 | 0.0038436 | 0.00096328
53 | 0.0015535 | 0.00038934
54 | 0.0015178 | 0.0003804
55 | 0.00074258 | 0.00018611
56 | 0.00091955 | 0.00023046
57 | 0.0035481 | 0.00088923
58 | 0.0039594 | 0.00099233
59 | 0.0027912 | 0.00069955
60 | 0.0023467 | 0.00058814
61 | 0.0038645 | 0.00096852
62 | 0.0010236 | 0.00025653
63 | 0.0079822 | 0.0020005
64 | 0.00021477 | 5.3827e-05
65 | 0.009255 | 0.0023195
66 | 0.0045957 | 0.0011518
67 | 0.0068046 | 0.0017054
68 | 0.013169 | 0.0033004
69 | 0.010191 | 0.0025542
70 | 0.0061102 | 0.0015313
71 | 0.0042134 | 0.001056
72 | 0.0051312 | 0.001286
73 | 0.0044546 | 0.0011164
74 | 0.0041892 | 0.0010499
75 | 0.0035967 | 0.00090141
76 | 0.0038371 | 0.00096166
77 | 0.0049512 | 0.0012409
78 | 0.0057058 | 0.00143
79 | 0.0054597 | 0.0013683
80 | 0.004873 | 0.0012213
81 | 0.011858 | 0.0029718
82 | 0.0010327 | 0.00025883
83 | 0.0010262 | 0.0002572
84 | 0.001946 | 0.00048771
85 | 0.0056809 | 0.0014238
86 | 0.004274 | 0.0010712
87 | 0.0046141 | 0.0011564
88 | 0.0049187 | 0.0012327
89 | 0.0042139 | 0.0010561
90 | 0.0065731 | 0.0016474
91 | 0.0016471 | 0.0004128
92 | 0.0038379 | 0.00096188
93 | 0.0022594 | 0.00056626
94 | 0.001336 | 0.00033483
95 | 0.0018442 | 0.0004622
96 | 0.0018271 | 0.00045792
97 | 0.0012534 | 0.00031414
98 | 0.0062681 | 0.0015709
99 | 0.0021905 | 0.00054899
100 | 0.0070395 | 0.0017643
101 | 0.010457 | 0.0026207
102 | 0.0034204 | 0.00085724
103 | 0.010466 | 0.0026231
104 | 0.0065973 | 0.0016534
105 | 0.0053593 | 0.0013432

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1