## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1372-50_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1372-50_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1372-50_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1372-50_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1372-50_0_4_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_1372-50_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1372-50_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1372-50_0_4_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1372-50_0_4_node_26 | 0.4 | n |  | TRUE
9 | bus_LV_1372-50_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1372-50_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1372-50_0_4_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_1372-50_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1372-50_0_4_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_1372-50_0_4_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_1372-50_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1372-50_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1372-50_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1372-50_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1372-50_0_4_node_34 | 0.4 | n |  | TRUE
20 | bus_LV_1372-50_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1372-50_0_4_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_1372-50_0_4_node_36 | 0.4 | n |  | TRUE
23 | bus_LV_1372-50_0_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1372-50_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1372-50_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1372-50_0_4_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1372-50_0_4_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1372-50_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1372-50_0_4_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1372-50_0_4_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_1372-50_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_1372-50_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_MV_22_1_node_198 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1372-50_0_4_load_0 | 0 | 0.065493 | 0.016414 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1372-50_0_4_load_1 | 1 | 0.035301 | 0.0088473 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1372-50_0_4_load_3 | 3 | 0.080469 | 0.020167 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1372-50_0_4_load_32 | 7 | 0.006666 | 0.0016707 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1372-50_0_4_load_26 | 8 | 0.031462 | 0.0078852 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1372-50_0_4_load_15 | 11 | 0.0027857 | 0.00069815 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1372-50_0_4_load_33 | 14 | 0.003095 | 0.00077567 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1372-50_0_4_load_13 | 17 | 0.028773 | 0.0072113 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1372-50_0_4_load_20 | 18 | 0.059896 | 0.015011 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1372-50_0_4_load_34 | 19 | 0.0021446 | 0.00053748 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1372-50_0_4_load_29 | 21 | 0.0029512 | 0.00073965 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1372-50_0_4_load_36 | 22 | 0.0036497 | 0.0009147 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1372-50_0_4_load_23 | 23 | 0.033653 | 0.0084341 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1372-50_0_4_load_21 | 25 | 0.027542 | 0.0069028 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1372-50_0_4_load_25 | 26 | 0.013028 | 0.0032652 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1372-50_0_4_load_27 | 28 | 0.01622 | 0.0040651 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1372-50_0_4_load_30 | 29 | 0.0015743 | 0.00039457 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1372-50_0_4_load_28 | 30 | 0.0084849 | 0.0021265 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1372-50_0_4_load_22 | 32 | 0.012034 | 0.0030161 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1372-50_0_4_line_0 |  | 0 | 1 | 0.021029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1372-50_0_4_line_1 |  | 0 | 2 | 0.016623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1372-50_0_4_line_2 |  | 2 | 3 | 0.028073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1372-50_0_4_line_3 |  | 3 | 4 | 0.0022252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1372-50_0_4_line_4 |  | 4 | 18 | 0.022715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1372-50_0_4_line_5 |  | 5 | 6 | 0.01691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1372-50_0_4_line_6 |  | 5 | 7 | 0.032127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1372-50_0_4_line_7 |  | 6 | 8 | 0.040091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1372-50_0_4_line_8 |  | 7 | 12 | 0.0064339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1372-50_0_4_line_9 |  | 8 | 10 | 0.0055477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1372-50_0_4_line_10 |  | 9 | 10 | 0.03058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1372-50_0_4_line_11 |  | 9 | 11 | 0.0051864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1372-50_0_4_line_12 |  | 11 | 20 | 0.0032666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1372-50_0_4_line_13 |  | 12 | 13 | 0.007899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1372-50_0_4_line_14 |  | 12 | 14 | 0.015492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1372-50_0_4_line_15 |  | 13 | 21 | 0.014331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1372-50_0_4_line_16 |  | 13 | 19 | 0.032739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1372-50_0_4_line_17 |  | 14 | 22 | 0.01826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1372-50_0_4_line_18 |  | 15 | 16 | 0.001779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1372-50_0_4_line_19 |  | 15 | 17 | 0.0077879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1372-50_0_4_line_20 |  | 16 | 23 | 0.023585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1372-50_0_4_line_21 |  | 18 | 24 | 0.013162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1372-50_0_4_line_22 |  | 20 | 24 | 0.006246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1372-50_0_4_line_23 |  | 21 | 30 | 0.00276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1372-50_0_4_line_24 |  | 23 | 25 | 0.012593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1372-50_0_4_line_25 |  | 24 | 26 | 0.03544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1372-50_0_4_line_26 |  | 25 | 32 | 0.0079926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1372-50_0_4_line_27 |  | 26 | 27 | 0.0016478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1372-50_0_4_line_28 |  | 27 | 28 | 0.0085891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1372-50_0_4_line_29 |  | 28 | 31 | 0.0084008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1372-50_0_4_line_30 |  | 29 | 30 | 0.0077703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1372-50_0_4_line_31 |  | 31 | 32 | 0.012032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1372-50_0_4_trafo_11 | 0.63 MVA 20/0.4 kV | 33 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2692406.476 | 1208501.306 | 2692411.8536 | 1208501.2698 | 2692427.5048 | 1208501.1562
1 | 2692390.6688 | 1208504.7887 | 2692392.8812 | 1208504.3115 | 2692393.7505 | 1208503.1686 | 2692402.0819 | 1208501.3408 | 2692404.85 | 1208501.317 | 2692406.476 | 1208501.306
2 | 2692390.6688 | 1208504.7887 | 2692396.4924 | 1208532.2512
3 | 2692396.954 | 1208534.428 | 2692396.4924 | 1208532.2512
4 | 2692396.954 | 1208534.428 | 2692399.9786 | 1208554.1658 | 2692400.0805 | 1208556.9107
5 | 2692329.511 | 1208537.8422 | 2692326.7156 | 1208538.6551 | 2692321.3087 | 1208539.1941 | 2692318.0302 | 1208540.7555 | 2692320.1435 | 1208545.2134
6 | 2692320.1435 | 1208545.2134 | 2692324.2096 | 1208544.3424 | 2692330.297 | 1208549.4511 | 2692339.766 | 1208558.6148 | 2692344.6935 | 1208563.3653
7 | 2692329.511 | 1208537.8422 | 2692332.1047 | 1208544.6647 | 2692336.0319 | 1208548.8394 | 2692338.6923 | 1208550.8596 | 2692340.6648 | 1208551.6351 | 2692361.3514 | 1208545.4177
8 | 2692350.0883 | 1208566.6799 | 2692346.5759 | 1208565.1801 | 2692344.6935 | 1208563.3653
9 | 2692366.3517 | 1208547.074 | 2692363.4176 | 1208547.0174 | 2692361.3514 | 1208545.4177
10 | 2692366.3517 | 1208547.074 | 2692381.1958 | 1208561.669 | 2692386.0826 | 1208570.1614
11 | 2692386.0826 | 1208570.1614 | 2692390.0377 | 1208571.0566 | 2692391.1672 | 1208571.1199
12 | 2692394.4287 | 1208571.3025 | 2692391.1672 | 1208571.1199
13 | 2692351.3819 | 1208574.4718 | 2692350.0883 | 1208566.6799
14 | 2692350.0883 | 1208566.6799 | 2692358.4451 | 1208568.6105 | 2692365.3005 | 1208569.5157
15 | 2692351.3819 | 1208574.4718 | 2692352.5013 | 1208578.2917 | 2692356.3587 | 1208587.8967
16 | 2692351.3819 | 1208574.4718 | 2692342.2086 | 1208580.1003 | 2692339.2868 | 1208581.7117 | 2692334.0608 | 1208583.8323 | 2692331.8499 | 1208586.1774 | 2692322.7204 | 1208589.6761
17 | 2692365.3005 | 1208569.5157 | 2692369.7967 | 1208570.1094 | 2692383.3085 | 1208572.5156
18 | 2692445.1409 | 1208499.384 | 2692445.1209 | 1208501.1627
19 | 2692445.1409 | 1208499.384 | 2692437.3538 | 1208499.4985
20 | 2692445.1209 | 1208501.1627 | 2692449.4754 | 1208524.3418
21 | 2692400.5687 | 1208570.0634 | 2692400.0805 | 1208556.9107
22 | 2692400.5687 | 1208570.0634 | 2692394.4287 | 1208571.3025
23 | 2692356.3587 | 1208587.8967 | 2692357.3872 | 1208590.4579
24 | 2692449.4754 | 1208524.3418 | 2692449.8762 | 1208526.4755 | 2692452.5972 | 1208536.5359
25 | 2692400.5687 | 1208570.0634 | 2692407.8106 | 1208568.3744 | 2692419.0122 | 1208565.8128 | 2692434.4046 | 1208559.8338
26 | 2692452.5972 | 1208536.5359 | 2692454.3637 | 1208543.0672 | 2692454.7418 | 1208544.234
27 | 2692435.9407 | 1208559.2372 | 2692434.4046 | 1208559.8338
28 | 2692435.9407 | 1208559.2372 | 2692444.0188 | 1208556.3189
29 | 2692452.1942 | 1208554.508 | 2692446.2403 | 1208555.5164 | 2692444.0188 | 1208556.3189
30 | 2692360.283 | 1208597.6685 | 2692357.3872 | 1208590.4579
31 | 2692452.1942 | 1208554.508 | 2692454.952 | 1208551.7155 | 2692456.3592 | 1208549.2245 | 2692454.7418 | 1208544.234

## bus_geodata
| x | y | coords
0 | 2692406.476 | 1208501.306
1 | 2692427.5048 | 1208501.1562
2 | 2692390.6688 | 1208504.7887
3 | 2692396.4924 | 1208532.2512
4 | 2692396.954 | 1208534.428
5 | 2692320.1435 | 1208545.2134
6 | 2692329.511 | 1208537.8422
7 | 2692344.6935 | 1208563.3653
8 | 2692361.3514 | 1208545.4177
9 | 2692386.0826 | 1208570.1614
10 | 2692366.3517 | 1208547.074
11 | 2692391.1672 | 1208571.1199
12 | 2692350.0883 | 1208566.6799
13 | 2692351.3819 | 1208574.4718
14 | 2692365.3005 | 1208569.5157
15 | 2692445.1409 | 1208499.384
16 | 2692445.1209 | 1208501.1627
17 | 2692437.3538 | 1208499.4985
18 | 2692400.0805 | 1208556.9107
19 | 2692322.7204 | 1208589.6761
20 | 2692394.4287 | 1208571.3025
21 | 2692356.3587 | 1208587.8967
22 | 2692383.3085 | 1208572.5156
23 | 2692449.4754 | 1208524.3418
24 | 2692400.5687 | 1208570.0634
25 | 2692452.5972 | 1208536.5359
26 | 2692434.4046 | 1208559.8338
27 | 2692435.9407 | 1208559.2372
28 | 2692444.0188 | 1208556.3189
29 | 2692360.283 | 1208597.6685
30 | 2692357.3872 | 1208590.4579
31 | 2692452.1942 | 1208554.508
32 | 2692454.7418 | 1208544.234
33 | 2692388.9679 | 1208537.0395

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99571 | -0.082391 | 0.065493 | 0.016414
1 | 0.99504 | -0.09545 | 0.035301 | 0.0088473
2 | 0.99724 | -0.052981 | 0 | 0
3 | 0.99982 | -0.0035158 | 0.080469 | 0.020167
4 | 1 | 0 | -0.4393 | -0.11063
5 | 0.99189 | -0.15583 | 0 | 0
6 | 0.99233 | -0.14728 | 0 | 0
7 | 0.99105 | -0.17211 | 0.006666 | 0.0016707
8 | 0.99338 | -0.12702 | 0.031462 | 0.0078852
9 | 0.99536 | -0.088791 | 0 | 0
10 | 0.99368 | -0.12114 | 0 | 0
11 | 0.99564 | -0.083315 | 0.0027857 | 0.00069815
12 | 0.99092 | -0.17461 | 0 | 0
13 | 0.99081 | -0.17673 | 0 | 0
14 | 0.99082 | -0.17646 | 0.003095 | 0.00077567
15 | 0.98684 | -0.25332 | 0 | 0
16 | 0.98689 | -0.2524 | 0 | 0
17 | 0.98664 | -0.25733 | 0.028773 | 0.0072113
18 | 0.99736 | -0.050408 | 0.059896 | 0.015011
19 | 0.99074 | -0.17798 | 0.0021446 | 0.00053748
20 | 0.99583 | -0.079707 | 0 | 0
21 | 0.99064 | -0.18004 | 0.0029512 | 0.00073965
22 | 0.99076 | -0.17765 | 0.0036497 | 0.0009147
23 | 0.98751 | -0.24027 | 0.033653 | 0.0084341
24 | 0.99619 | -0.072813 | 0 | 0
25 | 0.98824 | -0.22622 | 0.027542 | 0.0069028
26 | 0.99192 | -0.15486 | 0.013028 | 0.0032652
27 | 0.99174 | -0.15831 | 0 | 0
28 | 0.99081 | -0.17632 | 0.01622 | 0.0040651
29 | 0.9906 | -0.18075 | 0.0015743 | 0.00039457
30 | 0.99061 | -0.18054 | 0.0084849 | 0.0021265
31 | 0.99002 | -0.19155 | 0 | 0
32 | 0.9889 | -0.2134 | 0.012034 | 0.0030161
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.035323 | 0.0088611 | -0.035301 | -0.0088473 | 2.1977e-05 | 1.3792e-05 | 0.052791 | 0.052791 | 0.052791 | 0.99571 | -0.082391 | 0.99504 | -0.09545 | 14.5029
1 | -0.10082 | -0.025275 | 0.10096 | 0.025365 | 0.0001415 | 9.0345e-05 | 0.15066 | 0.15066 | 0.15066 | 0.99571 | -0.082391 | 0.99724 | -0.052981 | 41.3914
2 | -0.10096 | -0.025365 | 0.1012 | 0.025518 | 0.00023897 | 0.00015257 | 0.15066 | 0.15066 | 0.15066 | 0.99724 | -0.052981 | 0.99982 | -0.0035158 | 41.3914
3 | -0.18167 | -0.045685 | 0.1817 | 0.045705 | 3.0512e-05 | 1.9469e-05 | 0.27043 | 0.27042 | 0.27043 | 0.99982 | -0.0035158 | 1 | 0 | 37.1463
4 | 0.25596 | 0.064921 | -0.25534 | -0.064525 | 0.0006187 | 0.00039538 | 0.38114 | 0.38114 | 0.38114 | 1 | 0 | 0.99736 | -0.050408 | 52.3545
5 | -0.028595 | -0.0071764 | 0.028607 | 0.0071836 | 1.1671e-05 | 7.2512e-06 | 0.042902 | 0.042902 | 0.042902 | 0.99189 | -0.15583 | 0.99233 | -0.14728 | 11.7862
6 | 0.028595 | 0.0071764 | -0.028573 | -0.0071626 | 2.2175e-05 | 1.3777e-05 | 0.042902 | 0.042902 | 0.042902 | 0.99189 | -0.15583 | 0.99105 | -0.17211 | 11.7862
7 | -0.028607 | -0.0071836 | 0.028635 | 0.0072008 | 2.7671e-05 | 1.7191e-05 | 0.042902 | 0.042901 | 0.042902 | 0.99233 | -0.14728 | 0.99338 | -0.12702 | 11.7862
8 | 0.021907 | 0.005492 | -0.021904 | -0.0054904 | 2.6105e-06 | 1.5878e-06 | 0.032893 | 0.032893 | 0.032893 | 0.99105 | -0.17211 | 0.99092 | -0.17461 | 9.0366
9 | -0.060097 | -0.015086 | 0.060114 | 0.015097 | 1.6862e-05 | 1.072e-05 | 0.09003 | 0.09003 | 0.09003 | 0.99338 | -0.12702 | 0.99368 | -0.12114 | 24.7335
10 | 0.060207 | 0.015156 | -0.060114 | -0.015097 | 9.2948e-05 | 5.909e-05 | 0.09003 | 0.09003 | 0.09003 | 0.99536 | -0.088791 | 0.99368 | -0.12114 | 24.7335
11 | -0.060207 | -0.015156 | 0.060222 | 0.015166 | 1.5764e-05 | 1.0022e-05 | 0.09003 | 0.09003 | 0.09003 | 0.99536 | -0.088791 | 0.99564 | -0.083315 | 24.7334
12 | -0.063008 | -0.015864 | 0.063019 | 0.015871 | 1.0868e-05 | 6.9133e-06 | 0.094193 | 0.094193 | 0.094193 | 0.99564 | -0.083315 | 0.99583 | -0.079707 | 25.8772
13 | 0.015159 | 0.0037999 | -0.015158 | -0.003799 | 1.535e-06 | 8.8063e-07 | 0.022764 | 0.022764 | 0.022764 | 0.99092 | -0.17461 | 0.99081 | -0.17673 | 6.2538
14 | 0.0067455 | 0.0016904 | -0.0067449 | -0.0016903 | 5.9606e-07 | 1.8193e-07 | 0.010129 | 0.010129 | 0.010129 | 0.99092 | -0.17461 | 0.99082 | -0.17646 | 2.7828
15 | 0.013013 | 0.0032619 | -0.013011 | -0.0032608 | 2.0526e-06 | 1.1291e-06 | 0.019543 | 0.019543 | 0.019543 | 0.99081 | -0.17673 | 0.99064 | -0.18004 | 5.369
16 | 0.0021447 | 0.00053714 | -0.0021446 | -0.00053748 | 1.2736e-07 | -3.4011e-07 | 0.0032208 | 0.003221 | 0.003221 | 0.99081 | -0.17673 | 0.99074 | -0.17798 | 0.88488
17 | 0.0036499 | 0.00091459 | -0.0036497 | -0.0009147 | 2.0573e-07 | -1.0349e-07 | 0.0054813 | 0.0054814 | 0.0054814 | 0.99082 | -0.17646 | 0.99076 | -0.17765 | 1.5059
18 | -0.028779 | -0.0072147 | 0.02878 | 0.0072155 | 1.2563e-06 | 7.8129e-07 | 0.043395 | 0.043395 | 0.043395 | 0.98684 | -0.25332 | 0.98689 | -0.2524 | 11.9217
19 | 0.028779 | 0.0072147 | -0.028773 | -0.0072113 | 5.4997e-06 | 3.4203e-06 | 0.043395 | 0.043395 | 0.043395 | 0.98684 | -0.25332 | 0.98664 | -0.25733 | 11.9218
20 | -0.02878 | -0.0072155 | 0.028797 | 0.0072259 | 1.6655e-05 | 1.0358e-05 | 0.043395 | 0.043395 | 0.043395 | 0.98689 | -0.2524 | 0.98751 | -0.24027 | 11.9217
21 | 0.19544 | 0.049514 | -0.19523 | -0.04938 | 0.0002101 | 0.00013412 | 0.29178 | 0.29178 | 0.29178 | 0.99736 | -0.050408 | 0.99619 | -0.072813 | 40.0796
22 | -0.063019 | -0.015871 | 0.06304 | 0.015884 | 2.0781e-05 | 1.3219e-05 | 0.094193 | 0.094193 | 0.094193 | 0.99583 | -0.079707 | 0.99619 | -0.072813 | 25.8772
23 | 0.01006 | 0.0025211 | -0.010059 | -0.002521 | 2.3631e-07 | 1.1571e-07 | 0.01511 | 0.01511 | 0.01511 | 0.99064 | -0.18004 | 0.99061 | -0.18054 | 4.1512
24 | -0.062449 | -0.01566 | 0.062491 | 0.015687 | 4.1819e-05 | 2.6603e-05 | 0.094104 | 0.094104 | 0.094104 | 0.98751 | -0.24027 | 0.98824 | -0.22622 | 25.8527
25 | 0.13219 | 0.033496 | -0.13167 | -0.033164 | 0.00051885 | 0.0003316 | 0.19759 | 0.19759 | 0.19759 | 0.99619 | -0.072813 | 0.99192 | -0.15486 | 54.2822
26 | -0.090034 | -0.022589 | 0.090089 | 0.022625 | 5.5091e-05 | 3.5156e-05 | 0.13558 | 0.13558 | 0.13558 | 0.98824 | -0.22622 | 0.9889 | -0.2134 | 37.2459
27 | 0.11865 | 0.029899 | -0.11863 | -0.029887 | 1.9588e-05 | 1.2515e-05 | 0.17804 | 0.17804 | 0.17804 | 0.99192 | -0.15486 | 0.99174 | -0.15831 | 48.9128
28 | 0.11863 | 0.029887 | -0.11852 | -0.029821 | 0.0001021 | 6.5233e-05 | 0.17804 | 0.17804 | 0.17804 | 0.99174 | -0.15831 | 0.99081 | -0.17632 | 48.9128
29 | 0.1023 | 0.025756 | -0.10223 | -0.025709 | 7.4405e-05 | 4.7511e-05 | 0.15368 | 0.15368 | 0.15368 | 0.99081 | -0.17632 | 0.99002 | -0.19155 | 42.2207
30 | -0.0015743 | -0.00039457 | 0.0015744 | 0.00039448 | 1.6296e-08 | -8.9605e-08 | 0.0023649 | 0.0023648 | 0.0023649 | 0.9906 | -0.18075 | 0.99061 | -0.18054 | 0.64969
31 | 0.10223 | 0.025709 | -0.10212 | -0.025641 | 0.00010656 | 6.8046e-05 | 0.15368 | 0.15368 | 0.15368 | 0.99002 | -0.19155 | 0.9889 | -0.2134 | 42.2207

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4393 | 0.11063

## res_load
| p_mw | q_mvar
0 | 0.065493 | 0.016414
1 | 0.035301 | 0.0088473
2 | 0.080469 | 0.020167
3 | 0.006666 | 0.0016707
4 | 0.031462 | 0.0078852
5 | 0.0027857 | 0.00069815
6 | 0.003095 | 0.00077567
7 | 0.028773 | 0.0072113
8 | 0.059896 | 0.015011
9 | 0.0021446 | 0.00053748
10 | 0.0029512 | 0.00073965
11 | 0.0036497 | 0.0009147
12 | 0.033653 | 0.0084341
13 | 0.027542 | 0.0069028
14 | 0.013028 | 0.0032652
15 | 0.01622 | 0.0040651
16 | 0.0015743 | 0.00039457
17 | 0.0084849 | 0.0021265
18 | 0.012034 | 0.0030161

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1