## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1407-12_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1407-12_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1407-12_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1407-12_0_8_node_31 | 0.4 | n |  | TRUE
4 | bus_LV_1407-12_0_8_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1407-12_0_8_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_1407-12_0_8_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_1407-12_0_8_node_122 | 0.4 | n |  | TRUE
8 | bus_LV_1407-12_0_8_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_1407-12_0_8_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1407-12_0_8_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1407-12_0_8_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1407-12_0_8_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1407-12_0_8_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_1407-12_0_8_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1407-12_0_8_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1407-12_0_8_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_1407-12_0_8_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1407-12_0_8_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1407-12_0_8_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1407-12_0_8_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1407-12_0_8_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1407-12_0_8_node_51 | 0.4 | n |  | TRUE
23 | bus_LV_1407-12_0_8_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1407-12_0_8_node_108 | 0.4 | n |  | TRUE
25 | bus_LV_1407-12_0_8_node_52 | 0.4 | n |  | TRUE
26 | bus_LV_1407-12_0_8_node_53 | 0.4 | n |  | TRUE
27 | bus_LV_1407-12_0_8_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1407-12_0_8_node_107 | 0.4 | n |  | TRUE
29 | bus_LV_1407-12_0_8_node_57 | 0.4 | n |  | TRUE
30 | bus_LV_1407-12_0_8_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1407-12_0_8_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_1407-12_0_8_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_1407-12_0_8_node_106 | 0.4 | n |  | TRUE
34 | bus_LV_1407-12_0_8_node_105 | 0.4 | n |  | TRUE
35 | bus_LV_1407-12_0_8_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_1407-12_0_8_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_1407-12_0_8_node_104 | 0.4 | n |  | TRUE
38 | bus_LV_1407-12_0_8_node_103 | 0.4 | n |  | TRUE
39 | bus_LV_1407-12_0_8_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_1407-12_0_8_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_1407-12_0_8_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_1407-12_0_8_node_102 | 0.4 | n |  | TRUE
43 | bus_LV_1407-12_0_8_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_1407-12_0_8_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_1407-12_0_8_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_1407-12_0_8_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_1407-12_0_8_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_1407-12_0_8_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_1407-12_0_8_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_1407-12_0_8_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_1407-12_0_8_node_26 | 0.4 | n |  | TRUE
52 | bus_LV_1407-12_0_8_node_73 | 0.4 | n |  | TRUE
53 | bus_LV_1407-12_0_8_node_118 | 0.4 | n |  | TRUE
54 | bus_LV_1407-12_0_8_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_1407-12_0_8_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_1407-12_0_8_node_29 | 0.4 | n |  | TRUE
57 | bus_LV_1407-12_0_8_node_30 | 0.4 | n |  | TRUE
58 | bus_LV_1407-12_0_8_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_1407-12_0_8_node_58 | 0.4 | n |  | TRUE
60 | bus_LV_1407-12_0_8_node_33 | 0.4 | n |  | TRUE
61 | bus_LV_1407-12_0_8_node_35 | 0.4 | n |  | TRUE
62 | bus_LV_1407-12_0_8_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_1407-12_0_8_node_99 | 0.4 | n |  | TRUE
64 | bus_LV_1407-12_0_8_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_1407-12_0_8_node_98 | 0.4 | n |  | TRUE
66 | bus_LV_1407-12_0_8_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_1407-12_0_8_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_1407-12_0_8_node_49 | 0.4 | n |  | TRUE
69 | bus_LV_1407-12_0_8_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_1407-12_0_8_node_101 | 0.4 | n |  | TRUE
71 | bus_LV_1407-12_0_8_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_1407-12_0_8_node_64 | 0.4 | n |  | TRUE
73 | bus_LV_1407-12_0_8_node_117 | 0.4 | n |  | TRUE
74 | bus_LV_1407-12_0_8_node_116 | 0.4 | n |  | TRUE
75 | bus_LV_1407-12_0_8_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_1407-12_0_8_node_54 | 0.4 | n |  | TRUE
77 | bus_LV_1407-12_0_8_node_55 | 0.4 | n |  | TRUE
78 | bus_LV_1407-12_0_8_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_1407-12_0_8_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_1407-12_0_8_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_1407-12_0_8_node_119 | 0.4 | n |  | TRUE
82 | bus_LV_1407-12_0_8_node_120 | 0.4 | n |  | TRUE
83 | bus_LV_1407-12_0_8_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_1407-12_0_8_node_66 | 0.4 | n |  | TRUE
85 | bus_LV_1407-12_0_8_node_94 | 0.4 | n |  | TRUE
86 | bus_LV_1407-12_0_8_node_95 | 0.4 | n |  | TRUE
87 | bus_LV_1407-12_0_8_node_93 | 0.4 | n |  | TRUE
88 | bus_LV_1407-12_0_8_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_1407-12_0_8_node_67 | 0.4 | n |  | TRUE
90 | bus_LV_1407-12_0_8_node_68 | 0.4 | n |  | TRUE
91 | bus_LV_1407-12_0_8_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_1407-12_0_8_node_71 | 0.4 | n |  | TRUE
93 | bus_LV_1407-12_0_8_node_96 | 0.4 | n |  | TRUE
94 | bus_LV_1407-12_0_8_node_97 | 0.4 | n |  | TRUE
95 | bus_LV_1407-12_0_8_node_74 | 0.4 | n |  | TRUE
96 | bus_LV_1407-12_0_8_node_75 | 0.4 | n |  | TRUE
97 | bus_LV_1407-12_0_8_node_76 | 0.4 | n |  | TRUE
98 | bus_LV_1407-12_0_8_node_77 | 0.4 | n |  | TRUE
99 | bus_LV_1407-12_0_8_node_78 | 0.4 | n |  | TRUE
100 | bus_LV_1407-12_0_8_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_1407-12_0_8_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_1407-12_0_8_node_83 | 0.4 | n |  | TRUE
103 | bus_LV_1407-12_0_8_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_1407-12_0_8_node_81 | 0.4 | n |  | TRUE
105 | bus_LV_1407-12_0_8_node_82 | 0.4 | n |  | TRUE
106 | bus_LV_1407-12_0_8_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_1407-12_0_8_node_109 | 0.4 | n |  | TRUE
108 | bus_LV_1407-12_0_8_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_1407-12_0_8_node_86 | 0.4 | n |  | TRUE
110 | bus_LV_1407-12_0_8_node_87 | 0.4 | n |  | TRUE
111 | bus_LV_1407-12_0_8_node_88 | 0.4 | n |  | TRUE
112 | bus_LV_1407-12_0_8_node_89 | 0.4 | n |  | TRUE
113 | bus_LV_1407-12_0_8_node_90 | 0.4 | n |  | TRUE
114 | bus_LV_1407-12_0_8_node_91 | 0.4 | n |  | TRUE
115 | bus_LV_1407-12_0_8_node_92 | 0.4 | n |  | TRUE
116 | bus_LV_1407-12_0_8_node_100 | 0.4 | n |  | TRUE
117 | bus_LV_1407-12_0_8_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_1407-12_0_8_node_112 | 0.4 | n |  | TRUE
119 | bus_LV_1407-12_0_8_node_113 | 0.4 | n |  | TRUE
120 | bus_LV_1407-12_0_8_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_1407-12_0_8_node_115 | 0.4 | n |  | TRUE
122 | bus_LV_1407-12_0_8_node_121 | 0.4 | n |  | TRUE
123 | bus_MV_138_1_node_206 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1407-12_0_8_load_0 | 0 | 0.001731 | 0.00043382 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1407-12_0_8_load_1 | 1 | 0.00095011 | 0.00023812 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1407-12_0_8_load_31 | 3 | 0.002468 | 0.00061853 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1407-12_0_8_load_28 | 5 | 0.0012711 | 0.00031857 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1407-12_0_8_load_27 | 6 | 0.0045974 | 0.0011522 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1407-12_0_8_load_122 | 7 | 0.0038555 | 0.00096627 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1407-12_0_8_load_4 | 8 | 0.0024907 | 0.00062423 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1407-12_0_8_load_5 | 9 | 0.0062034 | 0.0015547 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1407-12_0_8_load_6 | 10 | 0.0054925 | 0.0013765 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1407-12_0_8_load_7 | 11 | 0.0045923 | 0.0011509 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1407-12_0_8_load_8 | 12 | 0.0099627 | 0.0024969 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1407-12_0_8_load_23 | 13 | 0.0033458 | 0.00083855 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1407-12_0_8_load_14 | 14 | 0.0080045 | 0.0020061 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1407-12_0_8_load_9 | 17 | 0.0031502 | 0.00078952 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1407-12_0_8_load_10 | 18 | 0.012593 | 0.0031562 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1407-12_0_8_load_11 | 19 | 0.0049761 | 0.0012471 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1407-12_0_8_load_12 | 20 | 0.0024735 | 0.00061992 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1407-12_0_8_load_13 | 21 | 0.0025769 | 0.00064582 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1407-12_0_8_load_16 | 23 | 0.0025742 | 0.00064517 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1407-12_0_8_load_108 | 24 | 0.0035838 | 0.00089818 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1407-12_0_8_load_52 | 25 | 0.033057 | 0.0082848 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1407-12_0_8_load_53 | 26 | 0.0054789 | 0.0013731 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1407-12_0_8_load_15 | 27 | 0.005262 | 0.0013188 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1407-12_0_8_load_107 | 28 | 0.0019013 | 0.00047652 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1407-12_0_8_load_57 | 29 | 0.0075416 | 0.0018901 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1407-12_0_8_load_17 | 31 | 0.0034937 | 0.00087561 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1407-12_0_8_load_106 | 33 | 0.0063468 | 0.0015907 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1407-12_0_8_load_105 | 34 | 0.0084868 | 0.002127 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1407-12_0_8_load_44 | 35 | 0.0092326 | 0.0023139 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1407-12_0_8_load_104 | 37 | 0.0024955 | 0.00062543 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1407-12_0_8_load_103 | 38 | 0.0050328 | 0.0012613 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1407-12_0_8_load_45 | 39 | 0.0077091 | 0.0019321 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1407-12_0_8_load_36 | 40 | 0.01154 | 0.0028922 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1407-12_0_8_load_32 | 41 | 0.0044 | 0.0011027 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1407-12_0_8_load_102 | 42 | 0.0098083 | 0.0024582 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1407-12_0_8_load_19 | 43 | 0.0016557 | 0.00041496 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1407-12_0_8_load_20 | 44 | 0.0081797 | 0.00205 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1407-12_0_8_load_21 | 45 | 0.0015946 | 0.00039965 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1407-12_0_8_load_37 | 46 | 0.0014164 | 0.00035498 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1407-12_0_8_load_38 | 47 | 0.0068179 | 0.0017087 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1407-12_0_8_load_47 | 49 | 0.010653 | 0.0026698 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1407-12_0_8_load_25 | 50 | 0.0096768 | 0.0024252 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1407-12_0_8_load_26 | 51 | 0.010057 | 0.0025205 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1407-12_0_8_load_73 | 52 | 0.0022465 | 0.00056302 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1407-12_0_8_load_118 | 53 | 0.0015166 | 0.0003801 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1407-12_0_8_load_72 | 54 | 0.0064705 | 0.0016217 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1407-12_0_8_load_41 | 55 | 0.002546 | 0.0006381 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1407-12_0_8_load_29 | 56 | 0.0019685 | 0.00049335 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1407-12_0_8_load_30 | 57 | 0.0022499 | 0.00056388 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1407-12_0_8_load_58 | 59 | 0.0022631 | 0.00056718 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1407-12_0_8_load_33 | 60 | 0.008673 | 0.0021737 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1407-12_0_8_load_35 | 61 | 0.0066215 | 0.0016595 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1407-12_0_8_load_48 | 62 | 0.017305 | 0.004337 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1407-12_0_8_load_99 | 63 | 0.012747 | 0.0031946 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1407-12_0_8_load_63 | 64 | 0.007951 | 0.0019927 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1407-12_0_8_load_98 | 65 | 0.011176 | 0.0028009 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1407-12_0_8_load_43 | 66 | 0.011737 | 0.0029415 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1407-12_0_8_load_40 | 67 | 0.001174 | 0.00029423 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1407-12_0_8_load_49 | 68 | 0.00144 | 0.0003609 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1407-12_0_8_load_46 | 69 | 0.012676 | 0.0031768 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1407-12_0_8_load_101 | 70 | 0.0066837 | 0.0016751 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1407-12_0_8_load_62 | 71 | 0.029257 | 0.0073324 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1407-12_0_8_load_117 | 73 | 0.0019343 | 0.00048479 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1407-12_0_8_load_116 | 74 | 0.0011716 | 0.00029363 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1407-12_0_8_load_54 | 76 | 0.0052899 | 0.0013258 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1407-12_0_8_load_55 | 77 | 0.006964 | 0.0017453 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1407-12_0_8_load_56 | 78 | 0.0050167 | 0.0012573 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1407-12_0_8_load_60 | 79 | 0.0055568 | 0.0013927 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1407-12_0_8_load_61 | 80 | 0.0047694 | 0.0011953 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1407-12_0_8_load_119 | 81 | 0.0032991 | 0.00082683 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1407-12_0_8_load_120 | 82 | 0.0022438 | 0.00056235 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1407-12_0_8_load_65 | 83 | 0.0036367 | 0.00091145 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1407-12_0_8_load_66 | 84 | 0.0026637 | 0.00066759 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1407-12_0_8_load_94 | 85 | 0.0064328 | 0.0016122 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1407-12_0_8_load_95 | 86 | 0.0014259 | 0.00035737 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1407-12_0_8_load_93 | 87 | 0.005475 | 0.0013722 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1407-12_0_8_load_70 | 88 | 0.0017924 | 0.00044922 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1407-12_0_8_load_67 | 89 | 0.0049229 | 0.0012338 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1407-12_0_8_load_68 | 90 | 0.003788 | 0.00094936 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1407-12_0_8_load_71 | 92 | 0.0021288 | 0.00053354 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1407-12_0_8_load_96 | 93 | 0.0010777 | 0.0002701 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1407-12_0_8_load_97 | 94 | 0.0028336 | 0.00071017 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1407-12_0_8_load_74 | 95 | 0.0045102 | 0.0011304 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1407-12_0_8_load_76 | 97 | 0.002583 | 0.00064736 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1407-12_0_8_load_77 | 98 | 0.0017262 | 0.00043262 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1407-12_0_8_load_79 | 100 | 0.0011442 | 0.00028677 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1407-12_0_8_load_80 | 101 | 0.0020429 | 0.00051201 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1407-12_0_8_load_85 | 103 | 0.0010008 | 0.00025083 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1407-12_0_8_load_81 | 104 | 0.0011665 | 0.00029234 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1407-12_0_8_load_82 | 105 | 0.0013626 | 0.00034149 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1407-12_0_8_load_84 | 106 | 0.0025617 | 0.00064202 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1407-12_0_8_load_109 | 107 | 0.0020757 | 0.00052021 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1407-12_0_8_load_110 | 108 | 0.0010654 | 0.00026701 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1407-12_0_8_load_86 | 109 | 0.0030227 | 0.00075755 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1407-12_0_8_load_87 | 110 | 0.0025414 | 0.00063693 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1407-12_0_8_load_88 | 111 | 0.0072814 | 0.0018249 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1407-12_0_8_load_89 | 112 | 0.0054271 | 0.0013602 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1407-12_0_8_load_90 | 113 | 0.0037281 | 0.00093436 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1407-12_0_8_load_91 | 114 | 0.0058121 | 0.0014567 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1407-12_0_8_load_92 | 115 | 0.0047947 | 0.0012017 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1407-12_0_8_load_100 | 116 | 0.011011 | 0.0027596 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1407-12_0_8_load_111 | 117 | 0.00072979 | 0.0001829 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1407-12_0_8_load_112 | 118 | 0.0027126 | 0.00067984 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1407-12_0_8_load_113 | 119 | 0.0011047 | 0.00027687 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1407-12_0_8_load_114 | 120 | 0.0016923 | 0.00042414 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1407-12_0_8_load_115 | 121 | 0.00044347 | 0.00011115 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1407-12_0_8_load_121 | 122 | 0.0022551 | 0.00056519 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1407-12_0_8_line_0 |  | 0 | 1 | 0.01661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1407-12_0_8_line_1 |  | 0 | 2 | 0.015909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1407-12_0_8_line_2 |  | 1 | 3 | 0.047066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1407-12_0_8_line_3 |  | 2 | 4 | 0.047012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1407-12_0_8_line_4 |  | 3 | 5 | 0.089637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1407-12_0_8_line_5 |  | 4 | 7 | 0.027281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1407-12_0_8_line_6 |  | 5 | 6 | 0.035659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1407-12_0_8_line_7 |  | 6 | 56 | 0.026046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1407-12_0_8_line_8 |  | 8 | 9 | 0.029657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1407-12_0_8_line_9 |  | 8 | 10 | 0.034089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1407-12_0_8_line_10 |  | 9 | 11 | 0.01963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1407-12_0_8_line_11 |  | 10 | 12 | 0.028034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1407-12_0_8_line_12 |  | 11 | 13 | 0.0050857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_1407-12_0_8_line_13 |  | 12 | 14 | 0.023328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1407-12_0_8_line_14 |  | 13 | 15 | 0.015465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1407-12_0_8_line_15 |  | 14 | 16 | 0.0088903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1407-12_0_8_line_16 |  | 15 | 50 | 0.023991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1407-12_0_8_line_17 |  | 15 | 51 | 0.044976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1407-12_0_8_line_18 |  | 16 | 29 | 0.011359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1407-12_0_8_line_19 |  | 16 | 30 | 0.02917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1407-12_0_8_line_20 |  | 17 | 18 | 0.0038802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1407-12_0_8_line_21 |  | 17 | 19 | 0.023353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1407-12_0_8_line_22 |  | 18 | 20 | 0.011207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1407-12_0_8_line_23 |  | 19 | 21 | 0.014629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1407-12_0_8_line_24 |  | 20 | 22 | 0.0090849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1407-12_0_8_line_25 |  | 21 | 23 | 0.0069864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1407-12_0_8_line_26 |  | 21 | 24 | 0.10873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1407-12_0_8_line_27 |  | 22 | 25 | 0.045621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1407-12_0_8_line_28 |  | 22 | 26 | 0.02963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1407-12_0_8_line_29 |  | 23 | 27 | 0.015066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1407-12_0_8_line_30 |  | 24 | 28 | 0.016964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1407-12_0_8_line_31 |  | 26 | 54 | 0.00074679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_1407-12_0_8_line_32 |  | 27 | 31 | 0.030584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1407-12_0_8_line_33 |  | 28 | 33 | 0.0077754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1407-12_0_8_line_34 |  | 29 | 58 | 0.057175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1407-12_0_8_line_35 |  | 30 | 46 | 0.054097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1407-12_0_8_line_36 |  | 30 | 47 | 0.028826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1407-12_0_8_line_37 |  | 30 | 44 | 0.015123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1407-12_0_8_line_38 |  | 31 | 32 | 0.018071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1407-12_0_8_line_39 |  | 32 | 35 | 0.036606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1407-12_0_8_line_40 |  | 32 | 36 | 0.033951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1407-12_0_8_line_41 |  | 33 | 34 | 0.025902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1407-12_0_8_line_42 |  | 34 | 37 | 0.006414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1407-12_0_8_line_43 |  | 35 | 39 | 0.021166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1407-12_0_8_line_44 |  | 36 | 40 | 0.014073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1407-12_0_8_line_45 |  | 36 | 41 | 0.015072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1407-12_0_8_line_46 |  | 37 | 38 | 0.02513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1407-12_0_8_line_47 |  | 38 | 42 | 0.040784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1407-12_0_8_line_48 |  | 39 | 69 | 0.00272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1407-12_0_8_line_49 |  | 40 | 63 | 0.014658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1407-12_0_8_line_50 |  | 41 | 60 | 0.025989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_1407-12_0_8_line_51 |  | 42 | 70 | 0.033654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1407-12_0_8_line_52 |  | 43 | 44 | 0.028613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1407-12_0_8_line_53 |  | 43 | 45 | 0.0087448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1407-12_0_8_line_54 |  | 46 | 48 | 0.014369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1407-12_0_8_line_55 |  | 47 | 49 | 0.015494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1407-12_0_8_line_56 |  | 48 | 66 | 0.070758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1407-12_0_8_line_57 |  | 50 | 52 | 0.032009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_1407-12_0_8_line_58 |  | 51 | 53 | 0.072346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1407-12_0_8_line_59 |  | 52 | 54 | 0.0109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1407-12_0_8_line_60 |  | 53 | 55 | 0.044418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1407-12_0_8_line_61 |  | 55 | 67 | 0.042806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1407-12_0_8_line_62 |  | 56 | 57 | 0.047513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1407-12_0_8_line_63 |  | 57 | 58 | 0.043715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1407-12_0_8_line_64 |  | 58 | 59 | 0.043299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1407-12_0_8_line_65 |  | 59 | 75 | 0.027118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1407-12_0_8_line_66 |  | 60 | 61 | 0.013374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1407-12_0_8_line_67 |  | 61 | 62 | 0.040363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_1407-12_0_8_line_68 |  | 62 | 64 | 0.024091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1407-12_0_8_line_69 |  | 63 | 65 | 0.021931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1407-12_0_8_line_70 |  | 64 | 72 | 0.046282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_1407-12_0_8_line_71 |  | 65 | 116 | 0.014754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1407-12_0_8_line_72 |  | 66 | 68 | 0.045653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1407-12_0_8_line_73 |  | 69 | 71 | 0.013887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1407-12_0_8_line_74 |  | 72 | 83 | 0.012826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1407-12_0_8_line_75 |  | 72 | 84 | 0.010818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1407-12_0_8_line_76 |  | 73 | 74 | 0.049989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1407-12_0_8_line_77 |  | 74 | 121 | 0.0038046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1407-12_0_8_line_78 |  | 75 | 80 | 0.0080107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1407-12_0_8_line_79 |  | 75 | 79 | 0.02533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1407-12_0_8_line_80 |  | 76 | 77 | 0.012359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1407-12_0_8_line_81 |  | 77 | 78 | 0.026153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1407-12_0_8_line_82 |  | 78 | 79 | 0.027879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1407-12_0_8_line_83 |  | 80 | 81 | 0.048122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1407-12_0_8_line_84 |  | 81 | 82 | 0.021425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1407-12_0_8_line_85 |  | 82 | 122 | 0.023703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1407-12_0_8_line_86 |  | 83 | 85 | 0.017898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1407-12_0_8_line_87 |  | 84 | 86 | 0.011636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_1407-12_0_8_line_88 |  | 85 | 87 | 0.0067166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1407-12_0_8_line_89 |  | 86 | 88 | 0.021329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_1407-12_0_8_line_90 |  | 87 | 115 | 0.024895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1407-12_0_8_line_91 |  | 88 | 90 | 0.018455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_1407-12_0_8_line_92 |  | 89 | 90 | 0.0016817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_1407-12_0_8_line_93 |  | 89 | 91 | 0.025374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_1407-12_0_8_line_94 |  | 91 | 92 | 0.051871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_1407-12_0_8_line_95 |  | 92 | 93 | 0.009535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_1407-12_0_8_line_96 |  | 93 | 94 | 0.010549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_1407-12_0_8_line_97 |  | 94 | 95 | 0.16981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_1407-12_0_8_line_98 |  | 95 | 96 | 0.071323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_1407-12_0_8_line_99 |  | 96 | 97 | 0.074736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_1407-12_0_8_line_100 |  | 97 | 98 | 0.028781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_1407-12_0_8_line_101 |  | 98 | 99 | 0.077621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1407-12_0_8_line_102 |  | 99 | 100 | 0.060148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1407-12_0_8_line_103 |  | 99 | 101 | 0.036263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1407-12_0_8_line_104 |  | 100 | 102 | 0.037243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1407-12_0_8_line_105 |  | 102 | 103 | 0.039103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1407-12_0_8_line_106 |  | 102 | 104 | 0.050839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1407-12_0_8_line_107 |  | 103 | 107 | 0.07974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1407-12_0_8_line_108 |  | 104 | 105 | 0.0081798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1407-12_0_8_line_109 |  | 105 | 106 | 0.014183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1407-12_0_8_line_110 |  | 107 | 108 | 0.089277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1407-12_0_8_line_111 |  | 108 | 117 | 0.012597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1407-12_0_8_line_112 |  | 109 | 110 | 0.0009832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1407-12_0_8_line_113 |  | 110 | 111 | 0.030791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1407-12_0_8_line_114 |  | 111 | 112 | 0.0016729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1407-12_0_8_line_115 |  | 112 | 113 | 0.028734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1407-12_0_8_line_116 |  | 113 | 114 | 0.00034681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1407-12_0_8_line_117 |  | 114 | 115 | 0.00054049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1407-12_0_8_line_118 |  | 117 | 118 | 0.020093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1407-12_0_8_line_119 |  | 118 | 119 | 0.015833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1407-12_0_8_line_120 |  | 119 | 120 | 0.0094528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1407-12_0_8_line_121 |  | 120 | 121 | 0.011096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1407-12_0_8_trafo_73 | 0.63 MVA 20/0.4 kV | 123 | 52 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2660413 | 1193112.7637 | 2660418.0227 | 1193118.8401 | 2660421.0345 | 1193127.0308
1 | 2660423.8118 | 1193142.6011 | 2660423.6614 | 1193137.1187 | 2660421.0345 | 1193127.0308
2 | 2660413 | 1193112.7637 | 2660365.937 | 1193112.2765
3 | 2660427.7767 | 1193183.209 | 2660431.3768 | 1193179.9435 | 2660429.3801 | 1193171.6185 | 2660423.2586 | 1193158.8827 | 2660419.5822 | 1193150.841 | 2660419.3137 | 1193146.4802 | 2660421.5336 | 1193143.2785 | 2660423.8118 | 1193142.6011
4 | 2660311.2049 | 1193041.2897 | 2660365.937 | 1193112.2765
5 | 2660427.7767 | 1193183.209 | 2660406.9506 | 1193200.8312
6 | 2660311.2049 | 1193041.2897 | 2660289.7208 | 1193012.8292
7 | 2660274.0282 | 1192992.0409 | 2660289.7208 | 1193012.8292
8 | 2660113.7116 | 1192795.2782 | 2660107.2017 | 1192788.5542 | 2660092.9458 | 1192774.3028 | 2660092.8555 | 1192774.196
9 | 2660113.7116 | 1192795.2782 | 2660137.4235 | 1192819.7698
10 | 2660080.1883 | 1192759.1994 | 2660084.5992 | 1192764.4245 | 2660092.8555 | 1192774.196
11 | 2660156.8196 | 1192840.0024 | 2660155.9071 | 1192838.8612 | 2660137.4235 | 1192819.7698
12 | 2660080.1883 | 1192759.1994 | 2660077.3299 | 1192755.8132 | 2660076.9456 | 1192755.2836
13 | 2660156.8196 | 1192840.0024 | 2660171.3879 | 1192858.2221
14 | 2660067.864 | 1192742.7663 | 2660076.9456 | 1192755.2836
15 | 2660176.9398 | 1192865.1656 | 2660171.3879 | 1192858.2221
16 | 2660067.864 | 1192742.7663 | 2660053.7707 | 1192723.3506
17 | 2660067.864 | 1192742.7663 | 2660048.7322 | 1192755.5817 | 2660030.6861 | 1192768.0746
18 | 2660176.9398 | 1192865.1656 | 2660183.8517 | 1192874.179
19 | 2660176.9398 | 1192865.1656 | 2660173.5871 | 1192869.6011 | 2660166.5839 | 1192892.1548
20 | 2660003.8146 | 1192639.8696 | 2660005.5959 | 1192643.3168
21 | 2659991.1104 | 1192620.3268 | 2660000.8902 | 1192634.21 | 2660003.8146 | 1192639.8696
22 | 2660010.7403 | 1192653.2729 | 2660005.5959 | 1192643.3168
23 | 2659982.6858 | 1192608.3674 | 2659991.1104 | 1192620.3268
24 | 2660014.9107 | 1192661.3439 | 2660010.7403 | 1192653.2729
25 | 2659982.6858 | 1192608.3674 | 2659982.221 | 1192607.7077 | 2659978.3411 | 1192602.8981
26 | 2659982.6858 | 1192608.3674 | 2660068.5039 | 1192541.6014
27 | 2660014.9107 | 1192661.3439 | 2659977.5922 | 1192687.7295
28 | 2660014.9107 | 1192661.3439 | 2660024.1528 | 1192679.2469 | 2660029.3342 | 1192687.1885
29 | 2659968.8817 | 1192591.1722 | 2659978.3411 | 1192602.8981
30 | 2660068.5039 | 1192541.6014 | 2660061.2452 | 1192526.2689
31 | 2660029.7422 | 1192687.8139 | 2660029.3342 | 1192687.1885
32 | 2659949.6791 | 1192567.3684 | 2659968.8817 | 1192591.1722
33 | 2660061.2452 | 1192526.2689 | 2660057.9182 | 1192519.2413
34 | 2660218.6438 | 1192919.5496 | 2660183.8517 | 1192874.179
35 | 2660166.5839 | 1192892.1548 | 2660159.1001 | 1192917.7832 | 2660155.5861 | 1192930.6776 | 2660149.9991 | 1192943.5511
36 | 2660166.5839 | 1192892.1548 | 2660147.776 | 1192870.3093
37 | 2660166.5839 | 1192892.1548 | 2660175.9533 | 1192904.0256
38 | 2659938.3328 | 1192553.3035 | 2659949.6791 | 1192567.3684
39 | 2659938.3328 | 1192553.3035 | 2659914.9065 | 1192525.1755
40 | 2659938.3328 | 1192553.3035 | 2659935.7476 | 1192555.6901 | 2659917.3867 | 1192573.7055 | 2659915.6729 | 1192578.1354
41 | 2660044.2076 | 1192497.3081 | 2660045.1351 | 1192498.7646 | 2660056.0604 | 1192515.317 | 2660057.9182 | 1192519.2413
42 | 2660040.7622 | 1192491.8979 | 2660044.2076 | 1192497.3081
43 | 2659914.9065 | 1192525.1755 | 2659901.3613 | 1192508.9118
44 | 2659915.6729 | 1192578.1354 | 2659906.7098 | 1192574.955 | 2659903.4354 | 1192571.7783
45 | 2659915.6729 | 1192578.1354 | 2659915.9073 | 1192582.1289 | 2659917.729 | 1192585.9493 | 2659921.9641 | 1192590.0719 | 2659922.6211 | 1192590.7284
46 | 2660027.2635 | 1192470.7015 | 2660040.7622 | 1192491.8979
47 | 2660009.424 | 1192434.2006 | 2660014.031 | 1192445.0663 | 2660019.0412 | 1192457.7905 | 2660027.2635 | 1192470.7015
48 | 2659899.6206 | 1192506.8218 | 2659901.3613 | 1192508.9118
49 | 2659903.4354 | 1192571.7783 | 2659892.9151 | 1192561.5719
50 | 2659922.6211 | 1192590.7284 | 2659933.1115 | 1192601.2121 | 2659936.497 | 1192606.4379 | 2659938.307 | 1192611.0251
51 | 2659997.3499 | 1192402.8384 | 2660000.0234 | 1192412.0291 | 2660009.424 | 1192434.2006
52 | 2660175.9533 | 1192904.0256 | 2660193.6805 | 1192926.4856
53 | 2660199.0983 | 1192933.3498 | 2660193.6805 | 1192926.4856
54 | 2660141.6267 | 1192955.2292 | 2660149.9991 | 1192943.5511
55 | 2660137.6666 | 1192858.5671 | 2660147.776 | 1192870.3093
56 | 2660141.6267 | 1192955.2292 | 2660136.2656 | 1192963.8248 | 2660132.7292 | 1192973.6504 | 2660132.4881 | 1192987.7784 | 2660135.0048 | 1193006.6034 | 2660140.5951 | 1193020.6899 | 2660141.3579 | 1193022.4384
57 | 2660035.6984 | 1192696.9431 | 2660045.4358 | 1192711.868 | 2660053.7707 | 1192723.3506
58 | 2660064.9284 | 1192824.0948 | 2660045.5282 | 1192805.2004 | 2660026.9752 | 1192784.6581 | 2660026.8598 | 1192774.8846 | 2660030.6861 | 1192768.0746
59 | 2660029.7422 | 1192687.8139 | 2660035.6984 | 1192696.9431
60 | 2660064.9284 | 1192824.0948 | 2660038.6222 | 1192859.8848
61 | 2660038.6222 | 1192859.8848 | 2660047.9448 | 1192865.1703 | 2660059.3484 | 1192871.2104 | 2660074.246 | 1192882.2662 | 2660074.6112 | 1192882.783
62 | 2660274.0282 | 1192992.0409 | 2660260.9263 | 1192974.6846 | 2660245.2462 | 1192954.2383
63 | 2660218.6438 | 1192919.5496 | 2660245.2462 | 1192954.2383
64 | 2660218.6438 | 1192919.5496 | 2660224.7419 | 1192912.7181 | 2660226.5825 | 1192905.5436 | 2660217.697 | 1192880.3286
65 | 2660223.6907 | 1192855.8526 | 2660219.2302 | 1192859.7766 | 2660216.0338 | 1192869.8725 | 2660217.697 | 1192880.3286
66 | 2659943.2158 | 1192623.4659 | 2659938.307 | 1192611.0251
67 | 2659943.2158 | 1192623.4659 | 2659943.2397 | 1192623.5263 | 2659944.6208 | 1192630.9889 | 2659943.6979 | 1192639.4178 | 2659941.1327 | 1192645.1399 | 2659937.8298 | 1192649.9318 | 2659929.3971 | 1192658.6628
68 | 2659913.8575 | 1192676.9336 | 2659917.9108 | 1192670.5554 | 2659929.3971 | 1192658.6628
69 | 2659877.1748 | 1192546.3013 | 2659892.9151 | 1192561.5719
70 | 2659909.7507 | 1192721.1806 | 2659911.1533 | 1192715.0911 | 2659907.4588 | 1192701.9021 | 2659907.5408 | 1192693.7093 | 2659910.3287 | 1192682.4863 | 2659913.8575 | 1192676.9336
71 | 2659877.1748 | 1192546.3013 | 2659866.5855 | 1192536.0281
72 | 2660132.2656 | 1193061.8589 | 2660142.8853 | 1193052.1866 | 2660146.638 | 1193041.318 | 2660145.2816 | 1193031.4321 | 2660141.3579 | 1193022.4384
73 | 2659899.6206 | 1192506.8218 | 2659890.7332 | 1192496.1506
74 | 2659909.7507 | 1192721.1806 | 2659918.5141 | 1192730.5458
75 | 2659909.7507 | 1192721.1806 | 2659905.9016 | 1192723.4323 | 2659899.7985 | 1192721.6479
76 | 2660134.5865 | 1193225.0974 | 2660158.797 | 1193241.2777 | 2660176.4094 | 1193252.473
77 | 2660131.4233 | 1193222.9834 | 2660134.5865 | 1193225.0974
78 | 2660223.6907 | 1192855.8526 | 2660227.8945 | 1192862.6717
79 | 2660223.6907 | 1192855.8526 | 2660209.9212 | 1192834.5925
80 | 2660167.9148 | 1192783.9074 | 2660177.5386 | 1192791.6617
81 | 2660177.5386 | 1192791.6617 | 2660182.2904 | 1192795.4903 | 2660194.6998 | 1192811.2401
82 | 2660209.9212 | 1192834.5925 | 2660195.2434 | 1192811.93 | 2660194.6998 | 1192811.2401
83 | 2660227.8945 | 1192862.6717 | 2660253.1472 | 1192903.6355
84 | 2660253.1472 | 1192903.6355 | 2660264.3906 | 1192921.8738
85 | 2660264.3906 | 1192921.8738 | 2660276.829 | 1192942.0509
86 | 2659930.6957 | 1192743.6581 | 2659928.2963 | 1192740.9998 | 2659918.5141 | 1192730.5458
87 | 2659899.7985 | 1192721.6479 | 2659892.3509 | 1192712.7074
88 | 2659930.6957 | 1192743.6581 | 2659935.1961 | 1192748.6439
89 | 2659892.3509 | 1192712.7074 | 2659888.2743 | 1192707.8136 | 2659883.276 | 1192693.7132
90 | 2659952.3271 | 1192766.6914 | 2659945.3192 | 1192759.8589 | 2659935.1961 | 1192748.6439
91 | 2659883.276 | 1192693.7132 | 2659883.2555 | 1192693.6552 | 2659879.2824 | 1192675.6964
92 | 2659878.9192 | 1192674.0544 | 2659879.2824 | 1192675.6964
93 | 2659862.5967 | 1192655.6935 | 2659871.1484 | 1192661.1265 | 2659875.8702 | 1192666.8882 | 2659878.8579 | 1192673.7776 | 2659878.9192 | 1192674.0544
94 | 2659862.5967 | 1192655.6935 | 2659857.3813 | 1192660.4107 | 2659845.5938 | 1192672.8778 | 2659842.8423 | 1192680.4769 | 2659843.9055 | 1192688.4921 | 2659845.8836 | 1192699.8345
95 | 2659847.5217 | 1192709.2278 | 2659845.8836 | 1192699.8345
96 | 2659849.334 | 1192719.6198 | 2659847.5217 | 1192709.2278
97 | 2659849.334 | 1192719.6198 | 2659697.6303 | 1192795.9289
98 | 2659729.226 | 1192853.8085 | 2659726.1597 | 1192851.7212 | 2659711.2352 | 1192840.9995 | 2659701.9197 | 1192828.8551 | 2659697.0266 | 1192817.3442 | 2659697.4745 | 1192801.484 | 2659697.6303 | 1192795.9289
99 | 2659729.226 | 1192853.8085 | 2659744.9002 | 1192864.2487 | 2659762.1473 | 1192878.24 | 2659773.272 | 1192886.278 | 2659784.1668 | 1192887.5653 | 2659792.4065 | 1192891.1828
100 | 2659792.4065 | 1192891.1828 | 2659798.5482 | 1192893.8792 | 2659812.5971 | 1192903.7141 | 2659816.192 | 1192907.0793
101 | 2659877.2014 | 1192955.0673 | 2659816.192 | 1192907.0793
102 | 2659877.2014 | 1192955.0673 | 2659908.5963 | 1192971.9689 | 2659926.8913 | 1192988.2531
103 | 2659893.8637 | 1192929.9529 | 2659894.0118 | 1192934.9572 | 2659892.4127 | 1192941.6562 | 2659886.5764 | 1192942.9319 | 2659879.3912 | 1192945.706 | 2659875.973 | 1192949.852 | 2659877.2014 | 1192955.0673
104 | 2659953.3125 | 1193014.1964 | 2659949.206 | 1193007.9295 | 2659929.6293 | 1192990.6902 | 2659926.8913 | 1192988.2531
105 | 2659953.3125 | 1193014.1964 | 2659958.5001 | 1193022.1196 | 2659969.7895 | 1193049.5175
106 | 2659953.3125 | 1193014.1964 | 2659950.5808 | 1193003.0849 | 2659943.0228 | 1192992.1029 | 2659934.5354 | 1192981.8231 | 2659934.9597 | 1192969.9094 | 2659935.4689 | 1192969.2754
107 | 2659969.7895 | 1193049.5175 | 2660017.8648 | 1193113.1357
108 | 2659935.4689 | 1192969.2754 | 2659940.5914 | 1192962.8981
109 | 2659950.5659 | 1192952.8447 | 2659942.5162 | 1192960.5018 | 2659940.5914 | 1192962.8981
110 | 2660017.8648 | 1193113.1357 | 2660080.65 | 1193176.6054
111 | 2660080.65 | 1193176.6054 | 2660088.9337 | 1193186.0959
112 | 2659997.4848 | 1192810.7185 | 2659996.7808 | 1192810.0322
113 | 2659996.7808 | 1192810.0322 | 2659974.7342 | 1192788.5375
114 | 2659974.7342 | 1192788.5375 | 2659973.5364 | 1192787.3697
115 | 2659973.5364 | 1192787.3697 | 2659952.9624 | 1192767.3108
116 | 2659952.9624 | 1192767.3108 | 2659952.7141 | 1192767.0687
117 | 2659952.7141 | 1192767.0687 | 2659952.3271 | 1192766.6914
118 | 2660088.9337 | 1193186.0959 | 2660097.0624 | 1193195.4089 | 2660102.9481 | 1193200.422
119 | 2660102.9481 | 1193200.422 | 2660115.0019 | 1193210.6887
120 | 2660122.1982 | 1193216.8181 | 2660122.1982 | 1193216.8181 | 2660115.0019 | 1193210.6887
121 | 2660131.4233 | 1193222.9834 | 2660122.1982 | 1193216.8181

## bus_geodata
| x | y | coords
0 | 2660421.0345 | 1193127.0308
1 | 2660413 | 1193112.7637
2 | 2660423.8118 | 1193142.6011
3 | 2660365.937 | 1193112.2765
4 | 2660427.7767 | 1193183.209
5 | 2660311.2049 | 1193041.2897
6 | 2660289.7208 | 1193012.8292
7 | 2660406.9506 | 1193200.8312
8 | 2660113.7116 | 1192795.2782
9 | 2660092.8555 | 1192774.196
10 | 2660137.4235 | 1192819.7698
11 | 2660080.1883 | 1192759.1994
12 | 2660156.8196 | 1192840.0024
13 | 2660076.9456 | 1192755.2836
14 | 2660171.3879 | 1192858.2221
15 | 2660067.864 | 1192742.7663
16 | 2660176.9398 | 1192865.1656
17 | 2660003.8146 | 1192639.8696
18 | 2660005.5959 | 1192643.3168
19 | 2659991.1104 | 1192620.3268
20 | 2660010.7403 | 1192653.2729
21 | 2659982.6858 | 1192608.3674
22 | 2660014.9107 | 1192661.3439
23 | 2659978.3411 | 1192602.8981
24 | 2660068.5039 | 1192541.6014
25 | 2659977.5922 | 1192687.7295
26 | 2660029.3342 | 1192687.1885
27 | 2659968.8817 | 1192591.1722
28 | 2660061.2452 | 1192526.2689
29 | 2660183.8517 | 1192874.179
30 | 2660166.5839 | 1192892.1548
31 | 2659949.6791 | 1192567.3684
32 | 2659938.3328 | 1192553.3035
33 | 2660057.9182 | 1192519.2413
34 | 2660044.2076 | 1192497.3081
35 | 2659914.9065 | 1192525.1755
36 | 2659915.6729 | 1192578.1354
37 | 2660040.7622 | 1192491.8979
38 | 2660027.2635 | 1192470.7015
39 | 2659901.3613 | 1192508.9118
40 | 2659903.4354 | 1192571.7783
41 | 2659922.6211 | 1192590.7284
42 | 2660009.424 | 1192434.2006
43 | 2660193.6805 | 1192926.4856
44 | 2660175.9533 | 1192904.0256
45 | 2660199.0983 | 1192933.3498
46 | 2660149.9991 | 1192943.5511
47 | 2660147.776 | 1192870.3093
48 | 2660141.6267 | 1192955.2292
49 | 2660137.6666 | 1192858.5671
50 | 2660053.7707 | 1192723.3506
51 | 2660030.6861 | 1192768.0746
52 | 2660035.6984 | 1192696.9431
53 | 2660064.9284 | 1192824.0948
54 | 2660029.7422 | 1192687.8139
55 | 2660038.6222 | 1192859.8848
56 | 2660274.0282 | 1192992.0409
57 | 2660245.2462 | 1192954.2383
58 | 2660218.6438 | 1192919.5496
59 | 2660217.697 | 1192880.3286
60 | 2659938.307 | 1192611.0251
61 | 2659943.2158 | 1192623.4659
62 | 2659929.3971 | 1192658.6628
63 | 2659892.9151 | 1192561.5719
64 | 2659913.8575 | 1192676.9336
65 | 2659877.1748 | 1192546.3013
66 | 2660141.3579 | 1193022.4384
67 | 2660074.6112 | 1192882.783
68 | 2660132.2656 | 1193061.8589
69 | 2659899.6206 | 1192506.8218
70 | 2659997.3499 | 1192402.8384
71 | 2659890.7332 | 1192496.1506
72 | 2659909.7507 | 1192721.1806
73 | 2660176.4094 | 1193252.473
74 | 2660134.5865 | 1193225.0974
75 | 2660223.6907 | 1192855.8526
76 | 2660167.9148 | 1192783.9074
77 | 2660177.5386 | 1192791.6617
78 | 2660194.6998 | 1192811.2401
79 | 2660209.9212 | 1192834.5925
80 | 2660227.8945 | 1192862.6717
81 | 2660253.1472 | 1192903.6355
82 | 2660264.3906 | 1192921.8738
83 | 2659918.5141 | 1192730.5458
84 | 2659899.7985 | 1192721.6479
85 | 2659930.6957 | 1192743.6581
86 | 2659892.3509 | 1192712.7074
87 | 2659935.1961 | 1192748.6439
88 | 2659883.276 | 1192693.7132
89 | 2659878.9192 | 1192674.0544
90 | 2659879.2824 | 1192675.6964
91 | 2659862.5967 | 1192655.6935
92 | 2659845.8836 | 1192699.8345
93 | 2659847.5217 | 1192709.2278
94 | 2659849.334 | 1192719.6198
95 | 2659697.6303 | 1192795.9289
96 | 2659729.226 | 1192853.8085
97 | 2659792.4065 | 1192891.1828
98 | 2659816.192 | 1192907.0793
99 | 2659877.2014 | 1192955.0673
100 | 2659926.8913 | 1192988.2531
101 | 2659893.8637 | 1192929.9529
102 | 2659953.3125 | 1193014.1964
103 | 2659969.7895 | 1193049.5175
104 | 2659935.4689 | 1192969.2754
105 | 2659940.5914 | 1192962.8981
106 | 2659950.5659 | 1192952.8447
107 | 2660017.8648 | 1193113.1357
108 | 2660080.65 | 1193176.6053
109 | 2659997.4848 | 1192810.7185
110 | 2659996.7808 | 1192810.0322
111 | 2659974.7342 | 1192788.5375
112 | 2659973.5364 | 1192787.3697
113 | 2659952.9624 | 1192767.3108
114 | 2659952.7141 | 1192767.0687
115 | 2659952.3271 | 1192766.6914
116 | 2659866.5855 | 1192536.0281
117 | 2660088.9337 | 1193186.0959
118 | 2660102.9481 | 1193200.422
119 | 2660115.0019 | 1193210.6887
120 | 2660122.1981 | 1193216.8181
121 | 2660131.4233 | 1193222.9834
122 | 2660276.829 | 1192942.0509
123 | 2660014.9107 | 1192661.3439

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9743 | -0.49545 | 0.001731 | 0.00043382
1 | 0.97439 | -0.49375 | 0.00095011 | 0.00023812
2 | 0.97424 | -0.49658 | 0 | 0
3 | 0.97467 | -0.4881 | 0.002468 | 0.00061853
4 | 0.97408 | -0.49991 | 0 | 0
5 | 0.97543 | -0.47329 | 0.0012711 | 0.00031857
6 | 0.97577 | -0.46658 | 0.0045974 | 0.0011522
7 | 0.97398 | -0.50184 | 0.0038555 | 0.00096627
8 | 0.99216 | -0.14861 | 0.0024907 | 0.00062423
9 | 0.99584 | -0.078622 | 0.0062034 | 0.0015547
10 | 0.98801 | -0.22818 | 0.0054925 | 0.0013765
11 | 0.99712 | -0.054506 | 0.0045923 | 0.0011509
12 | 0.98474 | -0.29135 | 0.0099627 | 0.0024969
13 | 0.99729 | -0.051285 | 0.0033458 | 0.00083855
14 | 0.98223 | -0.34004 | 0.0080045 | 0.0020061
15 | 0.99782 | -0.041268 | 0 | 0
16 | 0.98134 | -0.35737 | 0 | 0
17 | 0.99467 | -0.10129 | 0.0031502 | 0.00078952
18 | 0.99496 | -0.09588 | 0.012593 | 0.0031562
19 | 0.99298 | -0.13358 | 0.0049761 | 0.0012471
20 | 0.99581 | -0.079654 | 0.0024735 | 0.00061992
21 | 0.99194 | -0.15355 | 0.0025769 | 0.00064582
22 | 0.9965 | -0.066422 | 0 | 0
23 | 0.99152 | -0.16164 | 0.0025742 | 0.00064517
24 | 0.98751 | -0.23934 | 0.0035838 | 0.00089818
25 | 0.99513 | -0.092929 | 0.033057 | 0.0082848
26 | 0.99899 | -0.019116 | 0.0054789 | 0.0013731
27 | 0.99062 | -0.17895 | 0.005262 | 0.0013188
28 | 0.98687 | -0.25171 | 0.0019013 | 0.00047652
29 | 0.98067 | -0.3706 | 0.0075416 | 0.0018901
30 | 0.98017 | -0.38036 | 0 | 0
31 | 0.98883 | -0.21347 | 0.0034937 | 0.00087561
32 | 0.98778 | -0.23365 | 0 | 0
33 | 0.98659 | -0.25712 | 0.0063468 | 0.0015907
34 | 0.98582 | -0.27221 | 0.0084868 | 0.002127
35 | 0.9858 | -0.27222 | 0.0092326 | 0.0023139
36 | 0.98628 | -0.2627 | 0 | 0
37 | 0.98567 | -0.27497 | 0.0024955 | 0.00062543
38 | 0.98518 | -0.28468 | 0.0050328 | 0.0012613
39 | 0.98483 | -0.29108 | 0.0077091 | 0.0019321
40 | 0.98568 | -0.27443 | 0.01154 | 0.0028922
41 | 0.98578 | -0.27249 | 0.0044 | 0.0011027
42 | 0.98456 | -0.29677 | 0.0098083 | 0.0024582
43 | 0.97992 | -0.38519 | 0.0016557 | 0.00041496
44 | 0.98001 | -0.3835 | 0.0081797 | 0.00205
45 | 0.97991 | -0.38544 | 0.0015946 | 0.00039965
46 | 0.97944 | -0.3947 | 0.0014164 | 0.00035498
47 | 0.9797 | -0.3895 | 0.0068179 | 0.0017087
48 | 0.97926 | -0.39814 | 0 | 0
49 | 0.97955 | -0.3925 | 0.010653 | 0.0026698
50 | 0.99872 | -0.024146 | 0.0096768 | 0.0024252
51 | 0.99719 | -0.053322 | 0.010057 | 0.0025205
52 | 1 | 0 | -0.559 | -0.1427
53 | 0.99685 | -0.05997 | 0.0015166 | 0.0003801
54 | 0.99905 | -0.017909 | 0.0064705 | 0.0016217
55 | 0.9967 | -0.06287 | 0.002546 | 0.0006381
56 | 0.97613 | -0.45948 | 0.0019685 | 0.00049335
57 | 0.97687 | -0.44485 | 0.0022499 | 0.00056388
58 | 0.97765 | -0.42961 | 0 | 0
59 | 0.97613 | -0.45939 | 0.0022631 | 0.00056718
60 | 0.98494 | -0.28887 | 0.008673 | 0.0021737
61 | 0.98453 | -0.29679 | 0.0066215 | 0.0016595
62 | 0.98336 | -0.31953 | 0.017305 | 0.004337
63 | 0.98521 | -0.28362 | 0.012747 | 0.0031946
64 | 0.98276 | -0.33124 | 0.007951 | 0.0019927
65 | 0.98476 | -0.29236 | 0.011176 | 0.0028009
66 | 0.9784 | -0.41511 | 0.011737 | 0.0029415
67 | 0.99665 | -0.063752 | 0.001174 | 0.00029423
68 | 0.97834 | -0.4163 | 0.00144 | 0.0003609
69 | 0.98473 | -0.29313 | 0.012676 | 0.0031768
70 | 0.98435 | -0.30082 | 0.0066837 | 0.0016751
71 | 0.98435 | -0.30044 | 0.029257 | 0.0073324
72 | 0.98169 | -0.35213 | 0 | 0
73 | 0.97137 | -0.55478 | 0.0019343 | 0.00048479
74 | 0.97146 | -0.553 | 0.0011716 | 0.00029363
75 | 0.97524 | -0.47697 | 0 | 0
76 | 0.97389 | -0.5035 | 0.0052899 | 0.0013258
77 | 0.97395 | -0.5023 | 0.006964 | 0.0017453
78 | 0.97425 | -0.49641 | 0.0050167 | 0.0012573
79 | 0.9747 | -0.48757 | 0.0055568 | 0.0013927
80 | 0.97514 | -0.47882 | 0.0047694 | 0.0011953
81 | 0.97479 | -0.4857 | 0.0032991 | 0.00082683
82 | 0.9747 | -0.48747 | 0.0022438 | 0.00056235
83 | 0.98111 | -0.3633 | 0.0036367 | 0.00091145
84 | 0.98156 | -0.35466 | 0.0026637 | 0.00066759
85 | 0.98038 | -0.37774 | 0.0064328 | 0.0016122
86 | 0.98142 | -0.35724 | 0.0014259 | 0.00035737
87 | 0.98014 | -0.38238 | 0.005475 | 0.0013722
88 | 0.98119 | -0.36184 | 0.0017924 | 0.00044922
89 | 0.98098 | -0.36599 | 0.0049229 | 0.0012338
90 | 0.98099 | -0.36567 | 0.003788 | 0.00094936
91 | 0.98076 | -0.37026 | 0 | 0
92 | 0.98031 | -0.37899 | 0.0021288 | 0.00053354
93 | 0.98023 | -0.3805 | 0.0010777 | 0.0002701
94 | 0.98015 | -0.38213 | 0.0028336 | 0.00071017
95 | 0.97893 | -0.40609 | 0.0045102 | 0.0011304
96 | 0.97848 | -0.41471 | 0 | 0
97 | 0.97802 | -0.42374 | 0.002583 | 0.00064736
98 | 0.9777 | -0.43003 | 0.0017262 | 0.00043262
99 | 0.9761 | -0.46154 | 0 | 0
100 | 0.97496 | -0.48377 | 0.0011442 | 0.00028677
101 | 0.97603 | -0.46289 | 0.0020429 | 0.00051201
102 | 0.9743 | -0.49677 | 0 | 0
103 | 0.9738 | -0.50679 | 0.0010008 | 0.00025083
104 | 0.97406 | -0.50153 | 0.0011665 | 0.00029234
105 | 0.97403 | -0.50212 | 0.0013626 | 0.00034149
106 | 0.974 | -0.50279 | 0.0025617 | 0.00064202
107 | 0.97283 | -0.52577 | 0.0020757 | 0.00052021
108 | 0.97193 | -0.54364 | 0.0010654 | 0.00026701
109 | 0.9787 | -0.41064 | 0.0030227 | 0.00075755
110 | 0.9787 | -0.41059 | 0.0025414 | 0.00063693
111 | 0.97886 | -0.40747 | 0.0072814 | 0.0018249
112 | 0.97888 | -0.40708 | 0.0054271 | 0.0013602
113 | 0.97937 | -0.39754 | 0.0037281 | 0.00093436
114 | 0.97937 | -0.3974 | 0.0058121 | 0.0014567
115 | 0.97939 | -0.39712 | 0.0047947 | 0.0012017
116 | 0.98461 | -0.29528 | 0.011011 | 0.0027596
117 | 0.97182 | -0.54592 | 0.00072979 | 0.0001829
118 | 0.97165 | -0.54928 | 0.0027126 | 0.00067984
119 | 0.97155 | -0.55113 | 0.0011047 | 0.00027687
120 | 0.97151 | -0.55205 | 0.0016923 | 0.00042414
121 | 0.97147 | -0.55278 | 0.00044347 | 0.00011115
122 | 0.97465 | -0.48845 | 0.0022551 | 0.00056519
123 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0055876 | -0.0013997 | 0.0055881 | 0.0013998 | 4.5359e-07 | 8.3418e-08 | 0.0085335 | 0.0085334 | 0.0085335 | 0.9743 | -0.49545 | 0.97439 | -0.49375 | 2.3444
1 | 0.0038566 | 0.0009659 | -0.0038564 | -0.00096596 | 2.0696e-07 | -6.5658e-08 | 0.0058899 | 0.0058899 | 0.0058899 | 0.9743 | -0.49545 | 0.97424 | -0.49658 | 1.6181
2 | -0.0065382 | -0.0016379 | 0.0065399 | 0.0016385 | 1.7594e-06 | 5.3961e-07 | 0.0099844 | 0.0099842 | 0.0099844 | 0.97439 | -0.49375 | 0.97467 | -0.4881 | 2.743
3 | 0.0038564 | 0.00096596 | -0.0038558 | -0.00096616 | 6.1161e-07 | -1.9387e-07 | 0.0058899 | 0.0058901 | 0.0058901 | 0.97424 | -0.49658 | 0.97408 | -0.49991 | 1.6182
4 | -0.0090079 | -0.002257 | 0.0090143 | 0.0022599 | 6.3567e-06 | 2.9503e-06 | 0.013752 | 0.013752 | 0.013752 | 0.97467 | -0.4881 | 0.97543 | -0.47329 | 3.778
5 | 0.0038558 | 0.00096616 | -0.0038555 | -0.00096627 | 3.5494e-07 | -1.124e-07 | 0.0058901 | 0.0058903 | 0.0058903 | 0.97408 | -0.49991 | 0.97398 | -0.50184 | 1.6182
6 | -0.010285 | -0.0025785 | 0.010289 | 0.0025802 | 3.2921e-06 | 1.6617e-06 | 0.015691 | 0.015691 | 0.015691 | 0.97543 | -0.47329 | 0.97577 | -0.46658 | 4.3106
7 | -0.014886 | -0.0037324 | 0.014891 | 0.0037353 | 5.0336e-06 | 2.896e-06 | 0.022701 | 0.022701 | 0.022701 | 0.97577 | -0.46658 | 0.97613 | -0.45948 | 6.2366
8 | -0.13543 | -0.034587 | 0.13589 | 0.034881 | 0.00045984 | 0.00029391 | 0.20334 | 0.20334 | 0.20334 | 0.99216 | -0.14861 | 0.99584 | -0.078622 | 55.863
9 | 0.13294 | 0.033962 | -0.13243 | -0.033637 | 0.00050933 | 0.00032553 | 0.19961 | 0.19961 | 0.19961 | 0.99216 | -0.14861 | 0.98801 | -0.22818 | 54.8368
10 | -0.14209 | -0.036435 | 0.14226 | 0.036541 | 0.00016638 | 0.00010597 | 0.21261 | 0.21261 | 0.21261 | 0.99584 | -0.078622 | 0.99712 | -0.054506 | 29.2047
11 | 0.12694 | 0.03226 | -0.12655 | -0.032014 | 0.00038486 | 0.00024595 | 0.19133 | 0.19133 | 0.19133 | 0.98801 | -0.22818 | 0.98474 | -0.29135 | 52.5643
12 | -0.14685 | -0.037692 | 0.14687 | 0.037707 | 2.2964e-05 | 1.4432e-05 | 0.21946 | 0.21946 | 0.21946 | 0.99712 | -0.054506 | 0.99729 | -0.051285 | 15.073
13 | 0.11659 | 0.029517 | -0.11632 | -0.029344 | 0.00027184 | 0.00017368 | 0.17628 | 0.17628 | 0.17628 | 0.98474 | -0.29135 | 0.98223 | -0.34004 | 48.4286
14 | -0.15022 | -0.038545 | 0.15029 | 0.038591 | 7.3042e-05 | 4.5939e-05 | 0.22446 | 0.22445 | 0.22446 | 0.99729 | -0.051285 | 0.99782 | -0.041268 | 15.4159
15 | 0.10831 | 0.027338 | -0.10822 | -0.02728 | 8.9835e-05 | 5.7382e-05 | 0.16415 | 0.16415 | 0.16415 | 0.98223 | -0.34004 | 0.98134 | -0.35737 | 45.0972
16 | -0.1656 | -0.042428 | 0.16573 | 0.042515 | 0.00013753 | 8.6765e-05 | 0.24728 | 0.24728 | 0.24728 | 0.99782 | -0.041268 | 0.99872 | -0.024146 | 16.9834
17 | 0.015305 | 0.0038373 | -0.015296 | -0.0038323 | 8.786e-06 | 5.0359e-06 | 0.022824 | 0.022824 | 0.022824 | 0.99782 | -0.041268 | 0.99719 | -0.053322 | 6.2703
18 | 0.064647 | 0.016331 | -0.064606 | -0.016305 | 4.0966e-05 | 2.6075e-05 | 0.09807 | 0.09807 | 0.09807 | 0.98134 | -0.35737 | 0.98067 | -0.3706 | 26.9424
19 | 0.043575 | 0.010949 | -0.043528 | -0.010919 | 4.777e-05 | 3.0205e-05 | 0.066084 | 0.066084 | 0.066084 | 0.98134 | -0.35737 | 0.98017 | -0.38036 | 18.1549
20 | -0.31986 | -0.081426 | 0.31995 | 0.081479 | 8.3449e-05 | 5.3206e-05 | 0.47896 | 0.47896 | 0.47896 | 0.99467 | -0.10129 | 0.99496 | -0.09588 | 32.8954
21 | 0.31671 | 0.080636 | -0.31622 | -0.080322 | 0.00049239 | 0.00031392 | 0.47424 | 0.47424 | 0.47424 | 0.99467 | -0.10129 | 0.99298 | -0.13358 | 32.5718
22 | -0.33254 | -0.084635 | 0.3328 | 0.084801 | 0.00026034 | 0.00016603 | 0.49779 | 0.49779 | 0.49779 | 0.99496 | -0.09588 | 0.99581 | -0.079654 | 34.1889
23 | 0.31124 | 0.079075 | -0.31094 | -0.078885 | 0.00029883 | 0.00019049 | 0.46679 | 0.46679 | 0.46679 | 0.99298 | -0.13358 | 0.99194 | -0.15355 | 32.0596
24 | -0.33527 | -0.085421 | 0.33549 | 0.085558 | 0.00021419 | 0.00013661 | 0.50149 | 0.50149 | 0.50149 | 0.99581 | -0.079654 | 0.9965 | -0.066422 | 34.4428
25 | 0.26376 | 0.066961 | -0.26366 | -0.066895 | 0.0001027 | 6.5367e-05 | 0.39598 | 0.39598 | 0.39598 | 0.99194 | -0.15355 | 0.99152 | -0.16164 | 27.1963
26 | 0.044603 | 0.011278 | -0.044421 | -0.011163 | 0.00018274 | 0.00011555 | 0.066945 | 0.066945 | 0.066945 | 0.99194 | -0.15355 | 0.98751 | -0.23934 | 18.3916
27 | 0.033099 | 0.008311 | -0.033057 | -0.0082848 | 4.18e-05 | 2.6158e-05 | 0.04943 | 0.04943 | 0.04943 | 0.9965 | -0.066422 | 0.99513 | -0.092929 | 13.5796
28 | -0.36859 | -0.093869 | 0.36943 | 0.094407 | 0.00084309 | 0.00053803 | 0.55092 | 0.55092 | 0.55092 | 0.9965 | -0.066422 | 0.99899 | -0.019116 | 37.8376
29 | 0.26109 | 0.06625 | -0.26087 | -0.066112 | 0.00021716 | 0.00013821 | 0.39211 | 0.39211 | 0.39211 | 0.99152 | -0.16164 | 0.99062 | -0.17895 | 26.931
30 | 0.040837 | 0.010264 | -0.040813 | -0.010249 | 2.4096e-05 | 1.5205e-05 | 0.061545 | 0.061545 | 0.061545 | 0.98751 | -0.23934 | 0.98687 | -0.25171 | 16.908
31 | -0.37491 | -0.09578 | 0.37493 | 0.095794 | 2.1883e-05 | 1.3966e-05 | 0.55908 | 0.55908 | 0.55908 | 0.99899 | -0.019116 | 0.99905 | -0.017909 | 38.3981
32 | 0.25561 | 0.064793 | -0.25518 | -0.064524 | 0.00042325 | 0.00026931 | 0.38421 | 0.38421 | 0.38421 | 0.99062 | -0.17895 | 0.98883 | -0.21347 | 26.3881
33 | 0.038911 | 0.0097727 | -0.038901 | -0.0097663 | 1.0039e-05 | 6.3259e-06 | 0.058678 | 0.058678 | 0.058678 | 0.98687 | -0.25171 | 0.98659 | -0.25712 | 16.1204
34 | 0.057064 | 0.014415 | -0.056903 | -0.014313 | 0.0001609 | 0.00010225 | 0.086627 | 0.086627 | 0.086627 | 0.98067 | -0.3706 | 0.97765 | -0.42961 | 23.7987
35 | 0.014616 | 0.0036697 | -0.014606 | -0.003664 | 9.99e-06 | 5.7122e-06 | 0.022191 | 0.022191 | 0.022191 | 0.98017 | -0.38036 | 0.97944 | -0.3947 | 6.0965
36 | 0.01748 | 0.0043838 | -0.017472 | -0.0043793 | 7.6128e-06 | 4.509e-06 | 0.026537 | 0.026538 | 0.026538 | 0.98017 | -0.38036 | 0.9797 | -0.3895 | 7.2905
37 | 0.011432 | 0.0028652 | -0.01143 | -0.0028643 | 1.7081e-06 | 9.0263e-07 | 0.017355 | 0.017355 | 0.017355 | 0.98017 | -0.38036 | 0.98001 | -0.3835 | 4.7679
38 | 0.25169 | 0.063648 | -0.25145 | -0.063493 | 0.00024329 | 0.00015478 | 0.37895 | 0.37895 | 0.37895 | 0.98883 | -0.21347 | 0.98778 | -0.23365 | 26.0271
39 | 0.059042 | 0.014862 | -0.058933 | -0.014793 | 0.00010865 | 6.9066e-05 | 0.088964 | 0.088965 | 0.088965 | 0.98778 | -0.23365 | 0.9858 | -0.27222 | 24.4408
40 | 0.19241 | 0.048632 | -0.19214 | -0.048462 | 0.00026766 | 0.00016957 | 0.28999 | 0.28999 | 0.28999 | 0.98778 | -0.23365 | 0.98628 | -0.2627 | 19.9169
41 | 0.032554 | 0.0081757 | -0.032531 | -0.008161 | 2.3422e-05 | 1.466e-05 | 0.049106 | 0.049106 | 0.049106 | 0.98659 | -0.25712 | 0.98582 | -0.27221 | 13.4907
42 | 0.024044 | 0.006034 | -0.024041 | -0.0060321 | 3.1687e-06 | 1.9462e-06 | 0.036296 | 0.036296 | 0.036296 | 0.98582 | -0.27221 | 0.98567 | -0.27497 | 9.9714
43 | 0.049701 | 0.012479 | -0.049656 | -0.01245 | 4.468e-05 | 2.8326e-05 | 0.075028 | 0.075029 | 0.075029 | 0.9858 | -0.27222 | 0.98483 | -0.29108 | 20.6122
44 | 0.046525 | 0.01168 | -0.046499 | -0.011663 | 2.6007e-05 | 1.6465e-05 | 0.0702 | 0.0702 | 0.0702 | 0.98628 | -0.2627 | 0.98568 | -0.27443 | 19.2858
45 | 0.14561 | 0.036782 | -0.14554 | -0.036739 | 6.8259e-05 | 4.2917e-05 | 0.21979 | 0.21979 | 0.21979 | 0.98628 | -0.2627 | 0.98578 | -0.27249 | 15.0955
46 | 0.021546 | 0.0054066 | -0.021536 | -0.0054006 | 9.9713e-06 | 6.0615e-06 | 0.032529 | 0.032529 | 0.032529 | 0.98567 | -0.27497 | 0.98518 | -0.28468 | 8.9364
47 | 0.016503 | 0.0041392 | -0.016493 | -0.0041337 | 9.5031e-06 | 5.563e-06 | 0.024927 | 0.024927 | 0.024927 | 0.98518 | -0.28468 | 0.98456 | -0.29677 | 6.8481
48 | 0.041947 | 0.010518 | -0.041943 | -0.010516 | 4.0974e-06 | 2.5877e-06 | 0.063381 | 0.063381 | 0.063381 | 0.98483 | -0.29108 | 0.98473 | -0.29313 | 17.4123
49 | 0.034959 | 0.0087712 | -0.034944 | -0.0087615 | 1.5312e-05 | 9.6127e-06 | 0.052779 | 0.052779 | 0.052779 | 0.98568 | -0.27443 | 0.98521 | -0.28362 | 14.4998
50 | 0.14114 | 0.035637 | -0.14103 | -0.035567 | 0.00011069 | 6.952e-05 | 0.21315 | 0.21315 | 0.21315 | 0.98578 | -0.27249 | 0.98494 | -0.28887 | 14.6394
51 | 0.006685 | 0.0016755 | -0.0066837 | -0.0016751 | 1.2883e-06 | 3.966e-07 | 0.010103 | 0.010104 | 0.010104 | 0.98456 | -0.29677 | 0.98435 | -0.30082 | 2.7757
52 | -0.0032504 | -0.00081451 | 0.0032506 | 0.00081432 | 2.6138e-07 | -1.9321e-07 | 0.0049356 | 0.0049355 | 0.0049356 | 0.97992 | -0.38519 | 0.98001 | -0.3835 | 1.3559
53 | 0.0015947 | 0.00039956 | -0.0015946 | -0.00039965 | 1.9228e-08 | -9.7857e-08 | 0.0024215 | 0.0024215 | 0.0024215 | 0.97992 | -0.38519 | 0.97991 | -0.38544 | 0.66525
54 | 0.01319 | 0.003309 | -0.013187 | -0.0033078 | 2.1639e-06 | 1.2041e-06 | 0.020039 | 0.02004 | 0.02004 | 0.97944 | -0.3947 | 0.97926 | -0.39814 | 5.5054
55 | 0.010654 | 0.0026706 | -0.010653 | -0.0026698 | 1.5216e-06 | 7.7873e-07 | 0.016182 | 0.016182 | 0.016182 | 0.9797 | -0.3895 | 0.97955 | -0.3925 | 4.4457
56 | 0.013187 | 0.0033078 | -0.013177 | -0.0033018 | 1.0656e-05 | 5.9304e-06 | 0.02004 | 0.02004 | 0.02004 | 0.97926 | -0.39814 | 0.9784 | -0.41511 | 5.5054
57 | -0.17541 | -0.04494 | 0.17562 | 0.04507 | 0.00020551 | 0.00012985 | 0.2617 | 0.26169 | 0.2617 | 0.99872 | -0.024146 | 1 | 0 | 17.9736
58 | 0.0052389 | 0.0013118 | -0.0052372 | -0.0013117 | 1.6579e-06 | 1.1757e-07 | 0.0078171 | 0.0078174 | 0.0078174 | 0.99719 | -0.053322 | 0.99685 | -0.05997 | 2.1476
59 | 0.38173 | 0.097626 | -0.3814 | -0.097415 | 0.00033052 | 0.00021096 | 0.56871 | 0.56871 | 0.56871 | 1 | 0 | 0.99905 | -0.017909 | 39.06
60 | 0.0037206 | 0.00093155 | -0.0037201 | -0.0009318 | 5.1374e-07 | -2.5018e-07 | 0.0055535 | 0.0055537 | 0.0055537 | 0.99685 | -0.05997 | 0.9967 | -0.06287 | 1.5257
61 | 0.001174 | 0.0002937 | -0.001174 | -0.00029423 | 4.9311e-08 | -5.2629e-07 | 0.0017526 | 0.0017528 | 0.0017528 | 0.9967 | -0.06287 | 0.99665 | -0.063752 | 0.48154
62 | -0.01686 | -0.0042286 | 0.016871 | 0.0042356 | 1.177e-05 | 6.9384e-06 | 0.025702 | 0.025702 | 0.025702 | 0.97613 | -0.45948 | 0.97687 | -0.44485 | 7.061
63 | -0.019121 | -0.0047995 | 0.019135 | 0.0048078 | 1.3909e-05 | 8.3543e-06 | 0.029129 | 0.029129 | 0.029129 | 0.97687 | -0.44485 | 0.97765 | -0.42961 | 8.0025
64 | 0.037768 | 0.0095051 | -0.037714 | -0.0094713 | 5.3681e-05 | 3.3814e-05 | 0.057499 | 0.057499 | 0.057499 | 0.97765 | -0.42961 | 0.97613 | -0.45939 | 15.7964
65 | 0.035451 | 0.0089041 | -0.035421 | -0.0088855 | 2.9708e-05 | 1.8674e-05 | 0.054049 | 0.054049 | 0.054049 | 0.97613 | -0.45939 | 0.97524 | -0.47697 | 14.8486
66 | 0.13236 | 0.033394 | -0.13231 | -0.033362 | 5.0177e-05 | 3.1433e-05 | 0.20005 | 0.20005 | 0.20005 | 0.98494 | -0.28887 | 0.98453 | -0.29679 | 13.7395
67 | 0.12569 | 0.031703 | -0.12555 | -0.031617 | 0.00013666 | 8.5411e-05 | 0.19004 | 0.19004 | 0.19004 | 0.98453 | -0.29679 | 0.98336 | -0.31953 | 13.0522
68 | 0.10825 | 0.02728 | -0.10819 | -0.027243 | 6.0638e-05 | 3.7586e-05 | 0.16385 | 0.16385 | 0.16385 | 0.98336 | -0.31953 | 0.98276 | -0.33124 | 11.2538
69 | 0.022197 | 0.0055669 | -0.022188 | -0.0055613 | 9.2444e-06 | 5.6373e-06 | 0.033527 | 0.033527 | 0.033527 | 0.98521 | -0.28362 | 0.98476 | -0.29236 | 9.2108
70 | 0.10024 | 0.02525 | -0.10014 | -0.025188 | 0.0001 | 6.166e-05 | 0.15182 | 0.15182 | 0.15182 | 0.98276 | -0.33124 | 0.98169 | -0.35213 | 10.427
71 | 0.011013 | 0.0027604 | -0.011011 | -0.0027596 | 1.532e-06 | 7.9283e-07 | 0.016641 | 0.016641 | 0.016641 | 0.98476 | -0.29236 | 0.98461 | -0.29528 | 4.5716
72 | 0.0014401 | 0.00036038 | -0.00144 | -0.0003609 | 8.2117e-08 | -5.2075e-07 | 0.00219 | 0.0021902 | 0.0021902 | 0.9784 | -0.41511 | 0.97834 | -0.4163 | 0.6017
73 | 0.029267 | 0.0073388 | -0.029257 | -0.0073324 | 1.0186e-05 | 6.3426e-06 | 0.044226 | 0.044226 | 0.044226 | 0.98473 | -0.29313 | 0.98435 | -0.30044 | 12.1501
74 | 0.04825 | 0.012129 | -0.048224 | -0.012113 | 2.5736e-05 | 1.6309e-05 | 0.073149 | 0.073149 | 0.073149 | 0.98169 | -0.35213 | 0.98111 | -0.3633 | 20.0959
75 | 0.051886 | 0.013059 | -0.05188 | -0.013056 | 6.2764e-06 | 3.4699e-06 | 0.078668 | 0.078668 | 0.078668 | 0.98169 | -0.35213 | 0.98156 | -0.35466 | 5.403
76 | -0.0019343 | -0.00048479 | 0.0019345 | 0.00048427 | 1.6458e-07 | -5.1353e-07 | 0.0029631 | 0.0029629 | 0.0029631 | 0.97137 | -0.55478 | 0.97146 | -0.553 | 0.81405
77 | -0.0031061 | -0.0007779 | 0.0031061 | 0.00077788 | 3.2292e-08 | -2.6439e-08 | 0.0047575 | 0.0047575 | 0.0047575 | 0.97146 | -0.553 | 0.97147 | -0.55278 | 1.307
78 | 0.012572 | 0.0031511 | -0.01257 | -0.0031505 | 1.1053e-06 | 6.0745e-07 | 0.019182 | 0.019182 | 0.019182 | 0.97524 | -0.47697 | 0.97514 | -0.47882 | 5.2697
79 | 0.02285 | 0.0057344 | -0.022838 | -0.0057273 | 1.1548e-05 | 7.0746e-06 | 0.034867 | 0.034867 | 0.034867 | 0.97524 | -0.47697 | 0.9747 | -0.48757 | 9.5789
80 | -0.0052899 | -0.0013258 | 0.0052902 | 0.0013258 | 3.0276e-07 | 3.9974e-08 | 0.0080825 | 0.0080824 | 0.0080825 | 0.97389 | -0.5035 | 0.97395 | -0.5023 | 2.2205
81 | -0.012254 | -0.0030712 | 0.012258 | 0.003073 | 3.4377e-06 | 1.8746e-06 | 0.018722 | 0.018722 | 0.018722 | 0.97395 | -0.5023 | 0.97425 | -0.49641 | 5.1434
82 | -0.017274 | -0.0043303 | 0.017282 | 0.0043346 | 7.2777e-06 | 4.3104e-06 | 0.026384 | 0.026384 | 0.026384 | 0.97425 | -0.49641 | 0.9747 | -0.48757 | 7.2484
83 | 0.0078011 | 0.0019552 | -0.0077985 | -0.0019541 | 2.5573e-06 | 1.0365e-06 | 0.011904 | 0.011904 | 0.011904 | 0.97514 | -0.47882 | 0.97479 | -0.4857 | 3.2704
84 | 0.0044994 | 0.0011273 | -0.004499 | -0.0011273 | 3.7901e-07 | -2.4502e-08 | 0.0068682 | 0.0068683 | 0.0068683 | 0.97479 | -0.4857 | 0.9747 | -0.48747 | 1.8869
85 | 0.0022553 | 0.00056497 | -0.0022551 | -0.00056519 | 1.0536e-07 | -2.2799e-07 | 0.0034429 | 0.003443 | 0.003443 | 0.9747 | -0.48747 | 0.97465 | -0.48845 | 0.94587
86 | 0.044587 | 0.011201 | -0.044557 | -0.011182 | 3.0701e-05 | 1.9423e-05 | 0.067633 | 0.067633 | 0.067633 | 0.98111 | -0.3633 | 0.98038 | -0.37774 | 18.5806
87 | 0.049216 | 0.012388 | -0.04921 | -0.012385 | 6.0758e-06 | 3.3003e-06 | 0.07463 | 0.07463 | 0.07463 | 0.98156 | -0.35466 | 0.98142 | -0.35724 | 5.1257
88 | 0.038124 | 0.0095696 | -0.038115 | -0.0095643 | 8.4349e-06 | 5.3137e-06 | 0.05787 | 0.05787 | 0.05787 | 0.98038 | -0.37774 | 0.98014 | -0.38238 | 15.8982
89 | 0.047784 | 0.012028 | -0.047774 | -0.012022 | 1.0501e-05 | 5.643e-06 | 0.072468 | 0.072469 | 0.072469 | 0.98142 | -0.35724 | 0.98119 | -0.36184 | 4.9772
90 | 0.03264 | 0.0081921 | -0.032617 | -0.0081778 | 2.2928e-05 | 1.4361e-05 | 0.049558 | 0.049558 | 0.049558 | 0.98014 | -0.38238 | 0.97939 | -0.39712 | 13.6148
91 | 0.045981 | 0.011573 | -0.045973 | -0.011568 | 8.4172e-06 | 4.4549e-06 | 0.06975 | 0.069751 | 0.069751 | 0.98119 | -0.36184 | 0.98099 | -0.36567 | 4.7906
92 | -0.042184 | -0.010619 | 0.042185 | 0.010619 | 6.4588e-07 | 3.2843e-07 | 0.064005 | 0.064005 | 0.064005 | 0.98098 | -0.36599 | 0.98099 | -0.36567 | 4.3959
93 | 0.037261 | 0.0093847 | -0.037254 | -0.0093811 | 7.6038e-06 | 3.5854e-06 | 0.056537 | 0.056538 | 0.056538 | 0.98098 | -0.36599 | 0.98076 | -0.37026 | 3.8831
94 | 0.037254 | 0.0093811 | -0.037238 | -0.0093738 | 1.5545e-05 | 7.3314e-06 | 0.056538 | 0.056539 | 0.056539 | 0.98076 | -0.37026 | 0.98031 | -0.37899 | 3.8832
95 | 0.035109 | 0.0088403 | -0.035107 | -0.0088391 | 2.5402e-06 | 1.1449e-06 | 0.053307 | 0.053308 | 0.053308 | 0.98031 | -0.37899 | 0.98023 | -0.3805 | 3.6612
96 | 0.034029 | 0.008569 | -0.034027 | -0.0085679 | 2.6405e-06 | 1.158e-06 | 0.051672 | 0.051672 | 0.051672 | 0.98023 | -0.3805 | 0.98015 | -0.38213 | 3.5489
97 | 0.031193 | 0.0078577 | -0.031157 | -0.0078434 | 3.5726e-05 | 1.4314e-05 | 0.04737 | 0.047373 | 0.047373 | 0.98015 | -0.38213 | 0.97893 | -0.40609 | 3.2536
98 | 0.026647 | 0.006713 | -0.026636 | -0.0067096 | 1.0977e-05 | 3.4404e-06 | 0.040517 | 0.040519 | 0.040519 | 0.97893 | -0.40609 | 0.97848 | -0.41471 | 2.7829
99 | 0.026636 | 0.0067096 | -0.026625 | -0.006706 | 1.1503e-05 | 3.6089e-06 | 0.040519 | 0.04052 | 0.04052 | 0.97848 | -0.41471 | 0.97802 | -0.42374 | 2.783
100 | 0.024042 | 0.0060586 | -0.024034 | -0.0060547 | 7.225e-06 | 3.9019e-06 | 0.03659 | 0.03659 | 0.03659 | 0.97802 | -0.42374 | 0.9777 | -0.43003 | 5.0261
101 | 0.022308 | 0.0056221 | -0.022275 | -0.0056016 | 3.3576e-05 | 2.0517e-05 | 0.033963 | 0.033964 | 0.033964 | 0.9777 | -0.43003 | 0.9761 | -0.46154 | 9.3307
102 | 0.020232 | 0.0050899 | -0.02021 | -0.005077 | 2.1466e-05 | 1.2987e-05 | 0.030849 | 0.030849 | 0.030849 | 0.9761 | -0.46154 | 0.97496 | -0.48377 | 8.4751
103 | 0.0020431 | 0.00051164 | -0.0020429 | -0.00051201 | 1.3191e-07 | -3.6882e-07 | 0.0031144 | 0.0031146 | 0.0031146 | 0.9761 | -0.46154 | 0.97603 | -0.46289 | 0.85566
104 | 0.019066 | 0.0047902 | -0.019054 | -0.0047831 | 1.1829e-05 | 7.1067e-06 | 0.029103 | 0.029103 | 0.029103 | 0.97496 | -0.48377 | 0.9743 | -0.49677 | 7.9954
105 | 0.013962 | 0.0035073 | -0.013955 | -0.0035035 | 6.6694e-06 | 3.7817e-06 | 0.021327 | 0.021327 | 0.021327 | 0.9743 | -0.49677 | 0.9738 | -0.50679 | 5.859
106 | 0.0050921 | 0.0012758 | -0.0050909 | -0.0012757 | 1.153e-06 | 1.0496e-07 | 0.0077768 | 0.007777 | 0.007777 | 0.9743 | -0.49677 | 0.97406 | -0.50153 | 2.1365
107 | 0.012954 | 0.0032527 | -0.012943 | -0.0032461 | 1.172e-05 | 6.5098e-06 | 0.019797 | 0.019798 | 0.019798 | 0.9738 | -0.50679 | 0.97283 | -0.52577 | 5.4389
108 | 0.0039245 | 0.00098336 | -0.0039244 | -0.00098339 | 1.1025e-07 | -3.1257e-08 | 0.0059951 | 0.0059951 | 0.0059951 | 0.97406 | -0.50153 | 0.97403 | -0.50212 | 1.647
109 | 0.0025618 | 0.0006419 | -0.0025617 | -0.00064202 | 8.1463e-08 | -1.244e-07 | 0.0039135 | 0.0039136 | 0.0039136 | 0.97403 | -0.50212 | 0.974 | -0.50279 | 1.0752
110 | 0.010867 | 0.0027259 | -0.010858 | -0.0027211 | 9.2511e-06 | 4.8132e-06 | 0.016623 | 0.016623 | 0.016623 | 0.97283 | -0.52577 | 0.97193 | -0.54364 | 4.5668
111 | 0.0097925 | 0.0024541 | -0.0097914 | -0.0024536 | 1.0618e-06 | 5.2344e-07 | 0.014992 | 0.014992 | 0.014992 | 0.97193 | -0.54364 | 0.97182 | -0.54592 | 4.1187
112 | -0.0030227 | -0.00075755 | 0.0030227 | 0.00075755 | 7.7869e-09 | -7.3717e-09 | 0.0045957 | 0.0045957 | 0.0045957 | 0.9787 | -0.41064 | 0.9787 | -0.41059 | 1.2625
113 | -0.0055641 | -0.0013945 | 0.0055649 | 0.0013946 | 8.2631e-07 | 1.4184e-07 | 0.0084596 | 0.0084594 | 0.0084596 | 0.9787 | -0.41059 | 0.97886 | -0.40747 | 2.3241
114 | -0.012846 | -0.0032195 | 0.012847 | 0.0032196 | 2.3923e-07 | 1.3208e-07 | 0.019528 | 0.019528 | 0.019528 | 0.97886 | -0.40747 | 0.97888 | -0.40708 | 5.3649
115 | -0.018274 | -0.0045798 | 0.018282 | 0.0045848 | 8.3145e-06 | 4.9599e-06 | 0.027778 | 0.027778 | 0.027778 | 0.97888 | -0.40708 | 0.97937 | -0.39754 | 7.6314
116 | -0.02201 | -0.0055191 | 0.02201 | 0.0055192 | 1.4545e-07 | 8.8724e-08 | 0.033442 | 0.033442 | 0.033442 | 0.97937 | -0.39754 | 0.97937 | -0.3974 | 9.1875
117 | -0.027822 | -0.0069759 | 0.027823 | 0.0069761 | 3.622e-07 | 2.25e-07 | 0.042273 | 0.042273 | 0.042273 | 0.97937 | -0.3974 | 0.97939 | -0.39712 | 11.6135
118 | 0.0090616 | 0.0022707 | -0.0090602 | -0.00227 | 1.4505e-06 | 6.7943e-07 | 0.013875 | 0.013875 | 0.013875 | 0.97182 | -0.54592 | 0.97165 | -0.54928 | 3.8118
119 | 0.0063476 | 0.0015902 | -0.006347 | -0.00159 | 5.6105e-07 | 1.6298e-07 | 0.0097207 | 0.0097207 | 0.0097207 | 0.97165 | -0.54928 | 0.97155 | -0.55113 | 2.6705
120 | 0.0052423 | 0.0013131 | -0.005242 | -0.0013131 | 2.285e-07 | 2.9188e-08 | 0.0080288 | 0.0080288 | 0.0080288 | 0.97155 | -0.55113 | 0.97151 | -0.55205 | 2.2057
121 | 0.0035497 | 0.00088896 | -0.0035496 | -0.00088902 | 1.2299e-07 | -5.8673e-08 | 0.0054367 | 0.0054368 | 0.0054368 | 0.97151 | -0.55205 | 0.97147 | -0.55278 | 1.4936

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56124 | 0.14326

## res_load
| p_mw | q_mvar
0 | 0.001731 | 0.00043382
1 | 0.00095011 | 0.00023812
2 | 0.002468 | 0.00061853
3 | 0.0012711 | 0.00031857
4 | 0.0045974 | 0.0011522
5 | 0.0038555 | 0.00096627
6 | 0.0024907 | 0.00062423
7 | 0.0062034 | 0.0015547
8 | 0.0054925 | 0.0013765
9 | 0.0045923 | 0.0011509
10 | 0.0099627 | 0.0024969
11 | 0.0033458 | 0.00083855
12 | 0.0080045 | 0.0020061
13 | 0.0031502 | 0.00078952
14 | 0.012593 | 0.0031562
15 | 0.0049761 | 0.0012471
16 | 0.0024735 | 0.00061992
17 | 0.0025769 | 0.00064582
18 | 0.0025742 | 0.00064517
19 | 0.0035838 | 0.00089818
20 | 0.033057 | 0.0082848
21 | 0.0054789 | 0.0013731
22 | 0.005262 | 0.0013188
23 | 0.0019013 | 0.00047652
24 | 0.0075416 | 0.0018901
25 | 0.0034937 | 0.00087561
26 | 0.0063468 | 0.0015907
27 | 0.0084868 | 0.002127
28 | 0.0092326 | 0.0023139
29 | 0.0024955 | 0.00062543
30 | 0.0050328 | 0.0012613
31 | 0.0077091 | 0.0019321
32 | 0.01154 | 0.0028922
33 | 0.0044 | 0.0011027
34 | 0.0098083 | 0.0024582
35 | 0.0016557 | 0.00041496
36 | 0.0081797 | 0.00205
37 | 0.0015946 | 0.00039965
38 | 0.0014164 | 0.00035498
39 | 0.0068179 | 0.0017087
40 | 0.010653 | 0.0026698
41 | 0.0096768 | 0.0024252
42 | 0.010057 | 0.0025205
43 | 0.0022465 | 0.00056302
44 | 0.0015166 | 0.0003801
45 | 0.0064705 | 0.0016217
46 | 0.002546 | 0.0006381
47 | 0.0019685 | 0.00049335
48 | 0.0022499 | 0.00056388
49 | 0.0022631 | 0.00056718
50 | 0.008673 | 0.0021737
51 | 0.0066215 | 0.0016595
52 | 0.017305 | 0.004337
53 | 0.012747 | 0.0031946
54 | 0.007951 | 0.0019927
55 | 0.011176 | 0.0028009
56 | 0.011737 | 0.0029415
57 | 0.001174 | 0.00029423
58 | 0.00144 | 0.0003609
59 | 0.012676 | 0.0031768
60 | 0.0066837 | 0.0016751
61 | 0.029257 | 0.0073324
62 | 0.0019343 | 0.00048479
63 | 0.0011716 | 0.00029363
64 | 0.0052899 | 0.0013258
65 | 0.006964 | 0.0017453
66 | 0.0050167 | 0.0012573
67 | 0.0055568 | 0.0013927
68 | 0.0047694 | 0.0011953
69 | 0.0032991 | 0.00082683
70 | 0.0022438 | 0.00056235
71 | 0.0036367 | 0.00091145
72 | 0.0026637 | 0.00066759
73 | 0.0064328 | 0.0016122
74 | 0.0014259 | 0.00035737
75 | 0.005475 | 0.0013722
76 | 0.0017924 | 0.00044922
77 | 0.0049229 | 0.0012338
78 | 0.003788 | 0.00094936
79 | 0.0021288 | 0.00053354
80 | 0.0010777 | 0.0002701
81 | 0.0028336 | 0.00071017
82 | 0.0045102 | 0.0011304
83 | 0.002583 | 0.00064736
84 | 0.0017262 | 0.00043262
85 | 0.0011442 | 0.00028677
86 | 0.0020429 | 0.00051201
87 | 0.0010008 | 0.00025083
88 | 0.0011665 | 0.00029234
89 | 0.0013626 | 0.00034149
90 | 0.0025617 | 0.00064202
91 | 0.0020757 | 0.00052021
92 | 0.0010654 | 0.00026701
93 | 0.0030227 | 0.00075755
94 | 0.0025414 | 0.00063693
95 | 0.0072814 | 0.0018249
96 | 0.0054271 | 0.0013602
97 | 0.0037281 | 0.00093436
98 | 0.0058121 | 0.0014567
99 | 0.0047947 | 0.0012017
100 | 0.011011 | 0.0027596
101 | 0.00072979 | 0.0001829
102 | 0.0027126 | 0.00067984
103 | 0.0011047 | 0.00027687
104 | 0.0016923 | 0.00042414
105 | 0.00044347 | 0.00011115
106 | 0.0022551 | 0.00056519

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1