## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1407-15_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1407-15_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1407-15_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1407-15_0_5_node_43 | 0.4 | n |  | TRUE
4 | bus_LV_1407-15_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1407-15_0_5_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1407-15_0_5_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_1407-15_0_5_node_41 | 0.4 | n |  | TRUE
8 | bus_LV_1407-15_0_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1407-15_0_5_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_1407-15_0_5_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1407-15_0_5_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1407-15_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1407-15_0_5_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_1407-15_0_5_node_40 | 0.4 | n |  | TRUE
15 | bus_LV_1407-15_0_5_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_1407-15_0_5_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_1407-15_0_5_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1407-15_0_5_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_1407-15_0_5_node_44 | 0.4 | n |  | TRUE
20 | bus_LV_1407-15_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1407-15_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1407-15_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1407-15_0_5_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_1407-15_0_5_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1407-15_0_5_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1407-15_0_5_node_51 | 0.4 | n |  | TRUE
27 | bus_LV_1407-15_0_5_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1407-15_0_5_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_1407-15_0_5_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1407-15_0_5_node_72 | 0.4 | n |  | TRUE
31 | bus_LV_1407-15_0_5_node_73 | 0.4 | n |  | TRUE
32 | bus_LV_1407-15_0_5_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1407-15_0_5_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1407-15_0_5_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1407-15_0_5_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_1407-15_0_5_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_1407-15_0_5_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_1407-15_0_5_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1407-15_0_5_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_1407-15_0_5_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_1407-15_0_5_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_1407-15_0_5_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_1407-15_0_5_node_71 | 0.4 | n |  | TRUE
44 | bus_LV_1407-15_0_5_node_70 | 0.4 | n |  | TRUE
45 | bus_LV_1407-15_0_5_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_1407-15_0_5_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_1407-15_0_5_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_1407-15_0_5_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_1407-15_0_5_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_1407-15_0_5_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_1407-15_0_5_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_1407-15_0_5_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_1407-15_0_5_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_1407-15_0_5_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_1407-15_0_5_node_57 | 0.4 | n |  | TRUE
56 | bus_LV_1407-15_0_5_node_68 | 0.4 | n |  | TRUE
57 | bus_LV_1407-15_0_5_node_65 | 0.4 | n |  | TRUE
58 | bus_LV_1407-15_0_5_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_1407-15_0_5_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_1407-15_0_5_node_53 | 0.4 | n |  | TRUE
61 | bus_LV_1407-15_0_5_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_1407-15_0_5_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_1407-15_0_5_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_1407-15_0_5_node_66 | 0.4 | n |  | TRUE
65 | bus_LV_1407-15_0_5_node_60 | 0.4 | n |  | TRUE
66 | bus_LV_1407-15_0_5_node_61 | 0.4 | n |  | TRUE
67 | bus_LV_1407-15_0_5_node_62 | 0.4 | n |  | TRUE
68 | bus_LV_1407-15_0_5_node_63 | 0.4 | n |  | TRUE
69 | bus_LV_1407-15_0_5_node_64 | 0.4 | n |  | TRUE
70 | bus_LV_1407-15_0_5_node_67 | 0.4 | n |  | TRUE
71 | bus_LV_1407-15_0_5_node_74 | 0.4 | n |  | TRUE
72 | bus_MV_140_0_node_98 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1407-15_0_5_load_0 | 0 | 0.0063585 | 0.0015936 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1407-15_0_5_load_1 | 1 | 0.011094 | 0.0027803 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1407-15_0_5_load_3 | 2 | 0.00089436 | 0.00022415 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1407-15_0_5_load_4 | 4 | 0.020972 | 0.005256 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1407-15_0_5_load_38 | 6 | 0.00054405 | 0.00013635 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1407-15_0_5_load_41 | 7 | 0.00064333 | 0.00016123 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1407-15_0_5_load_9 | 8 | 0.0037913 | 0.0009502 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1407-15_0_5_load_10 | 9 | 0.0084547 | 0.0021189 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1407-15_0_5_load_5 | 10 | 0.023543 | 0.0059005 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1407-15_0_5_load_6 | 11 | 0.018243 | 0.004572 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1407-15_0_5_load_39 | 15 | 0.0010773 | 0.00026999 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1407-15_0_5_load_24 | 17 | 0.00085971 | 0.00021546 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1407-15_0_5_load_11 | 20 | 0.0022246 | 0.00055755 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1407-15_0_5_load_15 | 23 | 0.0021942 | 0.00054993 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1407-15_0_5_load_16 | 24 | 0.00035652 | 8.9353e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1407-15_0_5_load_18 | 25 | 0.0013264 | 0.00033243 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1407-15_0_5_load_51 | 26 | 0.0018965 | 0.00047532 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1407-15_0_5_load_17 | 27 | 0.0040705 | 0.0010202 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1407-15_0_5_load_49 | 28 | 0.0026925 | 0.00067481 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1407-15_0_5_load_21 | 29 | 0.0061521 | 0.0015419 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1407-15_0_5_load_72 | 30 | 0.0019633 | 0.00049206 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1407-15_0_5_load_73 | 31 | 0.062325 | 0.01562 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1407-15_0_5_load_22 | 32 | 0.0012148 | 0.00030445 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1407-15_0_5_load_23 | 33 | 0.0011919 | 0.00029871 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1407-15_0_5_load_25 | 34 | 0.0012787 | 0.00032048 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1407-15_0_5_load_26 | 35 | 0.0037981 | 0.0009519 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1407-15_0_5_load_33 | 38 | 0.0015885 | 0.00039811 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1407-15_0_5_load_31 | 39 | 0.010134 | 0.0025398 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1407-15_0_5_load_30 | 41 | 0.0013734 | 0.00034422 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1407-15_0_5_load_28 | 42 | 0.0026176 | 0.00065603 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1407-15_0_5_load_70 | 44 | 0.0047054 | 0.0011793 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1407-15_0_5_load_36 | 46 | 0.0024043 | 0.00060258 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1407-15_0_5_load_69 | 47 | 0.0072686 | 0.0018217 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1407-15_0_5_load_34 | 48 | 0.0030433 | 0.00076272 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1407-15_0_5_load_35 | 49 | 0.0020152 | 0.00050505 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1407-15_0_5_load_42 | 50 | 0.0054541 | 0.0013669 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1407-15_0_5_load_46 | 51 | 0.001285 | 0.00032205 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1407-15_0_5_load_47 | 52 | 0.018941 | 0.004747 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1407-15_0_5_load_48 | 53 | 0.0086166 | 0.0021595 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1407-15_0_5_load_50 | 54 | 0.0014786 | 0.00037058 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1407-15_0_5_load_57 | 55 | 0.0057487 | 0.0014408 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1407-15_0_5_load_68 | 56 | 0.0065937 | 0.0016525 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1407-15_0_5_load_58 | 58 | 0.0049077 | 0.00123 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1407-15_0_5_load_52 | 59 | 0.02101 | 0.0052655 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1407-15_0_5_load_53 | 60 | 0.0098785 | 0.0024758 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1407-15_0_5_load_54 | 61 | 0.05196 | 0.013022 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1407-15_0_5_load_55 | 62 | 0.00061102 | 0.00015314 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1407-15_0_5_load_66 | 64 | 0.00073876 | 0.00018515 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1407-15_0_5_load_60 | 65 | 0.0013119 | 0.00032879 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1407-15_0_5_load_61 | 66 | 0.0008023 | 0.00020108 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1407-15_0_5_load_63 | 68 | 0.0029252 | 0.00073313 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1407-15_0_5_load_64 | 69 | 0.0024331 | 0.00060979 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1407-15_0_5_load_67 | 70 | 0.00069851 | 0.00017506 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1407-15_0_5_load_74 | 71 | 0.019159 | 0.0048018 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1407-15_0_5_line_0 |  | 0 | 1 | 0.011254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1407-15_0_5_line_1 |  | 1 | 2 | 0.068541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1407-15_0_5_line_2 |  | 2 | 3 | 0.011694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1407-15_0_5_line_3 |  | 3 | 6 | 0.036764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1407-15_0_5_line_4 |  | 3 | 7 | 0.024947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1407-15_0_5_line_5 |  | 4 | 5 | 0.037258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1407-15_0_5_line_6 |  | 5 | 8 | 0.0098433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1407-15_0_5_line_7 |  | 5 | 9 | 0.048146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1407-15_0_5_line_8 |  | 6 | 45 | 0.014494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1407-15_0_5_line_9 |  | 7 | 50 | 0.023358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1407-15_0_5_line_10 |  | 8 | 14 | 0.0075813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1407-15_0_5_line_11 |  | 9 | 18 | 0.0009707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1407-15_0_5_line_12 |  | 10 | 11 | 0.042718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_1407-15_0_5_line_13 |  | 11 | 12 | 0.05813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_1407-15_0_5_line_14 |  | 12 | 13 | 0.066469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_1407-15_0_5_line_15 |  | 12 | 14 | 0.011014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1407-15_0_5_line_16 |  | 12 | 15 | 0.18053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1407-15_0_5_line_17 |  | 13 | 16 | 0.034063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_1407-15_0_5_line_18 |  | 15 | 17 | 0.18615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1407-15_0_5_line_19 |  | 16 | 29 | 0.045937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1407-15_0_5_line_20 |  | 16 | 27 | 0.066328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1407-15_0_5_line_21 |  | 17 | 32 | 0.011677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1407-15_0_5_line_22 |  | 18 | 19 | 0.029273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1407-15_0_5_line_23 |  | 19 | 50 | 0.0079037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1407-15_0_5_line_24 |  | 20 | 21 | 0.041598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_1407-15_0_5_line_25 |  | 20 | 22 | 0.010885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_1407-15_0_5_line_26 |  | 21 | 23 | 0.013836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_1407-15_0_5_line_27 |  | 22 | 24 | 0.038104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_1407-15_0_5_line_28 |  | 23 | 25 | 0.040619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_1407-15_0_5_line_29 |  | 24 | 26 | 0.02559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1407-15_0_5_line_30 |  | 25 | 27 | 0.0036984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_1407-15_0_5_line_31 |  | 26 | 28 | 0.048421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_1407-15_0_5_line_32 |  | 28 | 52 | 0.014929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_1407-15_0_5_line_33 |  | 29 | 30 | 0.021949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1407-15_0_5_line_34 |  | 30 | 31 | 0.054082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1407-15_0_5_line_35 |  | 31 | 71 | 0.015033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1407-15_0_5_line_36 |  | 32 | 33 | 0.023312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1407-15_0_5_line_37 |  | 34 | 35 | 0.024577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1407-15_0_5_line_38 |  | 34 | 36 | 0.024549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1407-15_0_5_line_39 |  | 36 | 37 | 0.059814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1407-15_0_5_line_40 |  | 37 | 38 | 0.03855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1407-15_0_5_line_41 |  | 37 | 39 | 0.044208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1407-15_0_5_line_42 |  | 38 | 48 | 0.030785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1407-15_0_5_line_43 |  | 40 | 41 | 0.076405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1407-15_0_5_line_44 |  | 40 | 42 | 0.030734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1407-15_0_5_line_45 |  | 41 | 45 | 0.066419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1407-15_0_5_line_46 |  | 42 | 43 | 0.065283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1407-15_0_5_line_47 |  | 43 | 44 | 0.052219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1407-15_0_5_line_48 |  | 44 | 47 | 0.023031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1407-15_0_5_line_49 |  | 45 | 46 | 0.049531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1407-15_0_5_line_50 |  | 46 | 49 | 0.024851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1407-15_0_5_line_51 |  | 48 | 49 | 0.0012444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1407-15_0_5_line_52 |  | 51 | 52 | 0.043143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_1407-15_0_5_line_53 |  | 51 | 53 | 0.064887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_1407-15_0_5_line_54 |  | 53 | 54 | 0.017205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_1407-15_0_5_line_55 |  | 54 | 55 | 0.08372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_1407-15_0_5_line_56 |  | 55 | 58 | 0.032138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_1407-15_0_5_line_57 |  | 56 | 57 | 0.074441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_1407-15_0_5_line_58 |  | 57 | 70 | 0.048674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1407-15_0_5_line_59 |  | 57 | 63 | 0.043268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_1407-15_0_5_line_60 |  | 58 | 61 | 0.092553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_1407-15_0_5_line_61 |  | 59 | 60 | 0.032887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_1407-15_0_5_line_62 |  | 59 | 61 | 0.059915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_1407-15_0_5_line_63 |  | 60 | 62 | 0.16789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_1407-15_0_5_line_64 |  | 62 | 63 | 0.02314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_1407-15_0_5_line_65 |  | 63 | 64 | 0.028691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_1407-15_0_5_line_66 |  | 64 | 69 | 0.011813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_1407-15_0_5_line_67 |  | 65 | 66 | 0.029418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1407-15_0_5_line_68 |  | 65 | 67 | 0.021607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_1407-15_0_5_line_69 |  | 66 | 68 | 0.041822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1407-15_0_5_line_70 |  | 67 | 69 | 0.040021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1407-15_0_5_trafo_5 | 0.63 MVA 20/0.4 kV | 72 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2662736.0951 | 1195698.7848 | 2662733.8037 | 1195687.7669
1 | 2662719.8478 | 1195620.6615 | 2662719.8478 | 1195620.6615 | 2662733.8037 | 1195687.7669
2 | 2662708.9749 | 1195616.3561 | 2662719.8478 | 1195620.6615
3 | 2662708.9749 | 1195616.3561 | 2662715.8859 | 1195601.7756 | 2662719.6687 | 1195594.8779 | 2662722.6361 | 1195590.184 | 2662725.8426 | 1195585.9263 | 2662727.0163 | 1195584.4592
4 | 2662708.9749 | 1195616.3561 | 2662698.8295 | 1195639.1467
5 | 2662632.154 | 1195724.5814 | 2662652.6115 | 1195731.7775 | 2662667.9247 | 1195734.6042
6 | 2662632.154 | 1195724.5814 | 2662625.1819 | 1195731.5299
7 | 2662632.154 | 1195724.5814 | 2662634.9475 | 1195721.9202 | 2662666.8213 | 1195691.1724
8 | 2662737.0379 | 1195574.0367 | 2662733.016 | 1195577.5744 | 2662729.2473 | 1195581.6706 | 2662727.0163 | 1195584.4592
9 | 2662698.8295 | 1195639.1467 | 2662690.7632 | 1195657.2669 | 2662689.0348 | 1195660.3376
10 | 2662619.8121 | 1195736.8816 | 2662625.1819 | 1195731.5299
11 | 2662667.5199 | 1195690.4984 | 2662666.8213 | 1195691.1724
12 | 2662674.4 | 1195824.2045 | 2662648.0435 | 1195790.5863
13 | 2662612.1785 | 1195744.8397 | 2662648.0435 | 1195790.5863
14 | 2662612.1785 | 1195744.8397 | 2662601.7169 | 1195755.8366 | 2662600.2533 | 1195757.3667 | 2662598.3893 | 1195759.3038 | 2662584.8403 | 1195773.3926 | 2662582.2984 | 1195776.0342 | 2662566.0699 | 1195792.8298
15 | 2662619.8121 | 1195736.8816 | 2662612.1785 | 1195744.8397
16 | 2662612.1785 | 1195744.8397 | 2662465.7157 | 1195639.2947
17 | 2662542.3778 | 1195817.3631 | 2662566.0699 | 1195792.8298
18 | 2662465.7157 | 1195639.2947 | 2662279.8843 | 1195650.2609
19 | 2662542.3778 | 1195817.3631 | 2662575.7692 | 1195848.9104
20 | 2662542.3778 | 1195817.3631 | 2662507.0636 | 1195853.9266 | 2662496.299 | 1195865.0719
21 | 2662279.8843 | 1195650.2609 | 2662270.2161 | 1195656.809
22 | 2662685.1579 | 1195667.2251 | 2662679.637 | 1195676.406 | 2662667.5199 | 1195690.4984
23 | 2662685.1579 | 1195667.2251 | 2662689.0348 | 1195660.3376
24 | 2662455.8992 | 1195906.901 | 2662426.0561 | 1195935.8798
25 | 2662418.2471 | 1195943.4627 | 2662426.0561 | 1195935.8798
26 | 2662455.8992 | 1195906.901 | 2662465.5109 | 1195896.9492
27 | 2662418.2471 | 1195943.4627 | 2662442.7518 | 1195972.6415
28 | 2662493.7297 | 1195867.7322 | 2662465.5109 | 1195896.9492
29 | 2662459.2091 | 1195992.2378 | 2662442.7518 | 1195972.6415
30 | 2662496.299 | 1195865.0719 | 2662493.7297 | 1195867.7322
31 | 2662459.2091 | 1195992.2378 | 2662468.3109 | 1196003.0756 | 2662490.052 | 1196029.5634
32 | 2662499.524 | 1196041.1034 | 2662490.052 | 1196029.5634
33 | 2662591.7242 | 1195863.9842 | 2662575.7692 | 1195848.9104
34 | 2662591.7242 | 1195863.9842 | 2662591.7242 | 1195863.9842 | 2662553.6189 | 1195902.3616
35 | 2662553.6189 | 1195902.3616 | 2662543.0269 | 1195913.0293
36 | 2662270.2161 | 1195656.809 | 2662265.3668 | 1195660.0933 | 2662260.2648 | 1195659.84 | 2662248.3282 | 1195662.9971
37 | 2662822.1047 | 1195418.4529 | 2662841.8836 | 1195403.8641
38 | 2662804.1648 | 1195435.2042 | 2662821.6635 | 1195418.7783 | 2662822.1047 | 1195418.4529
39 | 2662744.4693 | 1195431.4424 | 2662804.1648 | 1195435.2042
40 | 2662744.4693 | 1195431.4424 | 2662744.9922 | 1195465.112 | 2662745.2228 | 1195469.9827
41 | 2662744.4693 | 1195431.4424 | 2662736.9042 | 1195427.005 | 2662712.5367 | 1195402.4018 | 2662711.8834 | 1195401.9235
42 | 2662745.2228 | 1195469.9827 | 2662746.6786 | 1195500.7337
43 | 2662857.2882 | 1195499.533 | 2662850.9953 | 1195506.004 | 2662845.7293 | 1195510.4624 | 2662835.9547 | 1195518.3644 | 2662815.8552 | 1195534.3404 | 2662807.2817 | 1195540.3317 | 2662798.4473 | 1195545.7755 | 2662797.2136 | 1195546.4333
44 | 2662857.2882 | 1195499.533 | 2662861.997 | 1195503.1401 | 2662866.96 | 1195508.6622 | 2662871.9561 | 1195517.5532 | 2662875.3257 | 1195523.8923
45 | 2662737.0379 | 1195574.0367 | 2662744.3868 | 1195569.2887 | 2662751.3277 | 1195565.6594 | 2662766.7799 | 1195559.7958 | 2662781.8543 | 1195554.3508 | 2662788.6323 | 1195551.0089 | 2662797.2136 | 1195546.4333
46 | 2662875.3257 | 1195523.8923 | 2662875.3555 | 1195589.1752
47 | 2662875.3555 | 1195589.1752 | 2662832.8529 | 1195619.5127
48 | 2662814.1072 | 1195632.893 | 2662832.8529 | 1195619.5127
49 | 2662737.0379 | 1195574.0367 | 2662735.7296 | 1195570.9211 | 2662736.7518 | 1195563.5387 | 2662739.2723 | 1195554.9601 | 2662745.1269 | 1195543.7705 | 2662746.0586 | 1195541.39 | 2662746.2675 | 1195535.2775 | 2662746.5321 | 1195527.4868 | 2662746.539 | 1195526.8254
50 | 2662746.539 | 1195526.8254 | 2662746.7884 | 1195503.053 | 2662746.7375 | 1195501.9766
51 | 2662746.6786 | 1195500.7337 | 2662746.7375 | 1195501.9766
52 | 2662526.8964 | 1196074.4518 | 2662499.524 | 1196041.1034
53 | 2662526.8964 | 1196074.4518 | 2662536.5791 | 1196086.2485 | 2662573.9012 | 1196053.5419
54 | 2662562.8356 | 1196040.3679 | 2662573.9012 | 1196053.5419 | 2662573.9012 | 1196053.5419
55 | 2662562.8356 | 1196040.3679 | 2662624.8035 | 1195984.0745
56 | 2662655.1914 | 1195994.5359 | 2662624.8035 | 1195984.0745
57 | 2662753.515 | 1196203.722 | 2662696.7122 | 1196251.8348
58 | 2662753.515 | 1196203.722 | 2662744.8945 | 1196189.6123 | 2662727.4398 | 1196166.4824 | 2662725.359 | 1196164.1005
59 | 2662786.1313 | 1196175.192 | 2662753.515 | 1196203.722
60 | 2662707.262 | 1195918.0201 | 2662655.1914 | 1195994.5359
61 | 2662746.8106 | 1195963.0275 | 2662768.5187 | 1195987.7319
62 | 2662746.8106 | 1195963.0275 | 2662707.262 | 1195918.0201
63 | 2662768.5187 | 1195987.7319 | 2662794.4573 | 1196153.6014
64 | 2662786.1313 | 1196175.192 | 2662793.4688 | 1196156.2357 | 2662794.4573 | 1196153.6014
65 | 2662786.1313 | 1196175.192 | 2662789.7682 | 1196177.8206 | 2662803.141 | 1196197.9946
66 | 2662809.668 | 1196207.8412 | 2662803.141 | 1196197.9946
67 | 2662849.5514 | 1196228.909 | 2662873.7475 | 1196212.1762
68 | 2662831.7799 | 1196241.1987 | 2662849.5514 | 1196228.909
69 | 2662875.2112 | 1196179.6412 | 2662886.2639 | 1196197.1676 | 2662886.2221 | 1196201.1473 | 2662884.8613 | 1196204.4905 | 2662873.7475 | 1196212.1762
70 | 2662831.7799 | 1196241.1987 | 2662809.668 | 1196207.8412

## bus_geodata
| x | y | coords
0 | 2662736.0951 | 1195698.7848
1 | 2662733.8037 | 1195687.7669
2 | 2662719.8478 | 1195620.6615
3 | 2662708.9749 | 1195616.3561
4 | 2662667.9247 | 1195734.6042
5 | 2662632.154 | 1195724.5814
6 | 2662727.0163 | 1195584.4592
7 | 2662698.8295 | 1195639.1467
8 | 2662625.1819 | 1195731.5299
9 | 2662666.8213 | 1195691.1724
10 | 2662674.4 | 1195824.2045
11 | 2662648.0435 | 1195790.5863
12 | 2662612.1785 | 1195744.8397
13 | 2662566.0699 | 1195792.8298
14 | 2662619.8121 | 1195736.8816
15 | 2662465.7157 | 1195639.2947
16 | 2662542.3778 | 1195817.3631
17 | 2662279.8843 | 1195650.2609
18 | 2662667.5199 | 1195690.4984
19 | 2662685.1579 | 1195667.2251
20 | 2662426.0561 | 1195935.8798
21 | 2662455.8992 | 1195906.901
22 | 2662418.2471 | 1195943.4627
23 | 2662465.5109 | 1195896.9492
24 | 2662442.7518 | 1195972.6415
25 | 2662493.7297 | 1195867.7322
26 | 2662459.2091 | 1195992.2378
27 | 2662496.299 | 1195865.0719
28 | 2662490.052 | 1196029.5634
29 | 2662575.7692 | 1195848.9104
30 | 2662591.7242 | 1195863.9842
31 | 2662553.6189 | 1195902.3616
32 | 2662270.2161 | 1195656.809
33 | 2662248.3282 | 1195662.9971
34 | 2662822.1047 | 1195418.4529
35 | 2662841.8836 | 1195403.8641
36 | 2662804.1648 | 1195435.2042
37 | 2662744.4693 | 1195431.4424
38 | 2662745.2228 | 1195469.9827
39 | 2662711.8834 | 1195401.9235
40 | 2662857.2882 | 1195499.533
41 | 2662797.2136 | 1195546.4333
42 | 2662875.3257 | 1195523.8923
43 | 2662875.3555 | 1195589.1752
44 | 2662832.8529 | 1195619.5127
45 | 2662737.0379 | 1195574.0367
46 | 2662746.539 | 1195526.8254
47 | 2662814.1072 | 1195632.893
48 | 2662746.6786 | 1195500.7337
49 | 2662746.7375 | 1195501.9766
50 | 2662689.0348 | 1195660.3376
51 | 2662526.8964 | 1196074.4518
52 | 2662499.524 | 1196041.1034
53 | 2662573.9012 | 1196053.5419
54 | 2662562.8356 | 1196040.3679
55 | 2662624.8035 | 1195984.0745
56 | 2662696.7122 | 1196251.8348
57 | 2662753.515 | 1196203.722
58 | 2662655.1914 | 1195994.5359
59 | 2662746.8106 | 1195963.0275
60 | 2662768.5187 | 1195987.7319
61 | 2662707.262 | 1195918.0201
62 | 2662794.4573 | 1196153.6014
63 | 2662786.1313 | 1196175.192
64 | 2662803.141 | 1196197.9946
65 | 2662849.5514 | 1196228.909
66 | 2662873.7475 | 1196212.1762
67 | 2662831.7799 | 1196241.1987
68 | 2662875.2112 | 1196179.6412
69 | 2662809.668 | 1196207.8412
70 | 2662725.359 | 1196164.1005
71 | 2662543.0269 | 1195913.0293
72 | 2662674.4 | 1195824.2045

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9812 | -0.36088 | 0.0063585 | 0.0015936
1 | 0.98126 | -0.35958 | 0.011094 | 0.0027803
2 | 0.98237 | -0.33795 | 0.00089436 | 0.00022415
3 | 0.98257 | -0.33408 | 0 | 0
4 | 0.9901 | -0.18846 | 0.020972 | 0.005256
5 | 0.99081 | -0.17458 | 0 | 0
6 | 0.98118 | -0.36119 | 0.00054405 | 0.00013635
7 | 0.98393 | -0.30748 | 0.00064333 | 0.00016123
8 | 0.99167 | -0.15805 | 0.0037913 | 0.0009502
9 | 0.98753 | -0.23778 | 0.0084547 | 0.0021189
10 | 1 | 0 | -0.37385 | -0.095857
11 | 0.99711 | -0.054596 | 0.018243 | 0.004572
12 | 0.99336 | -0.12565 | 0 | 0
13 | 0.99035 | -0.18324 | 0 | 0
14 | 0.99236 | -0.14483 | 0 | 0
15 | 0.99265 | -0.13955 | 0.0010773 | 0.00026999
16 | 0.9888 | -0.21288 | 0 | 0
17 | 0.99209 | -0.15032 | 0.00085971 | 0.00021546
18 | 0.98747 | -0.23891 | 0 | 0
19 | 0.9857 | -0.27311 | 0 | 0
20 | 0.98414 | -0.30267 | 0.0022246 | 0.00055755
21 | 0.98528 | -0.28065 | 0 | 0
22 | 0.98385 | -0.30835 | 0 | 0
23 | 0.98566 | -0.27333 | 0.0021942 | 0.00054993
24 | 0.98282 | -0.32827 | 0.00035652 | 8.9353e-05
25 | 0.98679 | -0.25157 | 0.0013264 | 0.00033243
26 | 0.98213 | -0.34164 | 0.0018965 | 0.00047532
27 | 0.98689 | -0.24958 | 0.0040705 | 0.0010202
28 | 0.98085 | -0.36666 | 0.0026925 | 0.00067481
29 | 0.98499 | -0.28654 | 0.0061521 | 0.0015419
30 | 0.98329 | -0.3195 | 0.0019633 | 0.00049206
31 | 0.97921 | -0.39928 | 0.062325 | 0.01562
32 | 0.99207 | -0.15082 | 0.0012148 | 0.00030445
33 | 0.99204 | -0.15131 | 0.0011919 | 0.00029871
34 | 0.97757 | -0.4318 | 0.0012787 | 0.00032048
35 | 0.97749 | -0.4335 | 0.0037981 | 0.0009519
36 | 0.97769 | -0.42953 | 0 | 0
37 | 0.97797 | -0.42399 | 0 | 0
38 | 0.97852 | -0.41331 | 0.0015885 | 0.00039811
39 | 0.97756 | -0.43216 | 0.010134 | 0.0025398
40 | 0.97862 | -0.41128 | 0 | 0
41 | 0.97965 | -0.391 | 0.0013734 | 0.00034422
42 | 0.9782 | -0.41945 | 0.0026176 | 0.00065603
43 | 0.97748 | -0.4337 | 0 | 0
44 | 0.9769 | -0.44512 | 0.0047054 | 0.0011793
45 | 0.98064 | -0.37175 | 0 | 0
46 | 0.97952 | -0.39357 | 0.0024043 | 0.00060258
47 | 0.97674 | -0.44818 | 0.0072686 | 0.0018217
48 | 0.979 | -0.40389 | 0.0030433 | 0.00076272
49 | 0.97902 | -0.40344 | 0.0020152 | 0.00050505
50 | 0.98523 | -0.28237 | 0.0054541 | 0.0013669
51 | 0.97949 | -0.39321 | 0.001285 | 0.00032205
52 | 0.98046 | -0.37424 | 0.018941 | 0.004747
53 | 0.97804 | -0.4215 | 0.0086166 | 0.0021595
54 | 0.97768 | -0.42848 | 0.0014786 | 0.00037058
55 | 0.97597 | -0.46203 | 0.0057487 | 0.0014408
56 | 0.9721 | -0.53846 | 0.0065937 | 0.0016525
57 | 0.97233 | -0.53394 | 0 | 0
58 | 0.97535 | -0.47427 | 0.0049077 | 0.00123
59 | 0.97312 | -0.51829 | 0.02101 | 0.0052655
60 | 0.97296 | -0.52145 | 0.0098785 | 0.0024758
61 | 0.97365 | -0.50792 | 0.05196 | 0.013022
62 | 0.97246 | -0.53145 | 0.00061102 | 0.00015314
63 | 0.97239 | -0.53277 | 0 | 0
64 | 0.97235 | -0.53364 | 0.00073876 | 0.00018515
65 | 0.97226 | -0.53538 | 0.0013119 | 0.00032879
66 | 0.97216 | -0.5374 | 0.0008023 | 0.00020108
67 | 0.97229 | -0.53471 | 0 | 0
68 | 0.97204 | -0.53966 | 0.0029252 | 0.00073313
69 | 0.97233 | -0.53397 | 0.0024331 | 0.00060979
70 | 0.9723 | -0.53456 | 0.00069851 | 0.00017506
71 | 0.97894 | -0.40451 | 0.019159 | 0.0048018
72 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0063585 | -0.0015936 | 0.0063589 | 0.0015937 | 3.924e-07 | 1.0899e-07 | 0.0096428 | 0.0096428 | 0.0096428 | 0.9812 | -0.36088 | 0.98126 | -0.35958 | 2.6491
1 | -0.017453 | -0.004374 | 0.017471 | 0.0043847 | 1.8003e-05 | 1.0655e-05 | 0.026466 | 0.026465 | 0.026466 | 0.98126 | -0.35958 | 0.98237 | -0.33795 | 7.2708
2 | -0.018365 | -0.0046088 | 0.018368 | 0.0046109 | 3.3941e-06 | 2.0241e-06 | 0.02782 | 0.02782 | 0.02782 | 0.98237 | -0.33795 | 0.98257 | -0.33408 | 7.6429
3 | 0.040952 | 0.010326 | -0.040899 | -0.010292 | 5.3067e-05 | 3.3498e-05 | 0.062041 | 0.062042 | 0.062042 | 0.98257 | -0.33408 | 0.98118 | -0.36119 | 17.0444
4 | -0.059321 | -0.014937 | 0.059396 | 0.014985 | 7.5542e-05 | 4.8031e-05 | 0.089861 | 0.089861 | 0.089861 | 0.98257 | -0.33408 | 0.98393 | -0.30748 | 24.6872
5 | -0.020972 | -0.005256 | 0.020985 | 0.0052644 | 1.3879e-05 | 8.4033e-06 | 0.031518 | 0.031518 | 0.031518 | 0.9901 | -0.18846 | 0.99081 | -0.17458 | 8.6588
6 | -0.095372 | -0.024175 | 0.095448 | 0.024224 | 7.583e-05 | 4.8404e-05 | 0.14333 | 0.14333 | 0.14333 | 0.99081 | -0.17458 | 0.99167 | -0.15805 | 39.3759
7 | 0.074387 | 0.018911 | -0.074161 | -0.018767 | 0.00022571 | 0.00014384 | 0.11181 | 0.11181 | 0.11181 | 0.99081 | -0.17458 | 0.98753 | -0.23778 | 30.7172
8 | 0.040355 | 0.010156 | -0.040335 | -0.010143 | 2.0368e-05 | 1.2853e-05 | 0.061216 | 0.061216 | 0.061216 | 0.98118 | -0.36119 | 0.98064 | -0.37175 | 16.8177
9 | -0.06004 | -0.015146 | 0.060112 | 0.015192 | 7.2271e-05 | 4.5957e-05 | 0.090834 | 0.090834 | 0.090834 | 0.98393 | -0.30748 | 0.98523 | -0.28237 | 24.9544
10 | -0.099239 | -0.025174 | 0.099303 | 0.025214 | 6.3132e-05 | 4.0306e-05 | 0.14902 | 0.14902 | 0.14902 | 0.99167 | -0.15805 | 0.99236 | -0.14483 | 40.9388
11 | 0.065706 | 0.016648 | -0.065703 | -0.016646 | 3.5728e-06 | 2.2742e-06 | 0.099071 | 0.099071 | 0.099071 | 0.98753 | -0.23778 | 0.98747 | -0.23891 | 27.2174
12 | 0.3722 | 0.095857 | -0.37121 | -0.095229 | 0.00098598 | 0.00062823 | 0.55475 | 0.55475 | 0.55475 | 1 | 0 | 0.99711 | -0.054596 | 30.4808
13 | 0.35297 | 0.090657 | -0.35175 | -0.089884 | 0.0012132 | 0.0007727 | 0.52753 | 0.52753 | 0.52753 | 0.99711 | -0.054596 | 0.99336 | -0.12565 | 28.9851
14 | 0.24801 | 0.063525 | -0.24732 | -0.063088 | 0.00068987 | 0.00043723 | 0.372 | 0.372 | 0.372 | 0.99336 | -0.12565 | 0.99035 | -0.18324 | 20.4396
15 | 0.099394 | 0.025273 | -0.099303 | -0.025214 | 9.1717e-05 | 5.8556e-05 | 0.14902 | 0.14902 | 0.14902 | 0.99336 | -0.12565 | 0.99236 | -0.14483 | 40.9388
16 | 0.0043482 | 0.0010864 | -0.0043453 | -0.0010869 | 2.8714e-06 | -4.977e-07 | 0.0065122 | 0.0065131 | 0.0065131 | 0.99336 | -0.12565 | 0.99265 | -0.13955 | 1.7893
17 | 0.24732 | 0.063088 | -0.24697 | -0.062864 | 0.00035353 | 0.00022407 | 0.372 | 0.372 | 0.372 | 0.99035 | -0.18324 | 0.9888 | -0.21288 | 20.4396
18 | 0.0032681 | 0.00081689 | -0.0032664 | -0.00081822 | 1.6752e-06 | -1.333e-06 | 0.0048982 | 0.0048991 | 0.0048991 | 0.99265 | -0.13955 | 0.99209 | -0.15032 | 1.3459
19 | 0.090367 | 0.022945 | -0.090048 | -0.022741 | 0.00031907 | 0.00020362 | 0.1361 | 0.1361 | 0.1361 | 0.9888 | -0.21288 | 0.98499 | -0.28654 | 37.3891
20 | 0.1566 | 0.039918 | -0.15632 | -0.039746 | 0.00027684 | 0.00017293 | 0.2359 | 0.23591 | 0.23591 | 0.9888 | -0.21288 | 0.98689 | -0.24958 | 12.9619
21 | 0.0024067 | 0.00060276 | -0.0024066 | -0.00060287 | 5.7054e-08 | -1.1426e-07 | 0.0036096 | 0.0036097 | 0.0036097 | 0.99209 | -0.15032 | 0.99207 | -0.15082 | 0.99166
22 | 0.065703 | 0.016646 | -0.065595 | -0.016577 | 0.00010774 | 6.8583e-05 | 0.099071 | 0.099071 | 0.099071 | 0.98747 | -0.23891 | 0.9857 | -0.27311 | 27.2174
23 | 0.065595 | 0.016577 | -0.065566 | -0.016559 | 2.9091e-05 | 1.8518e-05 | 0.099071 | 0.099071 | 0.099071 | 0.9857 | -0.27311 | 0.98523 | -0.28237 | 27.2174
24 | -0.14835 | -0.037605 | 0.14851 | 0.037703 | 0.00015718 | 9.7951e-05 | 0.22446 | 0.22446 | 0.22446 | 0.98414 | -0.30267 | 0.98528 | -0.28065 | 12.3329
25 | 0.14613 | 0.037047 | -0.14609 | -0.037022 | 3.9907e-05 | 2.4849e-05 | 0.2211 | 0.2211 | 0.2211 | 0.98414 | -0.30267 | 0.98385 | -0.30835 | 12.1481
26 | -0.14851 | -0.037703 | 0.14856 | 0.037735 | 5.2279e-05 | 3.2577e-05 | 0.22446 | 0.22446 | 0.22446 | 0.98528 | -0.28065 | 0.98566 | -0.27333 | 12.3328
27 | 0.14609 | 0.037022 | -0.14595 | -0.036935 | 0.0001397 | 8.6989e-05 | 0.2211 | 0.2211 | 0.2211 | 0.98385 | -0.30835 | 0.98282 | -0.32827 | 12.1481
28 | -0.15076 | -0.038285 | 0.15091 | 0.038384 | 0.00015805 | 9.8558e-05 | 0.22777 | 0.22777 | 0.22777 | 0.98566 | -0.27333 | 0.98679 | -0.25157 | 12.5148
29 | 0.14559 | 0.036846 | -0.1455 | -0.036788 | 9.3363e-05 | 5.8132e-05 | 0.22056 | 0.22056 | 0.22056 | 0.98282 | -0.32827 | 0.98213 | -0.34164 | 12.1185
30 | -0.15224 | -0.038716 | 0.15225 | 0.038725 | 1.4644e-05 | 9.136e-06 | 0.22977 | 0.22977 | 0.22977 | 0.98679 | -0.25157 | 0.98689 | -0.24958 | 12.6247
31 | 0.1436 | 0.036313 | -0.14343 | -0.036206 | 0.00017209 | 0.00010708 | 0.21768 | 0.21768 | 0.21768 | 0.98213 | -0.34164 | 0.98085 | -0.36666 | 11.9607
32 | 0.14074 | 0.035531 | -0.14069 | -0.035499 | 5.1087e-05 | 3.1754e-05 | 0.2136 | 0.2136 | 0.2136 | 0.98085 | -0.36666 | 0.98046 | -0.37424 | 11.7363
33 | 0.083896 | 0.0212 | -0.083763 | -0.021115 | 0.00013235 | 8.4423e-05 | 0.1268 | 0.1268 | 0.1268 | 0.98499 | -0.28654 | 0.98329 | -0.3195 | 34.8359
34 | 0.0818 | 0.020623 | -0.081489 | -0.020425 | 0.00031099 | 0.00019835 | 0.12383 | 0.12383 | 0.12383 | 0.98329 | -0.3195 | 0.97921 | -0.39928 | 34.0197
35 | 0.019164 | 0.0048047 | -0.019159 | -0.0048018 | 4.7812e-06 | 2.8709e-06 | 0.029123 | 0.029123 | 0.029123 | 0.97921 | -0.39928 | 0.97894 | -0.40451 | 8.0007
36 | 0.0011919 | 0.00029842 | -0.0011919 | -0.00029871 | 2.7938e-08 | -2.8312e-07 | 0.0017876 | 0.0017877 | 0.0017877 | 0.99207 | -0.15082 | 0.99204 | -0.15131 | 0.49114
37 | 0.0037984 | 0.00095179 | -0.0037981 | -0.0009519 | 3.081e-07 | -1.1093e-07 | 0.0057817 | 0.0057818 | 0.0057818 | 0.97757 | -0.4318 | 0.97749 | -0.4335 | 1.5884
38 | -0.0050772 | -0.0012723 | 0.0050777 | 0.0012723 | 5.498e-07 | 4.4056e-08 | 0.0077281 | 0.007728 | 0.0077281 | 0.97757 | -0.4318 | 0.97769 | -0.42953 | 2.1231
39 | -0.0050777 | -0.0012723 | 0.0050791 | 0.0012724 | 1.3395e-06 | 1.07e-07 | 0.007728 | 0.0077278 | 0.007728 | 0.97769 | -0.42953 | 0.97797 | -0.42399 | 2.1231
40 | -0.015217 | -0.0038142 | 0.015225 | 0.0038187 | 7.7495e-06 | 4.4757e-06 | 0.023153 | 0.023153 | 0.023153 | 0.97797 | -0.42399 | 0.97852 | -0.41331 | 6.3608
41 | 0.010138 | 0.0025418 | -0.010134 | -0.0025398 | 3.9447e-06 | 1.9702e-06 | 0.015426 | 0.015426 | 0.015426 | 0.97797 | -0.42399 | 0.97756 | -0.43216 | 4.2378
42 | -0.016813 | -0.0042168 | 0.016821 | 0.0042212 | 7.5473e-06 | 4.4434e-06 | 0.025569 | 0.025569 | 0.025569 | 0.97852 | -0.41331 | 0.979 | -0.40389 | 7.0244
43 | -0.014613 | -0.0036686 | 0.014627 | 0.0036767 | 1.4148e-05 | 8.0939e-06 | 0.022222 | 0.022221 | 0.022222 | 0.97862 | -0.41128 | 0.97965 | -0.391 | 6.1049
44 | 0.014613 | 0.0036686 | -0.014607 | -0.0036653 | 5.6912e-06 | 3.2564e-06 | 0.022222 | 0.022222 | 0.022222 | 0.97862 | -0.41128 | 0.9782 | -0.41945 | 6.1049
45 | -0.016001 | -0.0040209 | 0.016015 | 0.0040295 | 1.4716e-05 | 8.5814e-06 | 0.024308 | 0.024307 | 0.024308 | 0.97965 | -0.391 | 0.98064 | -0.37175 | 6.6779
46 | 0.01199 | 0.0030093 | -0.011982 | -0.0030049 | 8.145e-06 | 4.3939e-06 | 0.01824 | 0.01824 | 0.01824 | 0.9782 | -0.41945 | 0.97748 | -0.4337 | 5.0111
47 | 0.011982 | 0.0030049 | -0.011975 | -0.0030014 | 6.5153e-06 | 3.5156e-06 | 0.01824 | 0.018241 | 0.018241 | 0.97748 | -0.4337 | 0.9769 | -0.44512 | 5.0112
48 | 0.0072697 | 0.0018221 | -0.0072686 | -0.0018217 | 1.059e-06 | 3.8947e-07 | 0.011073 | 0.011073 | 0.011073 | 0.9769 | -0.44512 | 0.97674 | -0.44818 | 3.0421
49 | 0.02432 | 0.0061137 | -0.024294 | -0.0060981 | 2.5303e-05 | 1.557e-05 | 0.036909 | 0.036909 | 0.036909 | 0.98064 | -0.37175 | 0.97952 | -0.39357 | 10.14
50 | 0.02189 | 0.0054955 | -0.02188 | -0.0054893 | 1.0307e-05 | 6.2841e-06 | 0.033257 | 0.033257 | 0.033257 | 0.97952 | -0.39357 | 0.97902 | -0.40344 | 9.1366
51 | -0.019864 | -0.004984 | 0.019864 | 0.0049842 | 4.2543e-07 | 2.5663e-07 | 0.030194 | 0.030194 | 0.030194 | 0.979 | -0.40389 | 0.97902 | -0.40344 | 8.2951
52 | -0.12163 | -0.030684 | 0.12174 | 0.030752 | 0.00011057 | 6.8047e-05 | 0.18486 | 0.18485 | 0.18486 | 0.97949 | -0.39321 | 0.98046 | -0.37424 | 10.1569
53 | 0.12035 | 0.030362 | -0.12019 | -0.030262 | 0.0001628 | 0.00010012 | 0.1829 | 0.1829 | 0.1829 | 0.97949 | -0.39321 | 0.97804 | -0.4215 | 10.0497
54 | 0.11157 | 0.028102 | -0.11153 | -0.02808 | 3.7201e-05 | 2.273e-05 | 0.1698 | 0.1698 | 0.1698 | 0.97804 | -0.4215 | 0.97768 | -0.42848 | 9.3294
55 | 0.11005 | 0.027709 | -0.10988 | -0.027601 | 0.00017626 | 0.00010757 | 0.16755 | 0.16755 | 0.16755 | 0.97768 | -0.42848 | 0.97597 | -0.46203 | 9.2059
56 | 0.10413 | 0.026161 | -0.10407 | -0.026124 | 6.077e-05 | 3.6886e-05 | 0.15878 | 0.15878 | 0.15878 | 0.97597 | -0.46203 | 0.97535 | -0.47427 | 8.7243
57 | -0.0065937 | -0.0016525 | 0.0065951 | 0.0016516 | 1.4218e-06 | -9.3625e-07 | 0.010093 | 0.010092 | 0.010093 | 0.9721 | -0.53846 | 0.97233 | -0.53394 | 1.3864
58 | 0.00069854 | 0.00017447 | -0.00069851 | -0.00017506 | 2.0855e-08 | -5.9036e-07 | 0.0010688 | 0.001069 | 0.001069 | 0.97233 | -0.53394 | 0.9723 | -0.53456 | 0.29369
59 | -0.0072937 | -0.0018261 | 0.0072941 | 0.0018237 | 4.0422e-07 | -2.4248e-06 | 0.011161 | 0.01116 | 0.011161 | 0.97233 | -0.53394 | 0.97239 | -0.53277 | 0.61326
60 | 0.09916 | 0.024894 | -0.099001 | -0.024798 | 0.00015889 | 9.5927e-05 | 0.1513 | 0.1513 | 0.1513 | 0.97535 | -0.47427 | 0.97365 | -0.50792 | 8.3131
61 | 0.026009 | 0.0064989 | -0.026005 | -0.0064984 | 3.9e-06 | 4.5348e-07 | 0.039764 | 0.039764 | 0.039764 | 0.97312 | -0.51829 | 0.97296 | -0.52145 | 2.1849
62 | -0.047018 | -0.011764 | 0.047042 | 0.011776 | 2.3223e-05 | 1.1139e-05 | 0.07189 | 0.071888 | 0.07189 | 0.97312 | -0.51829 | 0.97365 | -0.50792 | 3.95
63 | 0.016126 | 0.0040227 | -0.016119 | -0.0040282 | 7.656e-06 | -5.52e-06 | 0.024656 | 0.02466 | 0.02466 | 0.97296 | -0.52145 | 0.97246 | -0.53145 | 1.355
64 | 0.015508 | 0.003875 | -0.015507 | -0.0038758 | 9.7693e-07 | -8.1013e-07 | 0.023725 | 0.023726 | 0.023726 | 0.97246 | -0.53145 | 0.97239 | -0.53277 | 1.3036
65 | 0.0082127 | 0.0020522 | -0.0082124 | -0.0020538 | 3.3977e-07 | -1.562e-06 | 0.012565 | 0.012566 | 0.012566 | 0.97239 | -0.53277 | 0.97235 | -0.53364 | 0.69044
66 | 0.0074736 | 0.0018686 | -0.0074735 | -0.0018693 | 1.1587e-07 | -6.5848e-07 | 0.011436 | 0.011436 | 0.011436 | 0.97235 | -0.53364 | 0.97233 | -0.53397 | 0.62834
67 | 0.0037282 | 0.00093375 | -0.0037278 | -0.00093389 | 3.5915e-07 | -1.3494e-07 | 0.0057057 | 0.0057058 | 0.0057058 | 0.97226 | -0.53538 | 0.97216 | -0.5374 | 1.5675
68 | -0.0050401 | -0.0012625 | 0.0050402 | 0.0012618 | 1.6069e-07 | -7.0106e-07 | 0.0077135 | 0.0077132 | 0.0077135 | 0.97226 | -0.53538 | 0.97229 | -0.53471 | 0.70636
69 | 0.0029255 | 0.00073281 | -0.0029252 | -0.00073313 | 3.1447e-07 | -3.1723e-07 | 0.0044778 | 0.004478 | 0.004478 | 0.97216 | -0.5374 | 0.97204 | -0.53966 | 1.2302
70 | -0.0050402 | -0.0012618 | 0.0050404 | 0.0012595 | 1.7855e-07 | -2.3676e-06 | 0.0077132 | 0.0077123 | 0.0077132 | 0.97229 | -0.53471 | 0.97233 | -0.53397 | 0.4238

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39739 | 0.10176

## res_load
| p_mw | q_mvar
0 | 0.0063585 | 0.0015936
1 | 0.011094 | 0.0027803
2 | 0.00089436 | 0.00022415
3 | 0.020972 | 0.005256
4 | 0.00054405 | 0.00013635
5 | 0.00064333 | 0.00016123
6 | 0.0037913 | 0.0009502
7 | 0.0084547 | 0.0021189
8 | 0.023543 | 0.0059005
9 | 0.018243 | 0.004572
10 | 0.0010773 | 0.00026999
11 | 0.00085971 | 0.00021546
12 | 0.0022246 | 0.00055755
13 | 0.0021942 | 0.00054993
14 | 0.00035652 | 8.9353e-05
15 | 0.0013264 | 0.00033243
16 | 0.0018965 | 0.00047532
17 | 0.0040705 | 0.0010202
18 | 0.0026925 | 0.00067481
19 | 0.0061521 | 0.0015419
20 | 0.0019633 | 0.00049206
21 | 0.062325 | 0.01562
22 | 0.0012148 | 0.00030445
23 | 0.0011919 | 0.00029871
24 | 0.0012787 | 0.00032048
25 | 0.0037981 | 0.0009519
26 | 0.0015885 | 0.00039811
27 | 0.010134 | 0.0025398
28 | 0.0013734 | 0.00034422
29 | 0.0026176 | 0.00065603
30 | 0.0047054 | 0.0011793
31 | 0.0024043 | 0.00060258
32 | 0.0072686 | 0.0018217
33 | 0.0030433 | 0.00076272
34 | 0.0020152 | 0.00050505
35 | 0.0054541 | 0.0013669
36 | 0.001285 | 0.00032205
37 | 0.018941 | 0.004747
38 | 0.0086166 | 0.0021595
39 | 0.0014786 | 0.00037058
40 | 0.0057487 | 0.0014408
41 | 0.0065937 | 0.0016525
42 | 0.0049077 | 0.00123
43 | 0.02101 | 0.0052655
44 | 0.0098785 | 0.0024758
45 | 0.05196 | 0.013022
46 | 0.00061102 | 0.00015314
47 | 0.00073876 | 0.00018515
48 | 0.0013119 | 0.00032879
49 | 0.0008023 | 0.00020108
50 | 0.0029252 | 0.00073313
51 | 0.0024331 | 0.00060979
52 | 0.00069851 | 0.00017506
53 | 0.019159 | 0.0048018

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1