## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1407-21_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1407-21_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1407-21_0_3_node_12 | 0.4 | n |  | TRUE
3 | bus_LV_1407-21_0_3_node_33 | 0.4 | n |  | TRUE
4 | bus_LV_1407-21_0_3_node_13 | 0.4 | n |  | TRUE
5 | bus_LV_1407-21_0_3_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_1407-21_0_3_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_1407-21_0_3_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_1407-21_0_3_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_1407-21_0_3_node_40 | 0.4 | n |  | TRUE
10 | bus_LV_1407-21_0_3_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_1407-21_0_3_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1407-21_0_3_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_1407-21_0_3_node_22 | 0.4 | n |  | TRUE
14 | bus_LV_1407-21_0_3_node_41 | 0.4 | n |  | TRUE
15 | bus_LV_1407-21_0_3_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1407-21_0_3_node_46 | 0.4 | n |  | TRUE
17 | bus_LV_1407-21_0_3_node_43 | 0.4 | n |  | TRUE
18 | bus_LV_1407-21_0_3_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_1407-21_0_3_node_45 | 0.4 | n |  | TRUE
20 | bus_MV_141_0_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1407-21_0_3_load_0 | 0 | 0.056774 | 0.014229 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1407-21_0_3_load_33 | 3 | 0.054461 | 0.013649 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1407-21_0_3_load_13 | 4 | 0.005324 | 0.0013343 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1407-21_0_3_load_15 | 6 | 0.003245 | 0.00081327 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1407-21_0_3_load_16 | 7 | 0.004654 | 0.0011664 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1407-21_0_3_load_27 | 8 | 0.0023676 | 0.00059338 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1407-21_0_3_load_18 | 10 | 0.0011135 | 0.00027908 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1407-21_0_3_load_19 | 11 | 0.0017939 | 0.0004496 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1407-21_0_3_load_22 | 13 | 0.086283 | 0.021625 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1407-21_0_3_load_41 | 14 | 0.0071925 | 0.0018026 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1407-21_0_3_load_28 | 15 | 0.010031 | 0.0025139 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1407-21_0_3_load_43 | 17 | 0.022486 | 0.0056356 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1407-21_0_3_load_44 | 18 | 0.020316 | 0.0050918 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1407-21_0_3_load_45 | 19 | 0.018982 | 0.0047574 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1407-21_0_3_line_0 |  | 0 | 1 | 0.046034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1407-21_0_3_line_1 |  | 1 | 2 | 0.013346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1407-21_0_3_line_2 |  | 2 | 3 | 0.028383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1407-21_0_3_line_3 |  | 3 | 13 | 0.056053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1407-21_0_3_line_4 |  | 4 | 5 | 0.01357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1407-21_0_3_line_5 |  | 5 | 6 | 0.035175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1407-21_0_3_line_6 |  | 5 | 7 | 0.010843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1407-21_0_3_line_7 |  | 6 | 8 | 0.023027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1407-21_0_3_line_8 |  | 7 | 9 | 0.021697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1407-21_0_3_line_9 |  | 8 | 15 | 0.022158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1407-21_0_3_line_10 |  | 9 | 14 | 0.073299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1407-21_0_3_line_11 |  | 10 | 11 | 0.021357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1407-21_0_3_line_12 |  | 10 | 12 | 0.017905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1407-21_0_3_line_13 |  | 12 | 13 | 0.037561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1407-21_0_3_line_14 |  | 13 | 14 | 0.032846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1407-21_0_3_line_15 |  | 15 | 16 | 0.03802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1407-21_0_3_line_16 |  | 16 | 19 | 0.014082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1407-21_0_3_line_17 |  | 17 | 18 | 0.033971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1407-21_0_3_line_18 |  | 18 | 19 | 0.016126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1407-21_0_3_trafo_22 | 0.63 MVA 20/0.4 kV | 20 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2661891.8773 | 1194771.5343 | 2661869.9129 | 1194731.078
1 | 2661880.0099 | 1194777.7041 | 2661891.8773 | 1194771.5343
2 | 2661880.0099 | 1194777.7041 | 2661854.8263 | 1194790.7947
3 | 2661801.1524 | 1194806.9506 | 2661854.8263 | 1194790.7947
4 | 2661841.7739 | 1194928.6299 | 2661854.4047 | 1194933.5915
5 | 2661841.7739 | 1194928.6299 | 2661808.3037 | 1194917.8122
6 | 2661841.7739 | 1194928.6299 | 2661845.955 | 1194918.6256
7 | 2661786.393 | 1194910.7306 | 2661808.3037 | 1194917.8122
8 | 2661853.6313 | 1194898.3348 | 2661847.6494 | 1194914.5714 | 2661845.955 | 1194918.6256
9 | 2661786.393 | 1194910.7306 | 2661765.3086 | 1194903.916
10 | 2661853.6313 | 1194898.3348 | 2661836.8692 | 1194879.7508 | 2661821.0758 | 1194849.9925 | 2661814.9501 | 1194836.7586
11 | 2661781.8821 | 1194754.9402 | 2661776.2657 | 1194739.788 | 2661774.5603 | 1194734.8781
12 | 2661788.105 | 1194771.7287 | 2661781.8821 | 1194754.9402
13 | 2661788.105 | 1194771.7287 | 2661801.1524 | 1194806.9506 | 2661801.1524 | 1194806.9506
14 | 2661801.1524 | 1194806.9506 | 2661814.9501 | 1194836.7586
15 | 2661729.1316 | 1194892.2235 | 2661765.3086 | 1194903.916
16 | 2661729.1316 | 1194892.2235 | 2661728.4709 | 1194880.9324 | 2661727.4891 | 1194878.3402
17 | 2661709.7447 | 1194831.4916 | 2661721.7773 | 1194863.26
18 | 2661721.7773 | 1194863.26 | 2661727.4891 | 1194878.3402

## bus_geodata
| x | y | coords
0 | 2661869.9129 | 1194731.078
1 | 2661891.8773 | 1194771.5343
2 | 2661880.0099 | 1194777.7041
3 | 2661854.8263 | 1194790.7947
4 | 2661854.4047 | 1194933.5915
5 | 2661841.7739 | 1194928.6299
6 | 2661808.3037 | 1194917.8122
7 | 2661845.955 | 1194918.6256
8 | 2661786.393 | 1194910.7306
9 | 2661853.6313 | 1194898.3348
10 | 2661781.8821 | 1194754.9402
11 | 2661774.5603 | 1194734.8781
12 | 2661788.105 | 1194771.7287
13 | 2661801.1524 | 1194806.9506
14 | 2661814.95 | 1194836.7586
15 | 2661765.3086 | 1194903.916
16 | 2661729.1316 | 1194892.2235
17 | 2661709.7447 | 1194831.4916
18 | 2661721.7773 | 1194863.26
19 | 2661727.4891 | 1194878.3402
20 | 2661788.105 | 1194771.7287

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98973 | -0.19755 | 0.056774 | 0.014229
1 | 0.99213 | -0.15116 | 0 | 0
2 | 0.99282 | -0.13775 | 0 | 0
3 | 0.9943 | -0.1093 | 0.054461 | 0.013649
4 | 0.98855 | -0.2183 | 0.005324 | 0.0013343
5 | 0.98862 | -0.21701 | 0 | 0
6 | 0.9861 | -0.2657 | 0.003245 | 0.00081327
7 | 0.98945 | -0.20102 | 0.004654 | 0.0011664
8 | 0.98451 | -0.29637 | 0.0023676 | 0.00059338
9 | 0.9912 | -0.16731 | 0 | 0
10 | 0.99985 | -0.0028127 | 0.0011135 | 0.00027908
11 | 0.99982 | -0.0034809 | 0.0017939 | 0.0004496
12 | 0.9999 | -0.0019049 | 0 | 0
13 | 1 | 0 | -0.21276 | -0.053826
14 | 0.99713 | -0.054319 | 0.0071925 | 0.0018026
15 | 0.98304 | -0.32503 | 0.010031 | 0.0025139
16 | 0.98087 | -0.3675 | 0 | 0
17 | 0.97871 | -0.40969 | 0.022486 | 0.0056356
18 | 0.97942 | -0.3958 | 0.020316 | 0.0050918
19 | 0.98006 | -0.38327 | 0.018982 | 0.0047574
20 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.056774 | -0.014229 | 0.056899 | 0.014309 | 0.00012577 | 7.9901e-05 | 0.085356 | 0.085356 | 0.085356 | 0.98973 | -0.19755 | 0.99213 | -0.15116 | 23.4496
1 | -0.056899 | -0.014309 | 0.056936 | 0.014332 | 3.6463e-05 | 2.3164e-05 | 0.085356 | 0.085356 | 0.085356 | 0.99213 | -0.15116 | 0.99282 | -0.13775 | 23.4495
2 | -0.056936 | -0.014332 | 0.057013 | 0.014381 | 7.7545e-05 | 4.9261e-05 | 0.085356 | 0.085356 | 0.085356 | 0.99282 | -0.13775 | 0.9943 | -0.1093 | 23.4495
3 | -0.11147 | -0.02803 | 0.11206 | 0.028404 | 0.00058523 | 0.00037382 | 0.16686 | 0.16686 | 0.16686 | 0.9943 | -0.1093 | 1 | 0 | 45.8404
4 | -0.005324 | -0.0013343 | 0.0053243 | 0.0013344 | 3.2682e-07 | 3.5175e-08 | 0.008014 | 0.0080139 | 0.008014 | 0.98855 | -0.2183 | 0.98862 | -0.21701 | 2.2016
5 | 0.078031 | 0.019789 | -0.077849 | -0.019673 | 0.00018221 | 0.00011617 | 0.11753 | 0.11753 | 0.11753 | 0.98862 | -0.21701 | 0.9861 | -0.2657 | 32.289
6 | -0.083355 | -0.021123 | 0.08342 | 0.021164 | 6.4089e-05 | 4.0878e-05 | 0.12555 | 0.12555 | 0.12555 | 0.98862 | -0.21701 | 0.98945 | -0.20102 | 34.4905
7 | 0.074604 | 0.01886 | -0.074494 | -0.01879 | 0.00010955 | 6.9819e-05 | 0.11264 | 0.11264 | 0.11264 | 0.9861 | -0.2657 | 0.98451 | -0.29637 | 30.9437
8 | -0.088074 | -0.022331 | 0.088217 | 0.022422 | 0.00014294 | 9.1204e-05 | 0.13254 | 0.13254 | 0.13254 | 0.98945 | -0.20102 | 0.9912 | -0.16731 | 36.4133
9 | 0.072127 | 0.018196 | -0.072028 | -0.018133 | 9.8827e-05 | 6.2968e-05 | 0.10906 | 0.10906 | 0.10906 | 0.98451 | -0.29637 | 0.98304 | -0.32503 | 29.9607
10 | -0.088217 | -0.022422 | 0.088699 | 0.02273 | 0.00048289 | 0.0003081 | 0.13254 | 0.13254 | 0.13254 | 0.9912 | -0.16731 | 0.99713 | -0.054319 | 36.4133
11 | 0.001794 | 0.00044935 | -0.0017939 | -0.0004496 | 5.7087e-08 | -2.4356e-07 | 0.0026698 | 0.0026699 | 0.0026699 | 0.99985 | -0.0028127 | 0.99982 | -0.0034809 | 0.73348
12 | -0.0029075 | -0.00072843 | 0.0029076 | 0.00072828 | 1.2571e-07 | -1.5439e-07 | 0.004327 | 0.0043269 | 0.004327 | 0.99985 | -0.0028127 | 0.9999 | -0.0019049 | 1.1887
13 | -0.0029076 | -0.00072828 | 0.0029079 | 0.00072795 | 2.6369e-07 | -3.2396e-07 | 0.0043269 | 0.0043267 | 0.0043269 | 0.9999 | -0.0019049 | 1 | 0 | 1.1887
14 | 0.096145 | 0.024694 | -0.095892 | -0.024533 | 0.00025286 | 0.0001614 | 0.14328 | 0.14328 | 0.14328 | 1 | 0 | 0.99713 | -0.054319 | 39.3619
15 | 0.061997 | 0.01562 | -0.061872 | -0.01554 | 0.00012564 | 7.9928e-05 | 0.093874 | 0.093874 | 0.093874 | 0.98304 | -0.32503 | 0.98087 | -0.3675 | 25.7895
16 | 0.061872 | 0.01554 | -0.061825 | -0.01551 | 4.6537e-05 | 2.9606e-05 | 0.093874 | 0.093874 | 0.093874 | 0.98087 | -0.3675 | 0.98006 | -0.38327 | 25.7895
17 | -0.022486 | -0.0056356 | 0.022501 | 0.0056447 | 1.4889e-05 | 9.1018e-06 | 0.034187 | 0.034187 | 0.034187 | 0.97871 | -0.40969 | 0.97942 | -0.3958 | 9.3921
18 | -0.042817 | -0.010736 | 0.042843 | 0.010753 | 2.5591e-05 | 1.6175e-05 | 0.065054 | 0.065054 | 0.065054 | 0.97942 | -0.3958 | 0.98006 | -0.38327 | 17.8719

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29905 | 0.075451

## res_load
| p_mw | q_mvar
0 | 0.056774 | 0.014229
1 | 0.054461 | 0.013649
2 | 0.005324 | 0.0013343
3 | 0.003245 | 0.00081327
4 | 0.004654 | 0.0011664
5 | 0.0023676 | 0.00059338
6 | 0.0011135 | 0.00027908
7 | 0.0017939 | 0.0004496
8 | 0.086283 | 0.021625
9 | 0.0071925 | 0.0018026
10 | 0.010031 | 0.0025139
11 | 0.022486 | 0.0056356
12 | 0.020316 | 0.0050918
13 | 0.018982 | 0.0047574

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1