## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1407-29_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1407-29_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1407-29_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1407-29_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1407-29_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1407-29_0_5_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_1407-29_0_5_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_1407-29_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1407-29_0_5_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1407-29_0_5_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_1407-29_0_5_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1407-29_0_5_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_1407-29_0_5_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1407-29_0_5_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1407-29_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1407-29_0_5_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1407-29_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1407-29_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1407-29_0_5_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1407-29_0_5_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_1407-29_0_5_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1407-29_0_5_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_1407-29_0_5_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1407-29_0_5_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1407-29_0_5_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1407-29_0_5_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1407-29_0_5_node_44 | 0.4 | n |  | TRUE
27 | bus_LV_1407-29_0_5_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1407-29_0_5_node_42 | 0.4 | n |  | TRUE
29 | bus_LV_1407-29_0_5_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1407-29_0_5_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1407-29_0_5_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1407-29_0_5_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_1407-29_0_5_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_1407-29_0_5_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_1407-29_0_5_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1407-29_0_5_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_1407-29_0_5_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_1407-29_0_5_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_1407-29_0_5_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_1407-29_0_5_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_1407-29_0_5_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1407-29_0_5_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_1407-29_0_5_node_40 | 0.4 | n |  | TRUE
44 | bus_MV_141_0_node_50 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1407-29_0_5_load_0 | 0 | 0.037876 | 0.0094927 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1407-29_0_5_load_1 | 1 | 0.012696 | 0.0031819 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1407-29_0_5_load_3 | 3 | 0.01155 | 0.0028946 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1407-29_0_5_load_13 | 5 | 0.0066356 | 0.001663 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1407-29_0_5_load_23 | 6 | 0.019901 | 0.0049876 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1407-29_0_5_load_12 | 8 | 0.0029935 | 0.00075025 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1407-29_0_5_load_11 | 9 | 0.032031 | 0.0080277 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1407-29_0_5_load_14 | 10 | 0.0088208 | 0.0022107 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1407-29_0_5_load_24 | 11 | 0.021696 | 0.0054375 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1407-29_0_5_load_17 | 12 | 0.020798 | 0.0052125 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1407-29_0_5_load_6 | 13 | 0.0073764 | 0.0018487 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1407-29_0_5_load_7 | 14 | 0.0062565 | 0.001568 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1407-29_0_5_load_8 | 15 | 0.0062565 | 0.001568 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1407-29_0_5_load_9 | 16 | 0.0062116 | 0.0015568 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1407-29_0_5_load_10 | 17 | 0.01429 | 0.0035814 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1407-29_0_5_load_15 | 18 | 0.012411 | 0.0031104 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1407-29_0_5_load_38 | 19 | 0.029365 | 0.0073596 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1407-29_0_5_load_16 | 20 | 0.0053525 | 0.0013415 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1407-29_0_5_load_20 | 25 | 0.022518 | 0.0056437 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1407-29_0_5_load_44 | 26 | 0.019114 | 0.0047905 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1407-29_0_5_load_21 | 27 | 0.047637 | 0.011939 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1407-29_0_5_load_25 | 29 | 0.017712 | 0.0044391 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1407-29_0_5_load_26 | 30 | 0.019687 | 0.0049341 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1407-29_0_5_load_27 | 31 | 0.0097066 | 0.0024327 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1407-29_0_5_load_29 | 33 | 0.0053185 | 0.001333 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1407-29_0_5_load_30 | 34 | 0.017577 | 0.0044052 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1407-29_0_5_load_35 | 37 | 0.034289 | 0.0085936 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1407-29_0_5_load_32 | 38 | 0.0050682 | 0.0012702 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1407-29_0_5_load_43 | 39 | 0.0062579 | 0.0015684 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1407-29_0_5_load_45 | 40 | 0.032265 | 0.0080863 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1407-29_0_5_load_33 | 41 | 0.0077925 | 0.001953 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1407-29_0_5_load_41 | 42 | 0.0062594 | 0.0015687 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1407-29_0_5_load_40 | 43 | 0.042842 | 0.010737 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1407-29_0_5_line_0 |  | 0 | 1 | 0.0069783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1407-29_0_5_line_1 |  | 0 | 2 | 0.015359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1407-29_0_5_line_2 |  | 1 | 3 | 0.010843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1407-29_0_5_line_3 |  | 2 | 4 | 0.15421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1407-29_0_5_line_4 |  | 3 | 5 | 0.018689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1407-29_0_5_line_5 |  | 4 | 6 | 0.040374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1407-29_0_5_line_6 |  | 5 | 10 | 0.007732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1407-29_0_5_line_7 |  | 6 | 11 | 0.035281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1407-29_0_5_line_8 |  | 7 | 8 | 0.095568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_1407-29_0_5_line_9 |  | 7 | 9 | 0.14034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1407-29_0_5_line_10 |  | 8 | 12 | 0.024245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1407-29_0_5_line_11 |  | 10 | 20 | 0.020339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1407-29_0_5_line_12 |  | 12 | 22 | 0.015626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1407-29_0_5_line_13 |  | 13 | 14 | 0.0021685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1407-29_0_5_line_14 |  | 13 | 15 | 0.0019998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1407-29_0_5_line_15 |  | 14 | 16 | 0.018829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1407-29_0_5_line_16 |  | 15 | 17 | 0.0028116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1407-29_0_5_line_17 |  | 16 | 18 | 0.0018018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1407-29_0_5_line_18 |  | 17 | 19 | 0.033728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1407-29_0_5_line_19 |  | 18 | 20 | 0.0069625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1407-29_0_5_line_20 |  | 19 | 21 | 0.016414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1407-29_0_5_line_21 |  | 21 | 36 | 0.03264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1407-29_0_5_line_22 |  | 21 | 32 | 0.004306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1407-29_0_5_line_23 |  | 22 | 23 | 0.010659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1407-29_0_5_line_24 |  | 23 | 24 | 0.11367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1407-29_0_5_line_25 |  | 23 | 25 | 0.098072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_1407-29_0_5_line_26 |  | 24 | 26 | 0.065883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1407-29_0_5_line_27 |  | 25 | 27 | 0.021012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1407-29_0_5_line_28 |  | 26 | 28 | 0.091279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1407-29_0_5_line_29 |  | 28 | 43 | 0.070355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1407-29_0_5_line_30 |  | 29 | 30 | 0.0069376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1407-29_0_5_line_31 |  | 29 | 31 | 0.027409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1407-29_0_5_line_32 |  | 30 | 32 | 0.022233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1407-29_0_5_line_33 |  | 31 | 33 | 0.00014752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1407-29_0_5_line_34 |  | 32 | 34 | 0.028038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1407-29_0_5_line_35 |  | 33 | 35 | 0.021555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1407-29_0_5_line_36 |  | 35 | 37 | 0.027046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1407-29_0_5_line_37 |  | 35 | 38 | 0.035175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1407-29_0_5_line_38 |  | 36 | 39 | 0.023541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1407-29_0_5_line_39 |  | 36 | 40 | 0.023378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1407-29_0_5_line_40 |  | 38 | 41 | 0.021747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1407-29_0_5_line_41 |  | 39 | 42 | 0.0062322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_1407-29_0_5_line_42 |  | 42 | 43 | 0.00052528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1407-29_0_5_trafo_7 | 0.63 MVA 20/0.4 kV | 44 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2661855.5253 | 1194104.6599 | 2661860.7923 | 1194100.0823
1 | 2661843.933 | 1194114.7349 | 2661855.5253 | 1194104.6599
2 | 2661860.7923 | 1194100.0823 | 2661868.976 | 1194092.9697
3 | 2661785.3116 | 1193990.1794 | 2661785.529 | 1194017.0861 | 2661787.3982 | 1194036.072 | 2661790.5883 | 1194064.4102 | 2661789.9107 | 1194073.931 | 2661802.0179 | 1194080.0818 | 2661812.9543 | 1194093.3246 | 2661829.2113 | 1194097.595 | 2661843.933 | 1194114.7349
4 | 2661868.976 | 1194092.9697 | 2661883.082 | 1194080.7101
5 | 2661785.3116 | 1193990.1794 | 2661825.5063 | 1193986.3811
6 | 2661883.082 | 1194080.7101 | 2661888.918 | 1194075.638
7 | 2661828.153 | 1194021.5622 | 2661825.5063 | 1193986.3811
8 | 2661801.2679 | 1194210.9389 | 2661890.91 | 1194244.0689
9 | 2661801.2679 | 1194210.9389 | 2661810.3646 | 1194187.5859 | 2661814.8595 | 1194181.8179 | 2661819.2951 | 1194181.0522 | 2661916.4821 | 1194216.5299
10 | 2661890.91 | 1194244.0689 | 2661913.6512 | 1194252.4736
11 | 2661904.2696 | 1194062.2956 | 2661888.918 | 1194075.638
12 | 2661928.3081 | 1194257.8905 | 2661913.6512 | 1194252.4736
13 | 2661926.7333 | 1194042.7722 | 2661925.0966 | 1194044.1947
14 | 2661926.7333 | 1194042.7722 | 2661928.2427 | 1194041.4604
15 | 2661925.0966 | 1194044.1947 | 2661910.8847 | 1194056.5464
16 | 2661930.3648 | 1194039.616 | 2661928.2427 | 1194041.4604
17 | 2661910.8847 | 1194056.5464 | 2661909.5248 | 1194057.7283
18 | 2661954.1748 | 1194015.7558 | 2661935.3302 | 1194035.3006 | 2661930.3648 | 1194039.616
19 | 2661904.2696 | 1194062.2956 | 2661909.5248 | 1194057.7283
20 | 2661965.5676 | 1194003.9398 | 2661954.1748 | 1194015.7558
21 | 2661988.8253 | 1194026.9051 | 2661965.5676 | 1194003.9398
22 | 2661965.5676 | 1194003.9398 | 2661968.5944 | 1194000.8693
23 | 2661938.3997 | 1194261.4081 | 2661928.3081 | 1194257.8905
24 | 2661938.3997 | 1194261.4081 | 2661947.5764 | 1194264.2158 | 2661952.7616 | 1194265.3924 | 2661956.2914 | 1194265.9959 | 2661960.0541 | 1194266.1794 | 2661963.3929 | 1194266.0917 | 2661981.4983 | 1194263.2887 | 2661990.1521 | 1194262.1443 | 2662005.6089 | 1194259.7475 | 2662014.7746 | 1194258.4751 | 2662021.4917 | 1194257.4329 | 2662034.0823 | 1194255.1176 | 2662034.1488 | 1194252.3723 | 2662034.961 | 1194249.7459 | 2662036.4634 | 1194247.4379 | 2662038.5323 | 1194245.6138 | 2662041.0213 | 1194244.4278 | 2662043.7392 | 1194243.9557
25 | 2661938.3997 | 1194261.4081 | 2661955.1918 | 1194202.9368 | 2661957.7715 | 1194187.1099 | 2661956.8771 | 1194165.9274
26 | 2662046.5176 | 1194178.1463 | 2662043.7392 | 1194243.9557
27 | 2661955.9907 | 1194144.9336 | 2661956.8771 | 1194165.9274
28 | 2662046.5176 | 1194178.1463 | 2662049.6379 | 1194149.9067 | 2662060.0094 | 1194108.0899 | 2662065.4194 | 1194089.0683
29 | 2662065.4194 | 1194089.0683 | 2662050.5671 | 1194086.0459 | 2662010.7057 | 1194047.8638
30 | 2661947.0531 | 1193981.2 | 2661952.1763 | 1193985.878
31 | 2661947.0531 | 1193981.2 | 2661926.8128 | 1193962.7186
32 | 2661968.5944 | 1194000.8693 | 2661952.1763 | 1193985.878
33 | 2661926.7038 | 1193962.6192 | 2661926.8128 | 1193962.7186
34 | 2661968.5944 | 1194000.8693 | 2661987.7612 | 1193980.4052
35 | 2661910.7863 | 1193948.0849 | 2661926.7038 | 1193962.6192
36 | 2661910.7863 | 1193948.0849 | 2661892.7968 | 1193968.3217
37 | 2661910.7863 | 1193948.0849 | 2661918.6667 | 1193943.6527 | 2661936.629 | 1193924.6705
38 | 2661988.8253 | 1194026.9051 | 2662005.8258 | 1194043.1894
39 | 2661988.8253 | 1194026.9051 | 2662004.9652 | 1194009.9923
40 | 2661936.629 | 1193924.6705 | 2661951.5762 | 1193908.8745
41 | 2662010.3264 | 1194047.5004 | 2662005.8258 | 1194043.1894
42 | 2662010.7057 | 1194047.8638 | 2662010.3264 | 1194047.5004

## bus_geodata
| x | y | coords
0 | 2661855.5253 | 1194104.6599
1 | 2661860.7923 | 1194100.0823
2 | 2661843.933 | 1194114.7349
3 | 2661868.976 | 1194092.9697
4 | 2661785.3116 | 1193990.1794
5 | 2661883.082 | 1194080.7101
6 | 2661825.5063 | 1193986.3811
7 | 2661801.2679 | 1194210.9389
8 | 2661890.91 | 1194244.0689
9 | 2661916.4821 | 1194216.5299
10 | 2661888.918 | 1194075.638
11 | 2661828.153 | 1194021.5622
12 | 2661913.6512 | 1194252.4736
13 | 2661926.7333 | 1194042.7722
14 | 2661925.0966 | 1194044.1947
15 | 2661928.2427 | 1194041.4604
16 | 2661910.8847 | 1194056.5464
17 | 2661930.3648 | 1194039.616
18 | 2661909.5248 | 1194057.7283
19 | 2661954.1748 | 1194015.7558
20 | 2661904.2696 | 1194062.2956
21 | 2661965.5676 | 1194003.9398
22 | 2661928.3081 | 1194257.8905
23 | 2661938.3997 | 1194261.4081
24 | 2662043.7392 | 1194243.9557
25 | 2661956.8771 | 1194165.9274
26 | 2662046.5176 | 1194178.1463
27 | 2661955.9907 | 1194144.9336
28 | 2662065.4195 | 1194089.0683
29 | 2661947.0531 | 1193981.2
30 | 2661952.1763 | 1193985.878
31 | 2661926.8128 | 1193962.7186
32 | 2661968.5944 | 1194000.8693
33 | 2661926.7038 | 1193962.6192
34 | 2661987.7612 | 1193980.4052
35 | 2661910.7863 | 1193948.0849
36 | 2661988.8253 | 1194026.9051
37 | 2661892.7968 | 1193968.3217
38 | 2661936.629 | 1193924.6705
39 | 2662005.8258 | 1194043.1894
40 | 2662004.9652 | 1194009.9923
41 | 2661951.5762 | 1193908.8745
42 | 2662010.3264 | 1194047.5004
43 | 2662010.7057 | 1194047.8638
44 | 2661965.5676 | 1194003.9398

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99153 | -0.16228 | 0.037876 | 0.0094927
1 | 0.99204 | -0.15245 | 0.012696 | 0.0031819
2 | 0.99094 | -0.17361 | 0 | 0
3 | 0.99296 | -0.13477 | 0.01155 | 0.0028946
4 | 0.98502 | -0.28816 | 0 | 0
5 | 0.99474 | -0.10056 | 0.0066356 | 0.001663
6 | 0.98348 | -0.31838 | 0.019901 | 0.0049876
7 | 0.97322 | -0.51588 | 0 | 0
8 | 0.97417 | -0.49711 | 0.0029935 | 0.00075025
9 | 0.97112 | -0.55733 | 0.032031 | 0.0080277
10 | 0.99552 | -0.085539 | 0.0088208 | 0.0022107
11 | 0.98277 | -0.33218 | 0.021696 | 0.0054375
12 | 0.97444 | -0.49191 | 0.020798 | 0.0052125
13 | 0.99973 | -0.005132 | 0.0073764 | 0.0018487
14 | 1 | 0 | -0.55899 | -0.14239
15 | 0.99948 | -0.0097814 | 0.0062565 | 0.001568
16 | 0.99877 | -0.02352 | 0.0062116 | 0.0015568
17 | 0.99914 | -0.01622 | 0.01429 | 0.0035814
18 | 0.99854 | -0.027833 | 0.012411 | 0.0031104
19 | 0.99521 | -0.09097 | 0.029365 | 0.0073596
20 | 0.99774 | -0.043002 | 0.0053525 | 0.0013415
21 | 0.99344 | -0.12472 | 0 | 0
22 | 0.97471 | -0.48657 | 0 | 0
23 | 0.97489 | -0.48294 | 0 | 0
24 | 0.97935 | -0.39577 | 0 | 0
25 | 0.97168 | -0.54623 | 0.022518 | 0.0056437
26 | 0.98193 | -0.34561 | 0.019114 | 0.0047905
27 | 0.97075 | -0.56473 | 0.047637 | 0.011939
28 | 0.98605 | -0.26612 | 0 | 0
29 | 0.99044 | -0.1827 | 0.017712 | 0.0044391
30 | 0.99095 | -0.17285 | 0.019687 | 0.0049341
31 | 0.98887 | -0.21302 | 0.0097066 | 0.0024327
32 | 0.99298 | -0.13364 | 0 | 0
33 | 0.98887 | -0.21316 | 0.0053185 | 0.001333
34 | 0.99253 | -0.14235 | 0.017577 | 0.0044052
35 | 0.98793 | -0.23129 | 0 | 0
36 | 0.99109 | -0.16956 | 0 | 0
37 | 0.98708 | -0.24787 | 0.034289 | 0.0085936
38 | 0.98752 | -0.23938 | 0.0050682 | 0.0012702
39 | 0.98963 | -0.19752 | 0.0062579 | 0.0015684
40 | 0.9904 | -0.18295 | 0.032265 | 0.0080863
41 | 0.98736 | -0.24241 | 0.0077925 | 0.001953
42 | 0.98926 | -0.2047 | 0.0062594 | 0.0015687
43 | 0.98922 | -0.20529 | 0.042842 | 0.010737
44 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.079799 | -0.020124 | 0.079837 | 0.020147 | 3.7557e-05 | 2.3947e-05 | 0.1198 | 0.1198 | 0.1198 | 0.99153 | -0.16228 | 0.99204 | -0.15245 | 32.9123
1 | 0.041923 | 0.010631 | -0.0419 | -0.010616 | 2.2829e-05 | 1.4413e-05 | 0.062959 | 0.062959 | 0.062959 | 0.99153 | -0.16228 | 0.99094 | -0.17361 | 17.2963
2 | -0.092533 | -0.023329 | 0.092611 | 0.023379 | 7.8382e-05 | 5.0024e-05 | 0.13884 | 0.13884 | 0.13884 | 0.99204 | -0.15245 | 0.99296 | -0.13477 | 38.1439
3 | 0.0419 | 0.010616 | -0.041671 | -0.010472 | 0.00022922 | 0.00014472 | 0.062959 | 0.062959 | 0.062959 | 0.99094 | -0.17361 | 0.98502 | -0.28816 | 17.2965
4 | -0.10416 | -0.026274 | 0.10433 | 0.026383 | 0.00017089 | 0.00010913 | 0.15615 | 0.15615 | 0.15615 | 0.99296 | -0.13477 | 0.99474 | -0.10056 | 42.8988
5 | 0.041671 | 0.010472 | -0.041611 | -0.010434 | 6.0014e-05 | 3.7896e-05 | 0.062959 | 0.06296 | 0.06296 | 0.98502 | -0.28816 | 0.98348 | -0.31838 | 17.2966
6 | -0.11097 | -0.028046 | 0.11105 | 0.028097 | 7.9974e-05 | 5.1083e-05 | 0.16608 | 0.16608 | 0.16608 | 0.99474 | -0.10056 | 0.99552 | -0.085539 | 45.6257
7 | 0.02171 | 0.0054462 | -0.021696 | -0.0054375 | 1.4277e-05 | 8.6897e-06 | 0.03285 | 0.03285 | 0.03285 | 0.98348 | -0.31838 | 0.98277 | -0.33218 | 9.0247
8 | -0.032094 | -0.0080648 | 0.032123 | 0.0080796 | 2.8774e-05 | 1.4849e-05 | 0.049079 | 0.049077 | 0.049079 | 0.97322 | -0.51588 | 0.97417 | -0.49711 | 4.4944
9 | 0.032094 | 0.0080648 | -0.032031 | -0.0080277 | 6.3382e-05 | 3.7084e-05 | 0.049079 | 0.04908 | 0.04908 | 0.97322 | -0.51588 | 0.97112 | -0.55733 | 6.7417
10 | -0.035117 | -0.0088299 | 0.035125 | 0.0088346 | 8.7229e-06 | 4.6768e-06 | 0.05365 | 0.05365 | 0.05365 | 0.97417 | -0.49711 | 0.97444 | -0.49191 | 4.913
11 | -0.11987 | -0.030308 | 0.12011 | 0.030465 | 0.0002451 | 0.0001566 | 0.17926 | 0.17926 | 0.17926 | 0.99552 | -0.085539 | 0.99774 | -0.043002 | 49.2478
12 | -0.055923 | -0.014047 | 0.055938 | 0.014056 | 1.4248e-05 | 8.5348e-06 | 0.085409 | 0.085409 | 0.085409 | 0.97444 | -0.49191 | 0.97471 | -0.48657 | 7.8214
13 | -0.41287 | -0.10567 | 0.41297 | 0.10573 | 0.00010262 | 6.5593e-05 | 0.6153 | 0.6153 | 0.6153 | 0.99973 | -0.005132 | 1 | 0 | 56.3463
14 | 0.40549 | 0.10382 | -0.4054 | -0.10376 | 9.1292e-05 | 5.8348e-05 | 0.60432 | 0.60432 | 0.60432 | 0.99973 | -0.005132 | 0.99948 | -0.0097814 | 55.3409
15 | 0.14437 | 0.036654 | -0.14421 | -0.03655 | 0.00016319 | 0.00010395 | 0.21499 | 0.21499 | 0.21499 | 1 | 0 | 0.99877 | -0.02352 | 29.532
16 | 0.39915 | 0.10219 | -0.39902 | -0.10211 | 0.00012443 | 7.9522e-05 | 0.59501 | 0.59501 | 0.59501 | 0.99948 | -0.0097814 | 0.99914 | -0.01622 | 54.4879
17 | 0.138 | 0.034993 | -0.13797 | -0.034975 | 2.86e-05 | 1.8281e-05 | 0.20574 | 0.20574 | 0.20574 | 0.99877 | -0.02352 | 0.99854 | -0.027833 | 56.5216
18 | 0.38473 | 0.098532 | -0.38334 | -0.097645 | 0.0013878 | 0.00088685 | 0.57373 | 0.57373 | 0.57373 | 0.99914 | -0.01622 | 0.99521 | -0.09097 | 52.5391
19 | 0.12556 | 0.031864 | -0.12547 | -0.031806 | 9.1541e-05 | 5.8495e-05 | 0.18724 | 0.18724 | 0.18724 | 0.99854 | -0.027833 | 0.99774 | -0.043002 | 51.4408
20 | 0.35398 | 0.090285 | -0.3534 | -0.089917 | 0.00057594 | 0.00036796 | 0.52982 | 0.52982 | 0.52982 | 0.99521 | -0.09097 | 0.99344 | -0.12472 | 48.5184
21 | 0.2358 | 0.060273 | -0.23529 | -0.059948 | 0.00051018 | 0.00032525 | 0.35362 | 0.35362 | 0.35362 | 0.99344 | -0.12472 | 0.99109 | -0.16956 | 32.3826
22 | 0.1176 | 0.029644 | -0.11755 | -0.029612 | 5.0135e-05 | 3.2031e-05 | 0.1762 | 0.1762 | 0.1762 | 0.99344 | -0.12472 | 0.99298 | -0.13364 | 48.4078
23 | -0.055938 | -0.014056 | 0.055947 | 0.014061 | 9.7193e-06 | 5.8217e-06 | 0.085409 | 0.085409 | 0.085409 | 0.97471 | -0.48657 | 0.97489 | -0.48294 | 7.8213
24 | -0.12636 | -0.031804 | 0.12689 | 0.032138 | 0.00052878 | 0.00033415 | 0.19291 | 0.19291 | 0.19291 | 0.97489 | -0.48294 | 0.97935 | -0.39577 | 17.666
25 | 0.07041 | 0.017743 | -0.070198 | -0.017609 | 0.00021252 | 0.00013358 | 0.1075 | 0.10751 | 0.10751 | 0.97489 | -0.48294 | 0.97168 | -0.54623 | 14.7672
26 | -0.12689 | -0.032138 | 0.12719 | 0.032332 | 0.00030648 | 0.00019365 | 0.19291 | 0.19291 | 0.19291 | 0.97935 | -0.39577 | 0.98193 | -0.34561 | 17.6659
27 | 0.047679 | 0.011966 | -0.047637 | -0.011939 | 4.2015e-05 | 2.6629e-05 | 0.073021 | 0.073021 | 0.073021 | 0.97168 | -0.54623 | 0.97075 | -0.56473 | 20.0607
28 | -0.14631 | -0.037123 | 0.14687 | 0.037479 | 0.0005617 | 0.00035601 | 0.22188 | 0.22188 | 0.22188 | 0.98193 | -0.34561 | 0.98605 | -0.26612 | 20.3184
29 | -0.14687 | -0.037479 | 0.1473 | 0.037753 | 0.00043293 | 0.00027437 | 0.22188 | 0.22187 | 0.22188 | 0.98605 | -0.26612 | 0.98922 | -0.20529 | 20.3183
30 | -0.080052 | -0.020125 | 0.080089 | 0.020149 | 3.7645e-05 | 2.4003e-05 | 0.12029 | 0.12029 | 0.12029 | 0.99044 | -0.1827 | 0.99095 | -0.17285 | 33.0468
31 | 0.062339 | 0.015686 | -0.062249 | -0.015629 | 9.0201e-05 | 5.7377e-05 | 0.09368 | 0.09368 | 0.09368 | 0.99044 | -0.1827 | 0.98887 | -0.21302 | 25.7363
32 | -0.099777 | -0.025083 | 0.099964 | 0.025203 | 0.00018722 | 0.00011953 | 0.14985 | 0.14985 | 0.14985 | 0.99095 | -0.17285 | 0.99298 | -0.13364 | 41.1684
33 | 0.052543 | 0.013196 | -0.052542 | -0.013196 | 3.459e-07 | 2.1948e-07 | 0.079074 | 0.079074 | 0.079074 | 0.98887 | -0.21302 | 0.98887 | -0.21316 | 21.7236
34 | 0.017584 | 0.0044095 | -0.017577 | -0.0044052 | 7.3013e-06 | 4.3103e-06 | 0.026352 | 0.026352 | 0.026352 | 0.99298 | -0.13364 | 0.99253 | -0.14235 | 7.2395
35 | 0.047224 | 0.011863 | -0.047183 | -0.011837 | 4.0828e-05 | 2.5854e-05 | 0.071071 | 0.071071 | 0.071071 | 0.98887 | -0.21316 | 0.98793 | -0.23129 | 19.525
36 | 0.034316 | 0.0086106 | -0.034289 | -0.0085936 | 2.7099e-05 | 1.6997e-05 | 0.05169 | 0.051691 | 0.051691 | 0.98793 | -0.23129 | 0.98708 | -0.24787 | 14.2007
37 | 0.012867 | 0.0032264 | -0.012862 | -0.0032237 | 4.9545e-06 | 2.7207e-06 | 0.019381 | 0.019381 | 0.019381 | 0.98793 | -0.23129 | 0.98752 | -0.23938 | 5.3244
38 | 0.20301 | 0.051849 | -0.20273 | -0.051674 | 0.000274 | 0.00017445 | 0.30514 | 0.30514 | 0.30514 | 0.99109 | -0.16956 | 0.98963 | -0.19752 | 27.9435
39 | 0.032285 | 0.0080992 | -0.032265 | -0.0080863 | 2.0601e-05 | 1.2884e-05 | 0.048476 | 0.048476 | 0.048476 | 0.99109 | -0.16956 | 0.9904 | -0.18295 | 13.3175
40 | 0.0077937 | 0.0019534 | -0.0077925 | -0.001953 | 1.1247e-06 | 4.4164e-07 | 0.011744 | 0.011744 | 0.011744 | 0.98752 | -0.23938 | 0.98736 | -0.24241 | 3.2263
41 | 0.19648 | 0.050106 | -0.19641 | -0.050062 | 6.8133e-05 | 4.3365e-05 | 0.29573 | 0.29573 | 0.29573 | 0.98963 | -0.19752 | 0.98926 | -0.2047 | 27.0818
42 | 0.19015 | 0.048494 | -0.19014 | -0.04849 | 5.3827e-06 | 3.4247e-06 | 0.28632 | 0.28632 | 0.28632 | 0.98926 | -0.2047 | 0.98922 | -0.20529 | 26.2196

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56525 | 0.14396

## res_load
| p_mw | q_mvar
0 | 0.037876 | 0.0094927
1 | 0.012696 | 0.0031819
2 | 0.01155 | 0.0028946
3 | 0.0066356 | 0.001663
4 | 0.019901 | 0.0049876
5 | 0.0029935 | 0.00075025
6 | 0.032031 | 0.0080277
7 | 0.0088208 | 0.0022107
8 | 0.021696 | 0.0054375
9 | 0.020798 | 0.0052125
10 | 0.0073764 | 0.0018487
11 | 0.0062565 | 0.001568
12 | 0.0062565 | 0.001568
13 | 0.0062116 | 0.0015568
14 | 0.01429 | 0.0035814
15 | 0.012411 | 0.0031104
16 | 0.029365 | 0.0073596
17 | 0.0053525 | 0.0013415
18 | 0.022518 | 0.0056437
19 | 0.019114 | 0.0047905
20 | 0.047637 | 0.011939
21 | 0.017712 | 0.0044391
22 | 0.019687 | 0.0049341
23 | 0.0097066 | 0.0024327
24 | 0.0053185 | 0.001333
25 | 0.017577 | 0.0044052
26 | 0.034289 | 0.0085936
27 | 0.0050682 | 0.0012702
28 | 0.0062579 | 0.0015684
29 | 0.032265 | 0.0080863
30 | 0.0077925 | 0.001953
31 | 0.0062594 | 0.0015687
32 | 0.042842 | 0.010737

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1