## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1407-36_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1407-36_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1407-36_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1407-36_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1407-36_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1407-36_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1407-36_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1407-36_0_4_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_1407-36_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1407-36_0_4_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_1407-36_0_4_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_1407-36_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1407-36_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1407-36_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1407-36_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1407-36_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1407-36_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1407-36_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1407-36_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1407-36_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1407-36_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1407-36_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1407-36_0_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1407-36_0_4_node_73 | 0.4 | n |  | TRUE
24 | bus_LV_1407-36_0_4_node_74 | 0.4 | n |  | TRUE
25 | bus_LV_1407-36_0_4_node_75 | 0.4 | n |  | TRUE
26 | bus_LV_1407-36_0_4_node_76 | 0.4 | n |  | TRUE
27 | bus_LV_1407-36_0_4_node_77 | 0.4 | n |  | TRUE
28 | bus_LV_1407-36_0_4_node_78 | 0.4 | n |  | TRUE
29 | bus_LV_1407-36_0_4_node_121 | 0.4 | n |  | TRUE
30 | bus_LV_1407-36_0_4_node_88 | 0.4 | n |  | TRUE
31 | bus_LV_1407-36_0_4_node_85 | 0.4 | n |  | TRUE
32 | bus_LV_1407-36_0_4_node_87 | 0.4 | n |  | TRUE
33 | bus_LV_1407-36_0_4_node_89 | 0.4 | n |  | TRUE
34 | bus_LV_1407-36_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1407-36_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_1407-36_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_1407-36_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_1407-36_0_4_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_1407-36_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_1407-36_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_1407-36_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1407-36_0_4_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_1407-36_0_4_node_32 | 0.4 | n |  | TRUE
44 | bus_LV_1407-36_0_4_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1407-36_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_1407-36_0_4_node_124 | 0.4 | n |  | TRUE
47 | bus_LV_1407-36_0_4_node_84 | 0.4 | n |  | TRUE
48 | bus_LV_1407-36_0_4_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_1407-36_0_4_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1407-36_0_4_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_1407-36_0_4_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_1407-36_0_4_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_1407-36_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_1407-36_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_1407-36_0_4_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_1407-36_0_4_node_41 | 0.4 | n |  | TRUE
57 | bus_LV_1407-36_0_4_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_1407-36_0_4_node_44 | 0.4 | n |  | TRUE
59 | bus_LV_1407-36_0_4_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_1407-36_0_4_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_1407-36_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_1407-36_0_4_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_1407-36_0_4_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_1407-36_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_1407-36_0_4_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_1407-36_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_1407-36_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_1407-36_0_4_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_1407-36_0_4_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_1407-36_0_4_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_1407-36_0_4_node_90 | 0.4 | n |  | TRUE
72 | bus_LV_1407-36_0_4_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_1407-36_0_4_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_1407-36_0_4_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_1407-36_0_4_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_1407-36_0_4_node_60 | 0.4 | n |  | TRUE
77 | bus_LV_1407-36_0_4_node_62 | 0.4 | n |  | TRUE
78 | bus_LV_1407-36_0_4_node_64 | 0.4 | n |  | TRUE
79 | bus_LV_1407-36_0_4_node_118 | 0.4 | n |  | TRUE
80 | bus_LV_1407-36_0_4_node_99 | 0.4 | n |  | TRUE
81 | bus_LV_1407-36_0_4_node_94 | 0.4 | n |  | TRUE
82 | bus_LV_1407-36_0_4_node_100 | 0.4 | n |  | TRUE
83 | bus_LV_1407-36_0_4_node_98 | 0.4 | n |  | TRUE
84 | bus_LV_1407-36_0_4_node_65 | 0.4 | n |  | TRUE
85 | bus_LV_1407-36_0_4_node_66 | 0.4 | n |  | TRUE
86 | bus_LV_1407-36_0_4_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_1407-36_0_4_node_67 | 0.4 | n |  | TRUE
88 | bus_LV_1407-36_0_4_node_86 | 0.4 | n |  | TRUE
89 | bus_LV_1407-36_0_4_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_1407-36_0_4_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_1407-36_0_4_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_1407-36_0_4_node_83 | 0.4 | n |  | TRUE
93 | bus_LV_1407-36_0_4_node_123 | 0.4 | n |  | TRUE
94 | bus_LV_1407-36_0_4_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_1407-36_0_4_node_70 | 0.4 | n |  | TRUE
96 | bus_LV_1407-36_0_4_node_119 | 0.4 | n |  | TRUE
97 | bus_LV_1407-36_0_4_node_71 | 0.4 | n |  | TRUE
98 | bus_LV_1407-36_0_4_node_72 | 0.4 | n |  | TRUE
99 | bus_LV_1407-36_0_4_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_1407-36_0_4_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_1407-36_0_4_node_125 | 0.4 | n |  | TRUE
102 | bus_LV_1407-36_0_4_node_126 | 0.4 | n |  | TRUE
103 | bus_LV_1407-36_0_4_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_1407-36_0_4_node_91 | 0.4 | n |  | TRUE
105 | bus_LV_1407-36_0_4_node_93 | 0.4 | n |  | TRUE
106 | bus_LV_1407-36_0_4_node_95 | 0.4 | n |  | TRUE
107 | bus_LV_1407-36_0_4_node_96 | 0.4 | n |  | TRUE
108 | bus_LV_1407-36_0_4_node_97 | 0.4 | n |  | TRUE
109 | bus_LV_1407-36_0_4_node_109 | 0.4 | n |  | TRUE
110 | bus_LV_1407-36_0_4_node_110 | 0.4 | n |  | TRUE
111 | bus_LV_1407-36_0_4_node_101 | 0.4 | n |  | TRUE
112 | bus_LV_1407-36_0_4_node_102 | 0.4 | n |  | TRUE
113 | bus_LV_1407-36_0_4_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_1407-36_0_4_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_1407-36_0_4_node_105 | 0.4 | n |  | TRUE
116 | bus_LV_1407-36_0_4_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_1407-36_0_4_node_107 | 0.4 | n |  | TRUE
118 | bus_LV_1407-36_0_4_node_108 | 0.4 | n |  | TRUE
119 | bus_LV_1407-36_0_4_node_114 | 0.4 | n |  | TRUE
120 | bus_LV_1407-36_0_4_node_112 | 0.4 | n |  | TRUE
121 | bus_LV_1407-36_0_4_node_111 | 0.4 | n |  | TRUE
122 | bus_LV_1407-36_0_4_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_1407-36_0_4_node_115 | 0.4 | n |  | TRUE
124 | bus_LV_1407-36_0_4_node_116 | 0.4 | n |  | TRUE
125 | bus_MV_141_0_node_70 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1407-36_0_4_load_0 | 0 | 0.0014741 | 0.00036945 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1407-36_0_4_load_1 | 1 | 0.001706 | 0.00042756 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1407-36_0_4_load_2 | 2 | 0.0015435 | 0.00038683 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1407-36_0_4_load_4 | 4 | 0.0019693 | 0.00049356 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1407-36_0_4_load_5 | 5 | 0.00081113 | 0.00020329 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1407-36_0_4_load_6 | 6 | 0.00033477 | 8.39e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1407-36_0_4_load_18 | 7 | 0.00095331 | 0.00023892 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1407-36_0_4_load_19 | 8 | 0.00066507 | 0.00016668 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1407-36_0_4_load_22 | 9 | 0.0075655 | 0.0018961 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1407-36_0_4_load_20 | 10 | 0.00088667 | 0.00022222 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1407-36_0_4_load_10 | 11 | 0.00069842 | 0.00017504 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1407-36_0_4_load_8 | 12 | 0.00072284 | 0.00018116 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1407-36_0_4_load_9 | 13 | 0.00068613 | 0.00017196 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1407-36_0_4_load_7 | 14 | 0.0012 | 0.00030074 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1407-36_0_4_load_12 | 16 | 0.011071 | 0.0027746 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1407-36_0_4_load_13 | 17 | 0.00033843 | 8.4819e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1407-36_0_4_load_14 | 18 | 0.0011883 | 0.00029782 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1407-36_0_4_load_16 | 20 | 0.00068074 | 0.00017061 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1407-36_0_4_load_17 | 21 | 0.0034781 | 0.00087169 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1407-36_0_4_load_73 | 23 | 0.0016506 | 0.00041369 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1407-36_0_4_load_74 | 24 | 0.00020895 | 5.2368e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1407-36_0_4_load_75 | 25 | 0.00075844 | 0.00019008 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1407-36_0_4_load_78 | 28 | 0.00023181 | 5.8096e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1407-36_0_4_load_121 | 29 | 0.00074265 | 0.00018613 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1407-36_0_4_load_87 | 32 | 0.00034117 | 8.5506e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1407-36_0_4_load_89 | 33 | 0.00020081 | 5.0329e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1407-36_0_4_load_21 | 34 | 0.0013596 | 0.00034075 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1407-36_0_4_load_25 | 36 | 0.0013223 | 0.0003314 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1407-36_0_4_load_28 | 39 | 0.0028077 | 0.00070366 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1407-36_0_4_load_29 | 40 | 0.0010674 | 0.00026751 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1407-36_0_4_load_33 | 41 | 0.001203 | 0.0003015 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1407-36_0_4_load_32 | 43 | 0.0022797 | 0.00057134 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1407-36_0_4_load_30 | 44 | 0.0012897 | 0.00032322 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1407-36_0_4_load_34 | 45 | 0.00212 | 0.00053132 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1407-36_0_4_load_124 | 46 | 0.0028464 | 0.00071336 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1407-36_0_4_load_84 | 47 | 0.0005713 | 0.00014318 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1407-36_0_4_load_35 | 48 | 0.0062812 | 0.0015742 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1407-36_0_4_load_36 | 49 | 0.0094379 | 0.0023654 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1407-36_0_4_load_37 | 50 | 0.00099509 | 0.00024939 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1407-36_0_4_load_38 | 51 | 0.0022416 | 0.00056179 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1407-36_0_4_load_39 | 52 | 0.0098488 | 0.0024684 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1407-36_0_4_load_40 | 53 | 0.0068412 | 0.0017146 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1407-36_0_4_load_41 | 56 | 0.0087597 | 0.0021954 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1407-36_0_4_load_46 | 57 | 0.0059458 | 0.0014901 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1407-36_0_4_load_44 | 58 | 0.016222 | 0.0040655 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1407-36_0_4_load_51 | 59 | 0.0043039 | 0.0010787 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1407-36_0_4_load_45 | 60 | 0.0041735 | 0.001046 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1407-36_0_4_load_49 | 61 | 0.0088446 | 0.0022167 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1407-36_0_4_load_47 | 62 | 0.0071301 | 0.001787 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1407-36_0_4_load_48 | 63 | 0.0060663 | 0.0015203 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1407-36_0_4_load_50 | 64 | 0.004434 | 0.0011113 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1407-36_0_4_load_52 | 65 | 0.0053769 | 0.0013476 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1407-36_0_4_load_53 | 66 | 0.0039998 | 0.0010024 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1407-36_0_4_load_54 | 67 | 0.0020904 | 0.00052391 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1407-36_0_4_load_55 | 68 | 0.002348 | 0.00058845 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1407-36_0_4_load_56 | 69 | 0.0039623 | 0.00099304 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1407-36_0_4_load_90 | 71 | 0.0042833 | 0.0010735 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1407-36_0_4_load_57 | 73 | 0.022263 | 0.0055796 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1407-36_0_4_load_58 | 74 | 0.0026848 | 0.00067287 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1407-36_0_4_load_59 | 75 | 0.0086516 | 0.0021683 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1407-36_0_4_load_60 | 76 | 0.020839 | 0.0052228 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1407-36_0_4_load_62 | 77 | 0.019167 | 0.0048037 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1407-36_0_4_load_64 | 78 | 0.0043662 | 0.0010943 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1407-36_0_4_load_118 | 79 | 0.0077958 | 0.0019538 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1407-36_0_4_load_94 | 81 | 0.0024408 | 0.00061173 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1407-36_0_4_load_100 | 82 | 0.014398 | 0.0036085 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1407-36_0_4_load_98 | 83 | 0.0072388 | 0.0018142 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1407-36_0_4_load_65 | 84 | 0.00016741 | 4.1957e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1407-36_0_4_load_66 | 85 | 0.00014261 | 3.5742e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1407-36_0_4_load_120 | 86 | 0.00052961 | 0.00013273 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1407-36_0_4_load_67 | 87 | 0.00023646 | 5.9262e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1407-36_0_4_load_68 | 89 | 0.00036479 | 9.1425e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1407-36_0_4_load_69 | 91 | 0.00022691 | 5.6869e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1407-36_0_4_load_123 | 93 | 0.0012152 | 0.00030455 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1407-36_0_4_load_79 | 94 | 0.00032446 | 8.1317e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1407-36_0_4_load_70 | 95 | 0.00037336 | 9.3574e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1407-36_0_4_load_119 | 96 | 0.00038856 | 9.7383e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1407-36_0_4_load_72 | 98 | 0.00017102 | 4.2862e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1407-36_0_4_load_82 | 100 | 0.00035037 | 8.7812e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1407-36_0_4_load_125 | 101 | 0.00035387 | 8.8687e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1407-36_0_4_load_126 | 102 | 0.00066089 | 0.00016563 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1407-36_0_4_load_92 | 103 | 0.0085911 | 0.0021531 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1407-36_0_4_load_91 | 104 | 0.0023952 | 0.0006003 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1407-36_0_4_load_95 | 106 | 0.0065849 | 0.0016503 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1407-36_0_4_load_96 | 107 | 0.0033741 | 0.00084564 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1407-36_0_4_load_97 | 108 | 0.0037372 | 0.00093664 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1407-36_0_4_load_109 | 109 | 0.0011223 | 0.00028129 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1407-36_0_4_load_110 | 110 | 0.0032647 | 0.00081822 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1407-36_0_4_load_101 | 111 | 0.0077608 | 0.001945 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1407-36_0_4_load_102 | 112 | 0.0076401 | 0.0019148 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1407-36_0_4_load_103 | 113 | 0.0081673 | 0.0020469 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1407-36_0_4_load_104 | 114 | 0.0048385 | 0.0012127 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1407-36_0_4_load_105 | 115 | 0.0027526 | 0.00068987 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1407-36_0_4_load_107 | 117 | 0.0012203 | 0.00030584 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1407-36_0_4_load_108 | 118 | 0.0007503 | 0.00018804 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1407-36_0_4_load_114 | 119 | 0.0019432 | 0.00048701 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1407-36_0_4_load_112 | 120 | 0.0055564 | 0.0013926 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1407-36_0_4_load_111 | 121 | 0.0071067 | 0.0017811 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1407-36_0_4_load_113 | 122 | 0.0012083 | 0.00030283 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1407-36_0_4_load_115 | 123 | 0.0031095 | 0.00077931 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1407-36_0_4_load_116 | 124 | 0.0026698 | 0.00066911 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 61 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1407-36_0_4_line_0 |  | 0 | 1 | 0.025251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1407-36_0_4_line_1 |  | 0 | 2 | 0.016293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1407-36_0_4_line_2 |  | 1 | 3 | 0.1371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1407-36_0_4_line_3 |  | 2 | 4 | 0.082266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1407-36_0_4_line_4 |  | 3 | 7 | 0.16663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1407-36_0_4_line_5 |  | 4 | 5 | 0.10573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1407-36_0_4_line_6 |  | 4 | 6 | 0.02341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1407-36_0_4_line_7 |  | 5 | 14 | 0.01162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1407-36_0_4_line_8 |  | 6 | 12 | 0.0023944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1407-36_0_4_line_9 |  | 7 | 8 | 0.0051502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1407-36_0_4_line_10 |  | 7 | 9 | 0.21773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1407-36_0_4_line_11 |  | 8 | 10 | 0.0012521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1407-36_0_4_line_12 |  | 9 | 22 | 0.015765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1407-36_0_4_line_13 |  | 11 | 12 | 0.074849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1407-36_0_4_line_14 |  | 11 | 13 | 0.015376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1407-36_0_4_line_15 |  | 13 | 15 | 0.011889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1407-36_0_4_line_16 |  | 15 | 16 | 0.018216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1407-36_0_4_line_17 |  | 15 | 17 | 0.060837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1407-36_0_4_line_18 |  | 17 | 18 | 0.018639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1407-36_0_4_line_19 |  | 18 | 19 | 0.13818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1407-36_0_4_line_20 |  | 19 | 20 | 0.035169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1407-36_0_4_line_21 |  | 20 | 21 | 0.013016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1407-36_0_4_line_22 |  | 22 | 35 | 0.05253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1407-36_0_4_line_23 |  | 23 | 24 | 0.013195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1407-36_0_4_line_24 |  | 23 | 25 | 0.019995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1407-36_0_4_line_25 |  | 24 | 26 | 0.08659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1407-36_0_4_line_26 |  | 26 | 27 | 0.067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1407-36_0_4_line_27 |  | 26 | 28 | 0.021641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1407-36_0_4_line_28 |  | 27 | 29 | 0.052597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1407-36_0_4_line_29 |  | 27 | 30 | 0.095052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1407-36_0_4_line_30 |  | 28 | 31 | 0.072698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1407-36_0_4_line_31 |  | 30 | 32 | 0.043476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1407-36_0_4_line_32 |  | 31 | 88 | 0.040471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1407-36_0_4_line_33 |  | 32 | 33 | 0.0053953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1407-36_0_4_line_34 |  | 34 | 35 | 0.053098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1407-36_0_4_line_35 |  | 35 | 36 | 0.020038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1407-36_0_4_line_36 |  | 36 | 37 | 0.019795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1407-36_0_4_line_37 |  | 37 | 38 | 0.016621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1407-36_0_4_line_38 |  | 37 | 39 | 0.037431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1407-36_0_4_line_39 |  | 38 | 40 | 0.032591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1407-36_0_4_line_40 |  | 39 | 41 | 0.025822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1407-36_0_4_line_41 |  | 40 | 44 | 0.0064028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1407-36_0_4_line_42 |  | 41 | 45 | 0.030716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_1407-36_0_4_line_43 |  | 42 | 43 | 0.019067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1407-36_0_4_line_44 |  | 42 | 44 | 0.0092118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1407-36_0_4_line_45 |  | 43 | 46 | 0.22514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1407-36_0_4_line_46 |  | 45 | 48 | 0.023404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_1407-36_0_4_line_47 |  | 46 | 47 | 0.35869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1407-36_0_4_line_48 |  | 47 | 100 | 0.031156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1407-36_0_4_line_49 |  | 48 | 49 | 0.0021462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_1407-36_0_4_line_50 |  | 49 | 50 | 0.0019956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_1407-36_0_4_line_51 |  | 50 | 51 | 0.0056263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_1407-36_0_4_line_52 |  | 51 | 52 | 0.025544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_1407-36_0_4_line_53 |  | 52 | 53 | 0.0010675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1407-36_0_4_line_54 |  | 53 | 54 | 0.0043186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_1407-36_0_4_line_55 |  | 54 | 55 | 0.036401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_1407-36_0_4_line_56 |  | 54 | 56 | 0.024173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1407-36_0_4_line_57 |  | 55 | 57 | 0.025293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_1407-36_0_4_line_58 |  | 55 | 58 | 0.039463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1407-36_0_4_line_59 |  | 57 | 59 | 0.0072536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_1407-36_0_4_line_60 |  | 58 | 60 | 0.014471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1407-36_0_4_line_61 |  | 59 | 61 | 0.00041692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_1407-36_0_4_line_62 |  | 61 | 62 | 0.0081633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_1407-36_0_4_line_63 |  | 62 | 63 | 0.0061438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_1407-36_0_4_line_64 |  | 63 | 64 | 0.019068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_1407-36_0_4_line_65 |  | 64 | 65 | 0.0054811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_1407-36_0_4_line_66 |  | 65 | 66 | 0.00021287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_1407-36_0_4_line_67 |  | 66 | 67 | 0.020229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_1407-36_0_4_line_68 |  | 67 | 68 | 0.0096792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_1407-36_0_4_line_69 |  | 68 | 69 | 0.013818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_1407-36_0_4_line_70 |  | 69 | 70 | 0.015198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_1407-36_0_4_line_71 |  | 70 | 71 | 0.019798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1407-36_0_4_line_72 |  | 70 | 72 | 0.008317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1407-36_0_4_line_73 |  | 71 | 81 | 0.022379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1407-36_0_4_line_74 |  | 72 | 78 | 0.019412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1407-36_0_4_line_75 |  | 72 | 75 | 0.044688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1407-36_0_4_line_76 |  | 73 | 74 | 0.040802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1407-36_0_4_line_77 |  | 73 | 75 | 0.012527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1407-36_0_4_line_78 |  | 74 | 76 | 0.012375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1407-36_0_4_line_79 |  | 76 | 77 | 0.0080875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1407-36_0_4_line_80 |  | 77 | 79 | 0.012467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1407-36_0_4_line_81 |  | 78 | 80 | 0.052561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1407-36_0_4_line_82 |  | 80 | 82 | 0.026366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1407-36_0_4_line_83 |  | 80 | 83 | 0.025471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1407-36_0_4_line_84 |  | 81 | 103 | 0.0020479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1407-36_0_4_line_85 |  | 82 | 111 | 0.028517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1407-36_0_4_line_86 |  | 84 | 85 | 0.051182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1407-36_0_4_line_87 |  | 84 | 86 | 0.081479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1407-36_0_4_line_88 |  | 85 | 87 | 0.011249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1407-36_0_4_line_89 |  | 86 | 88 | 0.07537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1407-36_0_4_line_90 |  | 87 | 89 | 0.022256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1407-36_0_4_line_91 |  | 87 | 90 | 0.13906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1407-36_0_4_line_92 |  | 88 | 96 | 0.0365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1407-36_0_4_line_93 |  | 89 | 91 | 0.020826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1407-36_0_4_line_94 |  | 90 | 92 | 0.10258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1407-36_0_4_line_95 |  | 90 | 93 | 0.10925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1407-36_0_4_line_96 |  | 90 | 94 | 0.11911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1407-36_0_4_line_97 |  | 91 | 95 | 0.048456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1407-36_0_4_line_98 |  | 92 | 101 | 0.063065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1407-36_0_4_line_99 |  | 92 | 102 | 0.025521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1407-36_0_4_line_100 |  | 94 | 99 | 0.083376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1407-36_0_4_line_101 |  | 95 | 97 | 0.093375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1407-36_0_4_line_102 |  | 97 | 98 | 0.11931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1407-36_0_4_line_103 |  | 99 | 100 | 0.13047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1407-36_0_4_line_104 |  | 103 | 104 | 0.024911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1407-36_0_4_line_105 |  | 104 | 105 | 0.011729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1407-36_0_4_line_106 |  | 105 | 106 | 0.016894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1407-36_0_4_line_107 |  | 105 | 107 | 0.017882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1407-36_0_4_line_108 |  | 106 | 108 | 0.010602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1407-36_0_4_line_109 |  | 107 | 109 | 0.014566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1407-36_0_4_line_110 |  | 109 | 110 | 9.2175e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1407-36_0_4_line_111 |  | 110 | 118 | 0.026127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1407-36_0_4_line_112 |  | 111 | 112 | 0.014625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1407-36_0_4_line_113 |  | 112 | 113 | 0.034195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1407-36_0_4_line_114 |  | 114 | 115 | 0.048066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1407-36_0_4_line_115 |  | 114 | 116 | 0.029025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1407-36_0_4_line_116 |  | 116 | 117 | 0.00014424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1407-36_0_4_line_117 |  | 116 | 118 | 0.0039162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1407-36_0_4_line_118 |  | 117 | 119 | 0.0076091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1407-36_0_4_line_119 |  | 119 | 120 | 0.022512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1407-36_0_4_line_120 |  | 120 | 121 | 0.012756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1407-36_0_4_line_121 |  | 121 | 122 | 0.011769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1407-36_0_4_line_122 |  | 122 | 123 | 0.017643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1407-36_0_4_line_123 |  | 123 | 124 | 0.011416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1407-36_0_4_trafo_49 | 0.63 MVA 20/0.4 kV | 125 | 61 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2661709.416 | 1195905.7928 | 2661717.2636 | 1195908.4705 | 2661722.3331 | 1195912.5918 | 2661725.3535 | 1195922.5707
1 | 2661693.5189 | 1195902.3109 | 2661707.0828 | 1195904.9968 | 2661709.416 | 1195905.7928
2 | 2661838.9333 | 1195992.4312 | 2661830.6816 | 1195990.3003 | 2661738.4218 | 1195941.5525 | 2661728.9122 | 1195934.3279 | 2661725.3535 | 1195922.5707
3 | 2661667.4504 | 1195824.2843 | 2661693.5189 | 1195902.3109
4 | 2661838.9333 | 1195992.4312 | 2661731.6081 | 1196119.9005
5 | 2661667.4504 | 1195824.2843 | 2661647.6161 | 1195851.3747 | 2661645.3919 | 1195853.542 | 2661640.8854 | 1195854.6628 | 2661635.5703 | 1195854.3968 | 2661613.5598 | 1195846.2654 | 2661596.1826 | 1195840.9834 | 2661588.5182 | 1195839.5036 | 2661588.4778 | 1195843.4277 | 2661591.1073 | 1195848.5175
6 | 2661667.4504 | 1195824.2843 | 2661667.5222 | 1195824.1862 | 2661676.9677 | 1195816.9683 | 2661686.7364 | 1195811.0905
7 | 2661596.4406 | 1195858.8409 | 2661591.1073 | 1195848.5175
8 | 2661688.788 | 1195809.8561 | 2661686.7364 | 1195811.0905
9 | 2661731.6081 | 1196119.9005 | 2661727.4442 | 1196122.9314
10 | 2661914.5183 | 1196238.0118 | 2661731.6081 | 1196119.9005
11 | 2661726.4319 | 1196123.6683 | 2661727.4442 | 1196122.9314
12 | 2661909.42 | 1196252.1562 | 2661913.4011 | 1196247.3168 | 2661914.8389 | 1196241.6283 | 2661914.5183 | 1196238.0118
13 | 2661688.788 | 1195809.8561 | 2661694.0253 | 1195806.7048 | 2661716.9168 | 1195800.3372 | 2661723.1717 | 1195800.3462 | 2661745.4889 | 1195802.3887 | 2661756.5367 | 1195800.8574 | 2661761.3631 | 1195799.0398
14 | 2661775.7525 | 1195793.6207 | 2661761.3631 | 1195799.0398
15 | 2661786.8784 | 1195789.4307 | 2661775.7525 | 1195793.6207
16 | 2661786.8784 | 1195789.4307 | 2661777.2635 | 1195773.9446
17 | 2661786.8784 | 1195789.4307 | 2661844.0976 | 1195768.7635
18 | 2661860.6003 | 1195760.2015 | 2661848.0725 | 1195767.3278 | 2661844.0976 | 1195768.7635
19 | 2661974.4726 | 1195683.1311 | 2661971.1018 | 1195688.5882 | 2661962.3875 | 1195695.7799 | 2661868.8034 | 1195755.5353 | 2661860.6003 | 1195760.2015
20 | 2661974.4726 | 1195683.1311 | 2661972.7239 | 1195718.2564
21 | 2661972.0767 | 1195731.2565 | 2661972.7239 | 1195718.2564
22 | 2661956.0012 | 1196267.9921 | 2661937.2547 | 1196267.8201 | 2661932.0083 | 1196266.0981 | 2661926.0764 | 1196257.0203 | 2661924.0959 | 1196255.5211 | 2661909.42 | 1196252.1562
23 | 2661388.7103 | 1196687.5393 | 2661378.4425 | 1196695.8271
24 | 2661394.6985 | 1196668.984 | 2661391.991 | 1196680.4296 | 2661390.7849 | 1196685.8648 | 2661388.7103 | 1196687.5393
25 | 2661310.8094 | 1196748.8147 | 2661315.3976 | 1196741.8911 | 2661331.3647 | 1196727.7131 | 2661359.2027 | 1196707.3422 | 2661377.4425 | 1196696.6342 | 2661378.4425 | 1196695.8271
26 | 2661310.8094 | 1196748.8147 | 2661289.4548 | 1196727.5279 | 2661273.843 | 1196715.9613 | 2661258.4501 | 1196707.5654
27 | 2661310.8094 | 1196748.8147 | 2661325.9416 | 1196764.2854
28 | 2661258.4501 | 1196707.5654 | 2661259.5513 | 1196716.0705 | 2661268.563 | 1196735.3852 | 2661276.4993 | 1196746.6508 | 2661282.4794 | 1196753.316
29 | 2661258.4501 | 1196707.5654 | 2661248.1401 | 1196701.9455 | 2661230.8343 | 1196695.8648 | 2661213.9053 | 1196693.1455 | 2661189.2742 | 1196694.2163 | 2661166.4585 | 1196699.5195
30 | 2661352.4833 | 1196829.1555 | 2661349.7342 | 1196806.8032 | 2661347.4473 | 1196793.6054 | 2661342.7002 | 1196783.3507 | 2661338.9958 | 1196777.6316 | 2661325.9416 | 1196764.2854
31 | 2661166.4585 | 1196699.5195 | 2661167.8658 | 1196705.6708 | 2661172.2522 | 1196726.6501 | 2661176.1259 | 1196741.8986
32 | 2661352.4833 | 1196829.1555 | 2661360.8838 | 1196824.1054 | 2661373.3916 | 1196810.7593 | 2661382.8064 | 1196802.6289
33 | 2661178.3762 | 1196746.8022 | 2661176.1259 | 1196741.8986
34 | 2661956.0012 | 1196267.9921 | 2661950.2961 | 1196246.5761 | 2661937.8015 | 1196218.2762
35 | 2661956.0012 | 1196267.9921 | 2661967.9226 | 1196268.0934 | 2661975.798 | 1196266.1319
36 | 2661995.0066 | 1196261.3478 | 2661975.798 | 1196266.1319
37 | 2661995.0066 | 1196261.3478 | 2661995.8615 | 1196267.7938 | 2661996.4765 | 1196272.4028 | 2661996.9216 | 1196275.765 | 2661996.7326 | 1196277.8309
38 | 2661995.0066 | 1196261.3478 | 2662030.5624 | 1196249.6488
39 | 2661996.7326 | 1196277.8309 | 2661966.8497 | 1196278.9997 | 2661967.1722 | 1196281.666
40 | 2662030.5624 | 1196249.6488 | 2662055.0906 | 1196241.5782
41 | 2661967.1722 | 1196281.666 | 2661967.941 | 1196288.0225
42 | 2662055.0906 | 1196241.5782 | 2662056.7189 | 1196241.0424 | 2662067.9592 | 1196234.8443 | 2662080.9985 | 1196225.2892
43 | 2661967.3318 | 1196297.1709 | 2661963.6254 | 1196309.3174 | 2661961.4379 | 1196315.2982
44 | 2661967.3318 | 1196297.1709 | 2661968.1759 | 1196289.9643 | 2661967.941 | 1196288.0225
45 | 2661961.4379 | 1196315.2982 | 2662045.8902 | 1196523.9954
46 | 2662080.9985 | 1196225.2892 | 2662099.8767 | 1196211.4554
47 | 2662045.8902 | 1196523.9954 | 2661708.8664 | 1196646.7812
48 | 2661708.8664 | 1196646.7812 | 2661706.5554 | 1196650.0037 | 2661701.673 | 1196649.9533 | 2661697.7956 | 1196647.0005 | 2661693.0002 | 1196638.5128 | 2661687.8218 | 1196632.8335
49 | 2662101.6079 | 1196210.1869 | 2662099.8767 | 1196211.4554
50 | 2662101.6079 | 1196210.1869 | 2662103.2176 | 1196209.0073
51 | 2662103.2176 | 1196209.0073 | 2662107.7558 | 1196205.6817
52 | 2662107.7558 | 1196205.6817 | 2662128.3598 | 1196190.5833
53 | 2662128.3598 | 1196190.5833 | 2662129.2208 | 1196189.9524
54 | 2662132.7043 | 1196187.3997 | 2662129.2208 | 1196189.9524
55 | 2662132.7043 | 1196187.3997 | 2662161.5955 | 1196165.1535
56 | 2662132.7043 | 1196187.3997 | 2662147.6245 | 1196206.4189
57 | 2662161.5955 | 1196165.1535 | 2662180.4619 | 1196148.3079
58 | 2662161.5955 | 1196165.1535 | 2662181.7369 | 1196188.7321 | 2662186.5837 | 1196195.6574
59 | 2662180.4619 | 1196148.3079 | 2662185.8725 | 1196143.4768
60 | 2662194.8812 | 1196207.5131 | 2662186.5837 | 1196195.6574
61 | 2662185.8725 | 1196143.4768 | 2662186.1835 | 1196143.1991
62 | 2662192.2727 | 1196137.7621 | 2662186.1835 | 1196143.1991
63 | 2662192.2727 | 1196137.7621 | 2662196.8555 | 1196133.6702
64 | 2662196.8555 | 1196133.6702 | 2662210.064 | 1196121.8765 | 2662211.109 | 1196121.0059
65 | 2662215.3201 | 1196117.4975 | 2662211.109 | 1196121.0059
66 | 2662215.3201 | 1196117.4975 | 2662215.4837 | 1196117.3612
67 | 2662215.4837 | 1196117.3612 | 2662231.0256 | 1196104.4131
68 | 2662238.5559 | 1196098.3325 | 2662232.681 | 1196103.034 | 2662231.0256 | 1196104.4131
69 | 2662238.5559 | 1196098.3325 | 2662242.8294 | 1196094.9126 | 2662249.0586 | 1196089.3605
70 | 2662260.4081 | 1196079.253 | 2662257.563 | 1196081.7804 | 2662249.0586 | 1196089.3605
71 | 2662260.4081 | 1196079.253 | 2662264.7799 | 1196087.4144 | 2662269.7561 | 1196096.7053
72 | 2662256.5385 | 1196071.8862 | 2662260.4081 | 1196079.253
73 | 2662280.3221 | 1196116.4329 | 2662269.7561 | 1196096.7053
74 | 2662256.5385 | 1196071.8862 | 2662259.1587 | 1196070.4682 | 2662267.2572 | 1196066.0722 | 2662272.9987 | 1196061.6982
75 | 2662256.5385 | 1196071.8862 | 2662239.7519 | 1196040.7156 | 2662235.2592 | 1196032.5908
76 | 2662229.1972 | 1196021.6278 | 2662226.3593 | 1196016.4955 | 2662209.4446 | 1195985.9252
77 | 2662229.1972 | 1196021.6278 | 2662235.2592 | 1196032.5908
78 | 2662203.4534 | 1195975.097 | 2662209.4446 | 1195985.9252
79 | 2662199.5379 | 1195968.0206 | 2662203.4534 | 1195975.097
80 | 2662193.5022 | 1195957.112 | 2662199.5379 | 1195968.0206
81 | 2662314.4172 | 1196029.3417 | 2662299.3292 | 1196041.3694 | 2662286.1024 | 1196051.7155 | 2662272.9987 | 1196061.6982
82 | 2662314.4172 | 1196029.3417 | 2662331.0553 | 1196049.7945
83 | 2662314.4172 | 1196029.3417 | 2662334.333 | 1196013.4635
84 | 2662280.3221 | 1196116.4329 | 2662281.289 | 1196118.2381
85 | 2662331.0553 | 1196049.7945 | 2662349.0511 | 1196071.9163
86 | 2661505.5733 | 1196837.261 | 2661514.5203 | 1196843.35 | 2661543.8977 | 1196871.0239 | 2661543.8977 | 1196871.0239
87 | 2661447.3661 | 1196780.2453 | 2661505.5733 | 1196837.261
88 | 2661543.8977 | 1196871.0239 | 2661547.4893 | 1196875.8303 | 2661547.884 | 1196880.4037 | 2661547.7715 | 1196881.0522
89 | 2661447.3661 | 1196780.2453 | 2661440.7677 | 1196778.1763 | 2661433.8936 | 1196775.5152 | 2661425.5575 | 1196774.2845 | 2661418.9344 | 1196775.3616 | 2661410.5629 | 1196777.5769 | 2661405.0499 | 1196781.8228 | 2661400.6888 | 1196786.6475 | 2661385.873 | 1196799.981 | 2661382.8064 | 1196802.6289
90 | 2661530.3532 | 1196892.5638 | 2661530.3532 | 1196892.5638 | 2661545.0567 | 1196886.4448 | 2661547.2119 | 1196884.2769 | 2661547.7715 | 1196881.0522
91 | 2661675.6067 | 1196826.3098 | 2661547.7715 | 1196881.0522
92 | 2661382.8064 | 1196802.6289 | 2661391.8571 | 1196805.4901 | 2661401.0215 | 1196809.8867 | 2661409.8817 | 1196815.7144 | 2661412.9941 | 1196821.2051
93 | 2661530.3532 | 1196892.5638 | 2661527.7966 | 1196896.7289 | 2661523.1365 | 1196911.9712
94 | 2661675.6067 | 1196826.3098 | 2661669.2951 | 1196824.5103 | 2661658.7717 | 1196813.7956 | 2661645.6894 | 1196800.7976 | 2661637.4392 | 1196787.5382 | 2661623.5251 | 1196761.3685 | 2661614.1697 | 1196746.6969
95 | 2661675.6067 | 1196826.3098 | 2661780.7227 | 1196796.5548
96 | 2661675.6067 | 1196826.3098 | 2661675.2299 | 1196823.6933 | 2661663.5902 | 1196769.0636 | 2661653.0216 | 1196723.5614 | 2661647.8606 | 1196710.6599
97 | 2661523.1365 | 1196911.9712 | 2661518.6921 | 1196926.5082 | 2661509.9739 | 1196949.8433 | 2661506.6671 | 1196953.6337 | 2661503.6965 | 1196955.104 | 2661503.6965 | 1196955.104
98 | 2661614.1697 | 1196746.6969 | 2661602.7801 | 1196740.9095 | 2661588.0397 | 1196732.0748 | 2661580.9816 | 1196728.7891 | 2661577.1917 | 1196721.0345 | 2661571.5498 | 1196705.2339
99 | 2661601.0111 | 1196724.8153 | 2661610.5187 | 1196740.9893 | 2661614.1697 | 1196746.6969
100 | 2661680.1649 | 1196721.9069 | 2661676.8143 | 1196715.1462 | 2661668.5675 | 1196695.6498 | 2661664.4106 | 1196689.5145 | 2661661.2854 | 1196686.7584 | 2661657.888 | 1196684.5332 | 2661654.3567 | 1196683.474 | 2661651.0858 | 1196683.7627 | 2661647.9888 | 1196684.9092 | 2661645.4159 | 1196687.6843 | 2661643.0698 | 1196690.6285 | 2661642.0607 | 1196694.6649 | 2661643.1522 | 1196698.8897 | 2661647.8606 | 1196710.6599
101 | 2661424.3526 | 1196947.9068 | 2661425.8199 | 1196940.0284 | 2661427.5449 | 1196936.7219 | 2661431.9762 | 1196933.9547 | 2661437.1339 | 1196933.1294 | 2661446.0509 | 1196933.4101 | 2661457.0869 | 1196935.7804 | 2661470.2259 | 1196941.0518 | 2661493.3446 | 1196953.6189 | 2661497.6674 | 1196954.7307 | 2661503.6965 | 1196955.104
102 | 2661424.3526 | 1196947.9068 | 2661440.8412 | 1196951.8896 | 2661461.9576 | 1196960.6561 | 2661473.3834 | 1196971.78 | 2661482.1523 | 1196984.2329 | 2661502.5804 | 1196999.9187 | 2661516.6296 | 1197005.5442 | 2661524.0507 | 1197005.4327
103 | 2661680.1649 | 1196721.9069 | 2661682.1112 | 1196715.6344 | 2661679.9777 | 1196701.6598 | 2661668.0168 | 1196630.1392 | 2661667.1154 | 1196622.9924 | 2661668.7857 | 1196619.1073 | 2661672.3824 | 1196617.5213 | 2661676.9071 | 1196620.4919 | 2661685.2945 | 1196630.0617 | 2661687.8218 | 1196632.8335
104 | 2662293.0503 | 1196140.1974 | 2662281.289 | 1196118.2381
105 | 2662298.5879 | 1196150.5365 | 2662293.0503 | 1196140.1974
106 | 2662298.5879 | 1196150.5365 | 2662286.4219 | 1196157.0804 | 2662283.7106 | 1196158.5404
107 | 2662298.5879 | 1196150.5365 | 2662307.0286 | 1196166.3016
108 | 2662286.7434 | 1196167.1674 | 2662282.3307 | 1196159.2835 | 2662283.7106 | 1196158.5404
109 | 2662307.0286 | 1196166.3016 | 2662313.9041 | 1196179.1431
110 | 2662313.9041 | 1196179.1431 | 2662313.9476 | 1196179.2243
111 | 2662313.9476 | 1196179.2243 | 2662326.2796 | 1196202.2573
112 | 2662349.0511 | 1196071.9163 | 2662358.2804 | 1196083.2617
113 | 2662379.8594 | 1196109.7883 | 2662358.2804 | 1196083.2617
114 | 2662354.1801 | 1196192.9136 | 2662382.0752 | 1196179.2121 | 2662374.9072 | 1196163.8108
115 | 2662328.1281 | 1196205.7098 | 2662354.1801 | 1196192.9136
116 | 2662328.1281 | 1196205.7098 | 2662328.1958 | 1196205.8371
117 | 2662328.1281 | 1196205.7098 | 2662326.2796 | 1196202.2573
118 | 2662331.7695 | 1196212.5548 | 2662328.1958 | 1196205.8371
119 | 2662331.7695 | 1196212.5548 | 2662342.3425 | 1196232.4295
120 | 2662348.3333 | 1196243.6909 | 2662342.3425 | 1196232.4295
121 | 2662348.3333 | 1196243.6909 | 2662353.8607 | 1196254.081
122 | 2662353.8607 | 1196254.081 | 2662362.1468 | 1196269.657
123 | 2662362.1468 | 1196269.657 | 2662367.5083 | 1196279.7355

## bus_geodata
| x | y | coords
0 | 2661709.416 | 1195905.7928
1 | 2661725.3535 | 1195922.5707
2 | 2661693.5189 | 1195902.3109
3 | 2661838.9333 | 1195992.4312
4 | 2661667.4504 | 1195824.2843
5 | 2661591.1073 | 1195848.5175
6 | 2661686.7364 | 1195811.0905
7 | 2661731.6081 | 1196119.9005
8 | 2661727.4442 | 1196122.9314
9 | 2661914.5183 | 1196238.0118
10 | 2661726.4319 | 1196123.6683
11 | 2661761.3631 | 1195799.0398
12 | 2661688.788 | 1195809.8561
13 | 2661775.7525 | 1195793.6207
14 | 2661596.4406 | 1195858.8409
15 | 2661786.8784 | 1195789.4307
16 | 2661777.2635 | 1195773.9446
17 | 2661844.0976 | 1195768.7635
18 | 2661860.6003 | 1195760.2015
19 | 2661974.4726 | 1195683.1311
20 | 2661972.7239 | 1195718.2564
21 | 2661972.0767 | 1195731.2565
22 | 2661909.42 | 1196252.1562
23 | 2661388.7103 | 1196687.5393
24 | 2661378.4425 | 1196695.8271
25 | 2661394.6985 | 1196668.984
26 | 2661310.8094 | 1196748.8147
27 | 2661258.4501 | 1196707.5654
28 | 2661325.9416 | 1196764.2854
29 | 2661282.4794 | 1196753.316
30 | 2661166.4585 | 1196699.5195
31 | 2661352.4833 | 1196829.1555
32 | 2661176.1259 | 1196741.8986
33 | 2661178.3762 | 1196746.8022
34 | 2661937.8015 | 1196218.2762
35 | 2661956.0012 | 1196267.9921
36 | 2661975.798 | 1196266.1319
37 | 2661995.0066 | 1196261.3478
38 | 2661996.7326 | 1196277.8309
39 | 2662030.5624 | 1196249.6488
40 | 2661967.1722 | 1196281.666
41 | 2662055.0906 | 1196241.5782
42 | 2661967.3318 | 1196297.1709
43 | 2661961.4379 | 1196315.2982
44 | 2661967.941 | 1196288.0225
45 | 2662080.9985 | 1196225.2892
46 | 2662045.8902 | 1196523.9954
47 | 2661708.8664 | 1196646.7812
48 | 2662099.8767 | 1196211.4554
49 | 2662101.6079 | 1196210.1869
50 | 2662103.2176 | 1196209.0073
51 | 2662107.7558 | 1196205.6817
52 | 2662128.3598 | 1196190.5833
53 | 2662129.2208 | 1196189.9524
54 | 2662132.7043 | 1196187.3997
55 | 2662161.5955 | 1196165.1535
56 | 2662147.6245 | 1196206.4189
57 | 2662180.4619 | 1196148.3079
58 | 2662186.5837 | 1196195.6574
59 | 2662185.8725 | 1196143.4768
60 | 2662194.8812 | 1196207.5131
61 | 2662186.1835 | 1196143.1991
62 | 2662192.2727 | 1196137.7621
63 | 2662196.8555 | 1196133.6702
64 | 2662211.109 | 1196121.0059
65 | 2662215.3201 | 1196117.4975
66 | 2662215.4837 | 1196117.3612
67 | 2662231.0256 | 1196104.4131
68 | 2662238.5559 | 1196098.3325
69 | 2662249.0586 | 1196089.3605
70 | 2662260.4081 | 1196079.253
71 | 2662269.7561 | 1196096.7053
72 | 2662256.5385 | 1196071.8862
73 | 2662229.1972 | 1196021.6278
74 | 2662209.4446 | 1195985.9252
75 | 2662235.2592 | 1196032.5908
76 | 2662203.4534 | 1195975.0971
77 | 2662199.5379 | 1195968.0206
78 | 2662272.9987 | 1196061.6982
79 | 2662193.5022 | 1195957.112
80 | 2662314.4172 | 1196029.3417
81 | 2662280.3221 | 1196116.4329
82 | 2662331.0553 | 1196049.7945
83 | 2662334.333 | 1196013.4635
84 | 2661505.5733 | 1196837.261
85 | 2661543.8977 | 1196871.0239
86 | 2661447.3661 | 1196780.2453
87 | 2661547.7715 | 1196881.0522
88 | 2661382.8064 | 1196802.6289
89 | 2661530.3532 | 1196892.5638
90 | 2661675.6067 | 1196826.3098
91 | 2661523.1365 | 1196911.9712
92 | 2661614.1697 | 1196746.6969
93 | 2661780.7227 | 1196796.5548
94 | 2661647.8606 | 1196710.6599
95 | 2661503.6965 | 1196955.104
96 | 2661412.9941 | 1196821.2051
97 | 2661424.3526 | 1196947.9068
98 | 2661524.0507 | 1197005.4327
99 | 2661680.1649 | 1196721.9069
100 | 2661687.8218 | 1196632.8335
101 | 2661571.5498 | 1196705.2339
102 | 2661601.0111 | 1196724.8153
103 | 2662281.289 | 1196118.2381
104 | 2662293.0503 | 1196140.1974
105 | 2662298.5879 | 1196150.5365
106 | 2662283.7106 | 1196158.5404
107 | 2662307.0286 | 1196166.3016
108 | 2662286.7434 | 1196167.1674
109 | 2662313.9041 | 1196179.1431
110 | 2662313.9476 | 1196179.2243
111 | 2662349.0511 | 1196071.9163
112 | 2662358.2804 | 1196083.2617
113 | 2662379.8594 | 1196109.7883
114 | 2662354.1801 | 1196192.9136
115 | 2662374.9072 | 1196163.8108
116 | 2662328.1281 | 1196205.7098
117 | 2662328.1958 | 1196205.8371
118 | 2662326.2796 | 1196202.2573
119 | 2662331.7695 | 1196212.5548
120 | 2662342.3425 | 1196232.4295
121 | 2662348.3333 | 1196243.6909
122 | 2662353.8607 | 1196254.081
123 | 2662362.1468 | 1196269.657
124 | 2662367.5083 | 1196279.7355
125 | 2662161.5955 | 1196165.1535

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97777 | -0.4281 | 0.0014741 | 0.00036945
1 | 0.97838 | -0.41604 | 0.001706 | 0.00042756
2 | 0.97739 | -0.43546 | 0.0015435 | 0.00038683
3 | 0.98194 | -0.34658 | 0 | 0
4 | 0.97562 | -0.47034 | 0.0019693 | 0.00049356
5 | 0.97542 | -0.47423 | 0.00081113 | 0.00020329
6 | 0.9752 | -0.47858 | 0.00033477 | 8.39e-05
7 | 0.98627 | -0.26282 | 0.00095331 | 0.00023892
8 | 0.98627 | -0.26297 | 0.00066507 | 0.00016668
9 | 0.98935 | -0.20362 | 0.0075655 | 0.0018961
10 | 0.98627 | -0.26299 | 0.00088667 | 0.00022222
11 | 0.97389 | -0.50434 | 0.00069842 | 0.00017504
12 | 0.97515 | -0.4794 | 0.00072284 | 0.00018116
13 | 0.97364 | -0.50927 | 0.00068613 | 0.00017196
14 | 0.9754 | -0.47449 | 0.0012 | 0.00030074
15 | 0.97345 | -0.51294 | 0 | 0
16 | 0.97327 | -0.51665 | 0.011071 | 0.0027746
17 | 0.97313 | -0.51931 | 0.00033843 | 8.4819e-05
18 | 0.97304 | -0.52115 | 0.0011883 | 0.00029782
19 | 0.9725 | -0.53174 | 0 | 0
20 | 0.97237 | -0.53444 | 0.00068074 | 0.00017061
21 | 0.97232 | -0.53527 | 0.0034781 | 0.00087169
22 | 0.98963 | -0.19828 | 0 | 0
23 | 0.97817 | -0.42297 | 0.0016506 | 0.00041369
24 | 0.9782 | -0.42239 | 0.00020895 | 5.2368e-05
25 | 0.97816 | -0.42325 | 0.00075844 | 0.00019008
26 | 0.97841 | -0.41826 | 0 | 0
27 | 0.97833 | -0.41984 | 0 | 0
28 | 0.97849 | -0.41672 | 0.00023181 | 5.8096e-05
29 | 0.9783 | -0.42055 | 0.00074265 | 0.00018613
30 | 0.97829 | -0.42078 | 0 | 0
31 | 0.97877 | -0.41123 | 0 | 0
32 | 0.97826 | -0.42121 | 0.00034117 | 8.5506e-05
33 | 0.97826 | -0.42123 | 0.00020081 | 5.0329e-05
34 | 0.99049 | -0.18181 | 0.0013596 | 0.00034075
35 | 0.99056 | -0.18053 | 0 | 0
36 | 0.99092 | -0.17352 | 0.0013223 | 0.0003314
37 | 0.9913 | -0.16637 | 0 | 0
38 | 0.99102 | -0.17162 | 0 | 0
39 | 0.99231 | -0.14698 | 0.0028077 | 0.00070366
40 | 0.99049 | -0.1819 | 0.0010674 | 0.00026751
41 | 0.99304 | -0.13298 | 0.001203 | 0.0003015
42 | 0.99027 | -0.18633 | 0 | 0
43 | 0.99 | -0.19155 | 0.0022797 | 0.00057134
44 | 0.9904 | -0.1838 | 0.0012897 | 0.00032322
45 | 0.99392 | -0.11603 | 0.00212 | 0.00053132
46 | 0.98728 | -0.24428 | 0.0028464 | 0.00071336
47 | 0.98389 | -0.31043 | 0.0005713 | 0.00014318
48 | 0.99462 | -0.1027 | 0.0062812 | 0.0015742
49 | 0.99469 | -0.10136 | 0.0094379 | 0.0023654
50 | 0.99476 | -0.099943 | 0.00099509 | 0.00024939
51 | 0.99497 | -0.095914 | 0.0022416 | 0.00056179
52 | 0.99596 | -0.077138 | 0.0098488 | 0.0024684
53 | 0.996 | -0.076262 | 0.0068412 | 0.0017146
54 | 0.9962 | -0.072458 | 0 | 0
55 | 0.99802 | -0.037669 | 0 | 0
56 | 0.99601 | -0.076178 | 0.0087597 | 0.0021954
57 | 0.99952 | -0.0090696 | 0.0059458 | 0.0014901
58 | 0.99729 | -0.051764 | 0.016222 | 0.0040655
59 | 0.99997 | -0.00050754 | 0.0043039 | 0.0010787
60 | 0.99724 | -0.052823 | 0.0041735 | 0.001046
61 | 1 | 0 | -0.37879 | -0.096114
62 | 0.99912 | -0.016616 | 0.0071301 | 0.001787
63 | 0.99848 | -0.028757 | 0.0060663 | 0.0015203
64 | 0.99655 | -0.065524 | 0.004434 | 0.0011113
65 | 0.99601 | -0.075905 | 0.0053769 | 0.0013476
66 | 0.99599 | -0.076298 | 0.0039998 | 0.0010024
67 | 0.99406 | -0.11304 | 0.0020904 | 0.00052391
68 | 0.99315 | -0.13049 | 0.002348 | 0.00058845
69 | 0.99187 | -0.15517 | 0.0039623 | 0.00099304
70 | 0.99048 | -0.18186 | 0 | 0
71 | 0.98926 | -0.20544 | 0.0042833 | 0.0010735
72 | 0.98948 | -0.20123 | 0 | 0
73 | 0.98528 | -0.28256 | 0.022263 | 0.0055796
74 | 0.98338 | -0.31962 | 0.0026848 | 0.00067287
75 | 0.98613 | -0.26621 | 0.0086516 | 0.0021683
76 | 0.98284 | -0.33029 | 0.020839 | 0.0052228
77 | 0.98264 | -0.33422 | 0.019167 | 0.0048037
78 | 0.98859 | -0.21838 | 0.0043662 | 0.0010943
79 | 0.98255 | -0.33598 | 0.0077958 | 0.0019538
80 | 0.98641 | -0.26085 | 0 | 0
81 | 0.98797 | -0.23045 | 0.0024408 | 0.00061173
82 | 0.98548 | -0.2788 | 0.014398 | 0.0036085
83 | 0.98624 | -0.26416 | 0.0072388 | 0.0018142
84 | 0.97962 | -0.39444 | 0.00016741 | 4.1957e-05
85 | 0.97987 | -0.38956 | 0.00014261 | 3.5742e-05
86 | 0.97924 | -0.40195 | 0.00052961 | 0.00013273
87 | 0.97992 | -0.38846 | 0.00023646 | 5.9262e-05
88 | 0.97892 | -0.40817 | 0 | 0
89 | 0.9799 | -0.38893 | 0.00036479 | 9.1425e-05
90 | 0.98079 | -0.37139 | 0 | 0
91 | 0.97989 | -0.38922 | 0.00022691 | 5.6869e-05
92 | 0.9807 | -0.37328 | 0 | 0
93 | 0.98067 | -0.37379 | 0.0012152 | 0.00030455
94 | 0.98178 | -0.35195 | 0.00032446 | 8.1317e-05
95 | 0.97986 | -0.38971 | 0.00037336 | 9.3574e-05
96 | 0.97891 | -0.40843 | 0.00038856 | 9.7383e-05
97 | 0.97985 | -0.39001 | 0 | 0
98 | 0.97983 | -0.39038 | 0.00017102 | 4.2862e-05
99 | 0.9825 | -0.33787 | 0 | 0
100 | 0.98362 | -0.31588 | 0.00035037 | 8.7812e-05
101 | 0.98067 | -0.37369 | 0.00035387 | 8.8687e-05
102 | 0.98068 | -0.37359 | 0.00066089 | 0.00016563
103 | 0.98786 | -0.23266 | 0.0085911 | 0.0021531
104 | 0.98667 | -0.25566 | 0.0023952 | 0.0006003
105 | 0.98614 | -0.26601 | 0 | 0
106 | 0.98598 | -0.26913 | 0.0065849 | 0.0016503
107 | 0.9855 | -0.27849 | 0.0033741 | 0.00084564
108 | 0.98594 | -0.26984 | 0.0037372 | 0.00093664
109 | 0.98502 | -0.28779 | 0.0011223 | 0.00028129
110 | 0.98502 | -0.28784 | 0.0032647 | 0.00081822
111 | 0.98487 | -0.29087 | 0.0077608 | 0.001945
112 | 0.98465 | -0.29503 | 0.0076401 | 0.0019148
113 | 0.9844 | -0.30005 | 0.0081673 | 0.0020469
114 | 0.98396 | -0.30859 | 0.0048385 | 0.0012127
115 | 0.98383 | -0.31097 | 0.0027526 | 0.00068987
116 | 0.98416 | -0.30462 | 0 | 0
117 | 0.98416 | -0.30468 | 0.0012203 | 0.00030584
118 | 0.98427 | -0.30248 | 0.0007503 | 0.00018804
119 | 0.98401 | -0.30764 | 0.0019432 | 0.00048701
120 | 0.9836 | -0.31561 | 0.0055564 | 0.0013926
121 | 0.98343 | -0.31885 | 0.0071067 | 0.0017811
122 | 0.98336 | -0.32033 | 0.0012083 | 0.00030283
123 | 0.98326 | -0.32217 | 0.0031095 | 0.00077931
124 | 0.98323 | -0.32272 | 0.0026698 | 0.00066911
125 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.026288 | -0.0066163 | 0.026303 | 0.0066257 | 1.5163e-05 | 9.3877e-06 | 0.040017 | 0.040017 | 0.040017 | 0.97777 | -0.4281 | 0.97838 | -0.41604 | 10.9936
1 | 0.024814 | 0.0062469 | -0.024805 | -0.0062415 | 8.7175e-06 | 5.375e-06 | 0.037773 | 0.037774 | 0.037774 | 0.97777 | -0.4281 | 0.97739 | -0.43546 | 10.3774
2 | -0.028009 | -0.0070533 | 0.028103 | 0.0071113 | 9.3347e-05 | 5.8014e-05 | 0.042611 | 0.042611 | 0.042611 | 0.97838 | -0.41604 | 0.98194 | -0.34658 | 11.7064
3 | 0.023262 | 0.0058547 | -0.023223 | -0.0058309 | 3.8712e-05 | 2.3747e-05 | 0.035424 | 0.035424 | 0.035424 | 0.97739 | -0.43546 | 0.97562 | -0.47034 | 9.7319
4 | -0.028103 | -0.0071113 | 0.028216 | 0.0071818 | 0.00011346 | 7.0495e-05 | 0.042611 | 0.04261 | 0.042611 | 0.98194 | -0.34658 | 0.98627 | -0.26282 | 11.7063
5 | 0.0020115 | 0.00050281 | -0.0020111 | -0.00050389 | 3.7313e-07 | -1.0812e-06 | 0.0030675 | 0.0030679 | 0.0030679 | 0.97562 | -0.47034 | 0.97542 | -0.47423 | 0.84284
6 | 0.019242 | 0.0048346 | -0.019235 | -0.00483 | 7.5638e-06 | 4.5486e-06 | 0.029353 | 0.029353 | 0.029353 | 0.97562 | -0.47034 | 0.9752 | -0.47858 | 8.0641
7 | 0.0012 | 0.0003006 | -0.0012 | -0.00030074 | 1.4601e-08 | -1.3569e-07 | 0.0018305 | 0.0018306 | 0.0018306 | 0.97542 | -0.47423 | 0.9754 | -0.47449 | 0.50291
8 | 0.0189 | 0.0047461 | -0.018899 | -0.0047457 | 7.4694e-07 | 4.4817e-07 | 0.028842 | 0.028842 | 0.028842 | 0.9752 | -0.47858 | 0.97515 | -0.4794 | 7.9237
9 | 0.0015518 | 0.00038883 | -0.0015517 | -0.00038889 | 1.0586e-08 | -5.8949e-08 | 0.0023412 | 0.0023412 | 0.0023412 | 0.98627 | -0.26282 | 0.98627 | -0.26297 | 0.64318
10 | -0.030721 | -0.0078095 | 0.030809 | 0.0078602 | 8.7849e-05 | 5.0649e-05 | 0.046389 | 0.046387 | 0.046389 | 0.98627 | -0.26282 | 0.98935 | -0.20362 | 6.3722
11 | 0.00088668 | 0.00022221 | -0.00088667 | -0.00022222 | 8.4024e-10 | -1.544e-08 | 0.0013378 | 0.0013378 | 0.0013378 | 0.98627 | -0.26297 | 0.98627 | -0.26299 | 0.36752
12 | -0.038375 | -0.0097563 | 0.038385 | 0.0097622 | 9.8634e-06 | 5.9076e-06 | 0.057766 | 0.057766 | 0.057766 | 0.98935 | -0.20362 | 0.98963 | -0.19828 | 7.9349
13 | -0.018155 | -0.0045516 | 0.018177 | 0.0045645 | 2.1598e-05 | 1.289e-05 | 0.02774 | 0.027739 | 0.02774 | 0.97389 | -0.50434 | 0.97515 | -0.4794 | 7.6208
14 | 0.017457 | 0.0043766 | -0.017452 | -0.0043741 | 4.1021e-06 | 2.4341e-06 | 0.026673 | 0.026673 | 0.026673 | 0.97389 | -0.50434 | 0.97364 | -0.50927 | 7.3276
15 | 0.016766 | 0.0042022 | -0.016763 | -0.0042005 | 2.9273e-06 | 1.7256e-06 | 0.025624 | 0.025624 | 0.025624 | 0.97364 | -0.50927 | 0.97345 | -0.51294 | 7.0396
16 | 0.011073 | 0.0027757 | -0.011071 | -0.0027746 | 1.957e-06 | 1.0261e-06 | 0.016926 | 0.016926 | 0.016926 | 0.97345 | -0.51294 | 0.97327 | -0.51665 | 4.65
17 | 0.0056905 | 0.0014248 | -0.0056888 | -0.0014245 | 1.726e-06 | 3.4859e-07 | 0.008698 | 0.0086983 | 0.0086983 | 0.97345 | -0.51294 | 0.97313 | -0.51931 | 2.3896
18 | 0.0053504 | 0.0013396 | -0.0053499 | -0.0013396 | 4.6779e-07 | 6.7838e-08 | 0.0081808 | 0.0081809 | 0.0081809 | 0.97313 | -0.51931 | 0.97304 | -0.52115 | 2.2475
19 | 0.0041616 | 0.0010418 | -0.0041595 | -0.0010421 | 2.0987e-06 | -3.7236e-07 | 0.0063636 | 0.0063643 | 0.0063643 | 0.97304 | -0.52115 | 0.9725 | -0.53174 | 1.7484
20 | 0.0041595 | 0.0010421 | -0.0041589 | -0.0010422 | 5.3419e-07 | -9.4423e-08 | 0.0063643 | 0.0063644 | 0.0063644 | 0.9725 | -0.53174 | 0.97237 | -0.53444 | 1.7485
21 | 0.0034782 | 0.00087161 | -0.0034781 | -0.00087169 | 1.3829e-07 | -7.2946e-08 | 0.0053227 | 0.0053227 | 0.0053227 | 0.97237 | -0.53444 | 0.97232 | -0.53527 | 1.4623
22 | -0.038385 | -0.0097622 | 0.038417 | 0.0097819 | 3.2866e-05 | 1.9683e-05 | 0.057766 | 0.057765 | 0.057766 | 0.98963 | -0.19828 | 0.99056 | -0.18053 | 7.9349
23 | -0.0024091 | -0.00060353 | 0.0024092 | 0.0006034 | 6.6452e-08 | -1.2311e-07 | 0.0036647 | 0.0036646 | 0.0036647 | 0.97817 | -0.42297 | 0.9782 | -0.42239 | 1.0068
24 | 0.00075845 | 0.00018984 | -0.00075844 | -0.00019008 | 9.9806e-09 | -2.446e-07 | 0.0011537 | 0.0011538 | 0.0011538 | 0.97817 | -0.42297 | 0.97816 | -0.42325 | 0.31697
25 | -0.0026181 | -0.00065577 | 0.0026186 | 0.00065501 | 5.1494e-07 | -7.5769e-07 | 0.0039824 | 0.0039821 | 0.0039824 | 0.9782 | -0.42239 | 0.97841 | -0.41826 | 1.0941
26 | 0.0012848 | 0.00031875 | -0.0012847 | -0.00031953 | 9.5829e-08 | -7.8005e-07 | 0.0019528 | 0.0019531 | 0.0019531 | 0.97841 | -0.41826 | 0.97833 | -0.41984 | 0.53657
27 | -0.0039034 | -0.00097377 | 0.0039037 | 0.00097368 | 2.8584e-07 | -8.8872e-08 | 0.0059349 | 0.0059348 | 0.0059349 | 0.97841 | -0.41826 | 0.97849 | -0.41672 | 1.6305
28 | 0.00074267 | 0.00018548 | -0.00074265 | -0.00018613 | 2.5162e-08 | -6.4433e-07 | 0.0011294 | 0.0011296 | 0.0011296 | 0.97833 | -0.41984 | 0.9783 | -0.42055 | 0.31033
29 | 0.00054202 | 0.00013405 | -0.000542 | -0.00013523 | 2.42e-08 | -1.178e-06 | 0.00082376 | 0.00082419 | 0.00082419 | 0.97833 | -0.41984 | 0.97829 | -0.42078 | 0.22643
30 | -0.0041355 | -0.0010318 | 0.0041366 | 0.0010315 | 1.0776e-06 | -2.2376e-07 | 0.0062873 | 0.006287 | 0.0062873 | 0.97849 | -0.41672 | 0.97877 | -0.41123 | 1.7273
31 | 0.000542 | 0.00013523 | -0.00054199 | -0.00013577 | 1.1077e-08 | -5.3877e-07 | 0.00082419 | 0.00082438 | 0.00082438 | 0.97829 | -0.42078 | 0.97826 | -0.42121 | 0.22648
32 | -0.0041366 | -0.0010315 | 0.0041372 | 0.0010314 | 5.9985e-07 | -1.2482e-07 | 0.006287 | 0.0062868 | 0.006287 | 0.97877 | -0.41123 | 0.97892 | -0.40817 | 1.7272
33 | 0.00020082 | 5.0261e-05 | -0.00020081 | -5.0329e-05 | 1.8876e-10 | -6.7619e-08 | 0.00030543 | 0.00030546 | 0.00030546 | 0.97826 | -0.42121 | 0.97826 | -0.42123 | 0.083916
34 | -0.0013596 | -0.00034075 | 0.0013597 | 0.00034012 | 8.306e-08 | -6.3031e-07 | 0.0020425 | 0.0020423 | 0.0020425 | 0.99049 | -0.18181 | 0.99056 | -0.18053 | 0.56113
35 | -0.039777 | -0.010122 | 0.039791 | 0.01013 | 1.3439e-05 | 8.0849e-06 | 0.059808 | 0.059808 | 0.059808 | 0.99056 | -0.18053 | 0.99092 | -0.17352 | 8.2153
36 | -0.041113 | -0.010461 | 0.041127 | 0.01047 | 1.4172e-05 | 8.5601e-06 | 0.061793 | 0.061793 | 0.061793 | 0.99092 | -0.17352 | 0.9913 | -0.16637 | 8.4881
37 | 0.01782 | 0.0044828 | -0.017816 | -0.0044802 | 4.4618e-06 | 2.6413e-06 | 0.026755 | 0.026755 | 0.026755 | 0.9913 | -0.16637 | 0.99102 | -0.17162 | 7.3504
38 | -0.058947 | -0.014953 | 0.059002 | 0.014987 | 5.5029e-05 | 3.4252e-05 | 0.088548 | 0.088548 | 0.088548 | 0.9913 | -0.16637 | 0.99231 | -0.14698 | 12.1632
39 | 0.017816 | 0.0044802 | -0.017807 | -0.004475 | 8.749e-06 | 5.1796e-06 | 0.026755 | 0.026755 | 0.026755 | 0.99102 | -0.17162 | 0.99049 | -0.1819 | 7.3504
40 | -0.06181 | -0.015691 | 0.061851 | 0.015717 | 4.1657e-05 | 2.5993e-05 | 0.092758 | 0.092758 | 0.092758 | 0.99231 | -0.14698 | 0.99304 | -0.13298 | 12.7415
41 | 0.016739 | 0.0042075 | -0.016738 | -0.0042066 | 1.519e-06 | 8.8973e-07 | 0.025152 | 0.025152 | 0.025152 | 0.99049 | -0.1819 | 0.9904 | -0.1838 | 6.9099
42 | -0.063054 | -0.016018 | 0.063106 | 0.01605 | 5.1496e-05 | 3.2162e-05 | 0.09456 | 0.09456 | 0.09456 | 0.99304 | -0.13298 | 0.99392 | -0.11603 | 12.9891
43 | 0.015446 | 0.0038823 | -0.015443 | -0.0038801 | 3.8533e-06 | 2.2208e-06 | 0.023214 | 0.023214 | 0.023214 | 0.99027 | -0.18633 | 0.99 | -0.19155 | 6.3776
44 | -0.015446 | -0.0038823 | 0.015448 | 0.0038834 | 1.8616e-06 | 1.0729e-06 | 0.023214 | 0.023214 | 0.023214 | 0.99027 | -0.18633 | 0.9904 | -0.1838 | 6.3776
45 | 0.013163 | 0.0033087 | -0.01313 | -0.0032904 | 3.306e-05 | 1.8271e-05 | 0.019788 | 0.019789 | 0.019789 | 0.99 | -0.19155 | 0.98728 | -0.24428 | 5.4365
46 | -0.065226 | -0.016582 | 0.065268 | 0.016608 | 4.1917e-05 | 2.622e-05 | 0.097734 | 0.097734 | 0.097734 | 0.99392 | -0.11603 | 0.99462 | -0.1027 | 13.425
47 | 0.010283 | 0.0025771 | -0.010251 | -0.002561 | 3.2315e-05 | 1.6111e-05 | 0.015499 | 0.015501 | 0.015501 | 0.98728 | -0.24428 | 0.98389 | -0.31043 | 4.2584
48 | 0.0096798 | 0.0024178 | -0.0096773 | -0.0024166 | 2.503e-06 | 1.2063e-06 | 0.014637 | 0.014637 | 0.014637 | 0.98389 | -0.31043 | 0.98362 | -0.31588 | 4.0211
49 | -0.071549 | -0.018182 | 0.071554 | 0.018185 | 4.6184e-06 | 2.9001e-06 | 0.10713 | 0.10713 | 0.10713 | 0.99462 | -0.1027 | 0.99469 | -0.10136 | 14.7158
50 | -0.080991 | -0.02055 | 0.080997 | 0.020554 | 5.501e-06 | 3.4688e-06 | 0.12125 | 0.12125 | 0.12125 | 0.99469 | -0.10136 | 0.99476 | -0.099943 | 16.6551
51 | -0.081992 | -0.020803 | 0.082008 | 0.020813 | 1.5892e-05 | 1.0025e-05 | 0.12274 | 0.12274 | 0.12274 | 0.99476 | -0.099943 | 0.99497 | -0.095914 | 16.8596
52 | -0.084249 | -0.021375 | 0.084326 | 0.021423 | 7.6146e-05 | 4.8069e-05 | 0.12609 | 0.12609 | 0.12609 | 0.99497 | -0.095914 | 0.99596 | -0.077138 | 17.3201
53 | -0.094174 | -0.023892 | 0.094178 | 0.023894 | 3.9683e-06 | 2.5119e-06 | 0.1408 | 0.1408 | 0.1408 | 0.99596 | -0.077138 | 0.996 | -0.076262 | 19.3413
54 | -0.10102 | -0.025609 | 0.10104 | 0.02562 | 1.8469e-05 | 1.1708e-05 | 0.15103 | 0.15103 | 0.15103 | 0.996 | -0.076262 | 0.9962 | -0.072458 | 20.7452
55 | -0.1098 | -0.027816 | 0.10998 | 0.027933 | 0.00018382 | 0.0001167 | 0.16411 | 0.16411 | 0.16411 | 0.9962 | -0.072458 | 0.99802 | -0.037669 | 22.5428
56 | 0.0087612 | 0.0021961 | -0.0087597 | -0.0021954 | 1.5525e-06 | 6.7892e-07 | 0.013087 | 0.013087 | 0.013087 | 0.9962 | -0.072458 | 0.99601 | -0.076178 | 3.5953
57 | -0.13039 | -0.033053 | 0.13057 | 0.033167 | 0.00017948 | 0.00011421 | 0.19454 | 0.19454 | 0.19454 | 0.99802 | -0.037669 | 0.99952 | -0.0090696 | 26.7228
58 | 0.020409 | 0.0051197 | -0.020395 | -0.0051114 | 1.3704e-05 | 8.2553e-06 | 0.030431 | 0.030431 | 0.030431 | 0.99802 | -0.037669 | 0.99729 | -0.051764 | 8.3602
59 | -0.13652 | -0.034657 | 0.13657 | 0.034693 | 5.6263e-05 | 3.5818e-05 | 0.20339 | 0.20339 | 0.20339 | 0.99952 | -0.0090696 | 0.99997 | -0.00050754 | 27.9387
60 | 0.0041737 | 0.0010459 | -0.0041735 | -0.001046 | 2.1045e-07 | -5.4123e-08 | 0.0062274 | 0.0062275 | 0.0062275 | 0.99729 | -0.051764 | 0.99724 | -0.052823 | 1.7108
61 | -0.14088 | -0.035772 | 0.14088 | 0.035774 | 3.4408e-06 | 2.1912e-06 | 0.2098 | 0.2098 | 0.2098 | 0.99997 | -0.00050754 | 1 | 0 | 28.8184
62 | 0.23626 | 0.06034 | -0.23607 | -0.060219 | 0.0001896 | 0.00012113 | 0.35195 | 0.35195 | 0.35195 | 1 | 0 | 0.99912 | -0.016616 | 48.3452
63 | 0.22894 | 0.058432 | -0.2288 | -0.058346 | 0.00013421 | 8.5736e-05 | 0.34133 | 0.34133 | 0.34133 | 0.99912 | -0.016616 | 0.99848 | -0.028757 | 46.8865
64 | 0.22274 | 0.056826 | -0.22234 | -0.056573 | 0.00039477 | 0.00025215 | 0.33229 | 0.33229 | 0.33229 | 0.99848 | -0.028757 | 0.99655 | -0.065524 | 45.6447
65 | 0.21791 | 0.055462 | -0.2178 | -0.055392 | 0.000109 | 6.9618e-05 | 0.32567 | 0.32567 | 0.32567 | 0.99655 | -0.065524 | 0.99601 | -0.075905 | 44.7353
66 | 0.21242 | 0.054045 | -0.21242 | -0.054042 | 4.0271e-06 | 2.5718e-06 | 0.31764 | 0.31764 | 0.31764 | 0.99601 | -0.075905 | 0.99599 | -0.076298 | 43.6319
67 | 0.20842 | 0.05304 | -0.20805 | -0.052805 | 0.00036842 | 0.00023526 | 0.31166 | 0.31166 | 0.31166 | 0.99599 | -0.076298 | 0.99406 | -0.11304 | 42.8111
68 | 0.20596 | 0.052281 | -0.20579 | -0.05217 | 0.00017276 | 0.00011032 | 0.30854 | 0.30854 | 0.30854 | 0.99406 | -0.11304 | 0.99315 | -0.13049 | 42.3813
69 | 0.20344 | 0.051582 | -0.2032 | -0.051428 | 0.00024104 | 0.00015391 | 0.30502 | 0.30502 | 0.30502 | 0.99315 | -0.13049 | 0.99187 | -0.15517 | 41.8981
70 | 0.19923 | 0.050435 | -0.19898 | -0.050272 | 0.00025488 | 0.00016273 | 0.29907 | 0.29907 | 0.29907 | 0.99187 | -0.15517 | 0.99048 | -0.18186 | 41.0816
71 | 0.067269 | 0.01698 | -0.067193 | -0.016931 | 7.5889e-05 | 4.8315e-05 | 0.1011 | 0.1011 | 0.1011 | 0.99048 | -0.18186 | 0.98926 | -0.20544 | 27.7754
72 | 0.13171 | 0.033293 | -0.13159 | -0.033215 | 0.00012224 | 7.8125e-05 | 0.19797 | 0.19797 | 0.19797 | 0.99048 | -0.18186 | 0.98948 | -0.20123 | 54.3878
73 | 0.06291 | 0.015858 | -0.062835 | -0.01581 | 7.5197e-05 | 4.7839e-05 | 0.09466 | 0.09466 | 0.09466 | 0.98926 | -0.20544 | 0.98797 | -0.23045 | 26.0054
74 | 0.049756 | 0.01254 | -0.049716 | -0.012514 | 4.0783e-05 | 2.5852e-05 | 0.07485 | 0.07485 | 0.07485 | 0.98948 | -0.20123 | 0.98859 | -0.21838 | 20.5633
75 | 0.081832 | 0.020675 | -0.081578 | -0.020513 | 0.00025403 | 0.00016201 | 0.12312 | 0.12312 | 0.12312 | 0.98948 | -0.20123 | 0.98613 | -0.26621 | 33.8246
76 | 0.050607 | 0.012729 | -0.050517 | -0.012672 | 8.9415e-05 | 5.6707e-05 | 0.076444 | 0.076444 | 0.076444 | 0.98528 | -0.28256 | 0.98338 | -0.31962 | 21.0012
77 | -0.07287 | -0.018308 | 0.072926 | 0.018345 | 5.6912e-05 | 3.6264e-05 | 0.11007 | 0.11007 | 0.11007 | 0.98528 | -0.28256 | 0.98613 | -0.26621 | 30.2381
78 | 0.047832 | 0.011999 | -0.047808 | -0.011984 | 2.4313e-05 | 1.5404e-05 | 0.072382 | 0.072382 | 0.072382 | 0.98338 | -0.31962 | 0.98284 | -0.33029 | 19.8852
79 | 0.026969 | 0.0067609 | -0.026964 | -0.0067578 | 5.0563e-06 | 3.1335e-06 | 0.040831 | 0.040831 | 0.040831 | 0.98284 | -0.33029 | 0.98264 | -0.33422 | 11.2174
80 | 0.0077965 | 0.0019541 | -0.0077958 | -0.0019538 | 6.5166e-07 | 2.5915e-07 | 0.011806 | 0.011806 | 0.011806 | 0.98264 | -0.33422 | 0.98255 | -0.33598 | 3.2435
81 | 0.045349 | 0.011419 | -0.045257 | -0.011361 | 9.1889e-05 | 5.8136e-05 | 0.068278 | 0.068279 | 0.068279 | 0.98859 | -0.21838 | 0.98641 | -0.26085 | 18.7579
82 | 0.038018 | 0.0095467 | -0.037985 | -0.0095262 | 3.2527e-05 | 2.0481e-05 | 0.057357 | 0.057357 | 0.057357 | 0.98641 | -0.26085 | 0.98548 | -0.2788 | 15.7574
83 | 0.00724 | 0.0018146 | -0.0072388 | -0.0018142 | 1.1393e-06 | 4.0411e-07 | 0.010922 | 0.010922 | 0.010922 | 0.98641 | -0.26085 | 0.98624 | -0.26416 | 3.0005
84 | 0.060394 | 0.015198 | -0.060388 | -0.015194 | 6.3571e-06 | 4.0423e-06 | 0.090984 | 0.090984 | 0.090984 | 0.98797 | -0.23045 | 0.98786 | -0.23266 | 24.9955
85 | 0.023587 | 0.0059177 | -0.023573 | -0.0059094 | 1.3566e-05 | 8.319e-06 | 0.035617 | 0.035617 | 0.035617 | 0.98548 | -0.2788 | 0.98487 | -0.29087 | 9.7849
86 | -0.0052259 | -0.0013031 | 0.0052271 | 0.0013032 | 1.2086e-06 | 1.2899e-07 | 0.0079356 | 0.0079354 | 0.0079356 | 0.97962 | -0.39444 | 0.97987 | -0.38956 | 2.1801
87 | 0.0050585 | 0.0012611 | -0.0050567 | -0.001261 | 1.8029e-06 | 1.2843e-07 | 0.0076813 | 0.0076817 | 0.0076817 | 0.97962 | -0.39444 | 0.97924 | -0.40195 | 2.1104
88 | -0.0053697 | -0.0013389 | 0.00537 | 0.001339 | 2.8032e-07 | 3.7704e-08 | 0.008152 | 0.0081519 | 0.008152 | 0.97987 | -0.38956 | 0.97992 | -0.38846 | 2.2396
89 | 0.0045271 | 0.0011283 | -0.0045257 | -0.0011284 | 1.3367e-06 | -9.2368e-08 | 0.0068769 | 0.0068773 | 0.0068773 | 0.97924 | -0.40195 | 0.97892 | -0.40817 | 1.8894
90 | 0.0011361 | 0.00028093 | -0.0011361 | -0.0002812 | 2.4803e-08 | -2.6449e-07 | 0.0017239 | 0.001724 | 0.001724 | 0.97992 | -0.38846 | 0.9799 | -0.38893 | 0.47362
91 | -0.0067426 | -0.0016792 | 0.0067481 | 0.0016809 | 5.4623e-06 | 1.7425e-06 | 0.010235 | 0.010234 | 0.010235 | 0.97992 | -0.38846 | 0.98079 | -0.37139 | 2.8118
92 | 0.00038857 | 9.6927e-05 | -0.00038856 | -9.7383e-05 | 4.7737e-09 | -4.5582e-07 | 0.00059048 | 0.00059064 | 0.00059064 | 0.97892 | -0.40817 | 0.97891 | -0.40843 | 0.16226
93 | 0.00077132 | 0.00018977 | -0.00077131 | -0.00019003 | 1.0692e-08 | -2.555e-07 | 0.00117 | 0.0011701 | 0.0011701 | 0.9799 | -0.38893 | 0.97989 | -0.38922 | 0.32146
94 | 0.0010149 | 0.00025198 | -0.0010148 | -0.00025321 | 9.1119e-08 | -1.2361e-06 | 0.0015389 | 0.0015393 | 0.0015393 | 0.98079 | -0.37139 | 0.9807 | -0.37328 | 0.42289
95 | 0.0012153 | 0.00030326 | -0.0012152 | -0.00030455 | 1.3924e-07 | -1.2894e-06 | 0.0018433 | 0.0018438 | 0.0018438 | 0.98079 | -0.37139 | 0.98067 | -0.37379 | 0.50654
96 | -0.0089782 | -0.0022362 | 0.0089865 | 0.00224 | 8.281e-06 | 3.7951e-06 | 0.013616 | 0.013616 | 0.013616 | 0.98079 | -0.37139 | 0.98178 | -0.35195 | 3.7408
97 | 0.0005444 | 0.00013316 | -0.00054439 | -0.00013376 | 1.2387e-08 | -6.0246e-07 | 0.00082555 | 0.00082576 | 0.00082576 | 0.97989 | -0.38922 | 0.97986 | -0.38971 | 0.22686
98 | 0.00035387 | 8.7896e-05 | -0.00035387 | -8.8687e-05 | 6.8145e-09 | -7.9135e-07 | 0.00053665 | 0.00053694 | 0.00053694 | 0.9807 | -0.37328 | 0.98067 | -0.37369 | 0.14751
99 | 0.00066089 | 0.00016532 | -0.00066089 | -0.00016563 | 9.6226e-09 | -3.1585e-07 | 0.0010027 | 0.0010028 | 0.0010028 | 0.9807 | -0.37328 | 0.98068 | -0.37359 | 0.27549
100 | -0.009311 | -0.0023213 | 0.0093172 | 0.0023242 | 6.2226e-06 | 2.9273e-06 | 0.014108 | 0.014107 | 0.014108 | 0.98178 | -0.35195 | 0.9825 | -0.33787 | 3.8757
101 | 0.00017103 | 4.0186e-05 | -0.00017102 | -4.1361e-05 | 2.3487e-09 | -1.1746e-06 | 0.00025879 | 0.00025919 | 0.00025919 | 0.97986 | -0.38971 | 0.97985 | -0.39001 | 0.071207
102 | 0.00017102 | 4.1361e-05 | -0.00017102 | -4.2862e-05 | 3.0119e-09 | -1.5009e-06 | 0.00025919 | 0.00025972 | 0.00025972 | 0.97985 | -0.39001 | 0.97983 | -0.39038 | 0.071352
103 | -0.0093172 | -0.0023242 | 0.0093269 | 0.0023288 | 9.7366e-06 | 4.5773e-06 | 0.014107 | 0.014107 | 0.014107 | 0.9825 | -0.33787 | 0.98362 | -0.31588 | 3.8756
104 | 0.051797 | 0.013041 | -0.05174 | -0.013005 | 5.6896e-05 | 3.6095e-05 | 0.078043 | 0.078043 | 0.078043 | 0.98786 | -0.23266 | 0.98667 | -0.25566 | 21.4403
105 | 0.049344 | 0.012405 | -0.04932 | -0.012389 | 2.4366e-05 | 1.5445e-05 | 0.074431 | 0.074431 | 0.074431 | 0.98667 | -0.25566 | 0.98614 | -0.26601 | 20.448
106 | 0.010324 | 0.0025877 | -0.010322 | -0.0025869 | 1.5374e-06 | 7.6842e-07 | 0.015578 | 0.015578 | 0.015578 | 0.98614 | -0.26601 | 0.98598 | -0.26913 | 4.2797
107 | 0.038996 | 0.0098015 | -0.038973 | -0.0097869 | 2.3227e-05 | 1.4637e-05 | 0.058853 | 0.058853 | 0.058853 | 0.98614 | -0.26601 | 0.9855 | -0.27849 | 16.1683
108 | 0.0037374 | 0.00093659 | -0.0037372 | -0.00093664 | 1.2648e-07 | -5.4265e-08 | 0.0056403 | 0.0056404 | 0.0056404 | 0.98598 | -0.26913 | 0.98594 | -0.26984 | 1.5495
109 | 0.035599 | 0.0089412 | -0.035583 | -0.0089313 | 1.5786e-05 | 9.9174e-06 | 0.053758 | 0.053758 | 0.053758 | 0.9855 | -0.27849 | 0.98502 | -0.28779 | 14.7687
110 | 0.034461 | 0.00865 | -0.034461 | -0.00865 | 9.369e-08 | 5.8788e-08 | 0.052063 | 0.052063 | 0.052063 | 0.98502 | -0.28779 | 0.98502 | -0.28784 | 14.3029
111 | 0.031196 | 0.0078318 | -0.031174 | -0.0078182 | 2.1763e-05 | 1.3596e-05 | 0.047131 | 0.047131 | 0.047131 | 0.98502 | -0.28784 | 0.98427 | -0.30248 | 12.9481
112 | 0.015812 | 0.0039643 | -0.015809 | -0.0039625 | 3.1305e-06 | 1.8174e-06 | 0.023891 | 0.023891 | 0.023891 | 0.98487 | -0.29087 | 0.98465 | -0.29503 | 6.5635
113 | 0.0081693 | 0.0020477 | -0.0081673 | -0.0020469 | 1.9545e-06 | 8.1601e-07 | 0.012346 | 0.012346 | 0.012346 | 0.98465 | -0.29503 | 0.9844 | -0.30005 | 3.3917
114 | 0.0027529 | 0.00068946 | -0.0027526 | -0.00068987 | 3.124e-07 | -4.1051e-07 | 0.004163 | 0.0041633 | 0.0041633 | 0.98396 | -0.30859 | 0.98383 | -0.31097 | 1.1438
115 | -0.0075915 | -0.0019021 | 0.0075929 | 0.0019027 | 1.4345e-06 | 5.4934e-07 | 0.01148 | 0.01148 | 0.01148 | 0.98396 | -0.30859 | 0.98416 | -0.30462 | 3.1539
116 | 0.022828 | 0.0057255 | -0.022828 | -0.0057255 | 6.4444e-08 | 3.9411e-08 | 0.034517 | 0.034517 | 0.034517 | 0.98416 | -0.30462 | 0.98416 | -0.30468 | 9.4826
117 | -0.030421 | -0.0076282 | 0.030424 | 0.0076301 | 3.1071e-06 | 1.9387e-06 | 0.045997 | 0.045997 | 0.045997 | 0.98416 | -0.30462 | 0.98427 | -0.30248 | 12.6364
118 | 0.021608 | 0.0054196 | -0.021604 | -0.0054178 | 3.0458e-06 | 1.8527e-06 | 0.032671 | 0.032672 | 0.032672 | 0.98416 | -0.30468 | 0.98401 | -0.30764 | 8.9757
119 | 0.019661 | 0.0049308 | -0.019654 | -0.0049263 | 7.4632e-06 | 4.4906e-06 | 0.029733 | 0.029733 | 0.029733 | 0.98401 | -0.30764 | 0.9836 | -0.31561 | 8.1684
120 | 0.014097 | 0.0035337 | -0.014095 | -0.0035325 | 2.1758e-06 | 1.2306e-06 | 0.021327 | 0.021327 | 0.021327 | 0.9836 | -0.31561 | 0.98343 | -0.31885 | 5.8592
121 | 0.0069886 | 0.0017514 | -0.0069881 | -0.0017512 | 4.9348e-07 | 1.6652e-07 | 0.010574 | 0.010574 | 0.010574 | 0.98343 | -0.31885 | 0.98336 | -0.32033 | 2.9051
122 | 0.0057798 | 0.0014484 | -0.0057793 | -0.0014483 | 5.0608e-07 | 1.0009e-07 | 0.008746 | 0.0087461 | 0.0087461 | 0.98336 | -0.32033 | 0.98326 | -0.32217 | 2.4028
123 | 0.0026698 | 0.00066901 | -0.0026698 | -0.00066911 | 6.9885e-08 | -1.0007e-07 | 0.0040404 | 0.0040404 | 0.0040404 | 0.98326 | -0.32217 | 0.98323 | -0.32272 | 1.11

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38763 | 0.09833

## res_load
| p_mw | q_mvar
0 | 0.0014741 | 0.00036945
1 | 0.001706 | 0.00042756
2 | 0.0015435 | 0.00038683
3 | 0.0019693 | 0.00049356
4 | 0.00081113 | 0.00020329
5 | 0.00033477 | 8.39e-05
6 | 0.00095331 | 0.00023892
7 | 0.00066507 | 0.00016668
8 | 0.0075655 | 0.0018961
9 | 0.00088667 | 0.00022222
10 | 0.00069842 | 0.00017504
11 | 0.00072284 | 0.00018116
12 | 0.00068613 | 0.00017196
13 | 0.0012 | 0.00030074
14 | 0.011071 | 0.0027746
15 | 0.00033843 | 8.4819e-05
16 | 0.0011883 | 0.00029782
17 | 0.00068074 | 0.00017061
18 | 0.0034781 | 0.00087169
19 | 0.0016506 | 0.00041369
20 | 0.00020895 | 5.2368e-05
21 | 0.00075844 | 0.00019008
22 | 0.00023181 | 5.8096e-05
23 | 0.00074265 | 0.00018613
24 | 0.00034117 | 8.5506e-05
25 | 0.00020081 | 5.0329e-05
26 | 0.0013596 | 0.00034075
27 | 0.0013223 | 0.0003314
28 | 0.0028077 | 0.00070366
29 | 0.0010674 | 0.00026751
30 | 0.001203 | 0.0003015
31 | 0.0022797 | 0.00057134
32 | 0.0012897 | 0.00032322
33 | 0.00212 | 0.00053132
34 | 0.0028464 | 0.00071336
35 | 0.0005713 | 0.00014318
36 | 0.0062812 | 0.0015742
37 | 0.0094379 | 0.0023654
38 | 0.00099509 | 0.00024939
39 | 0.0022416 | 0.00056179
40 | 0.0098488 | 0.0024684
41 | 0.0068412 | 0.0017146
42 | 0.0087597 | 0.0021954
43 | 0.0059458 | 0.0014901
44 | 0.016222 | 0.0040655
45 | 0.0043039 | 0.0010787
46 | 0.0041735 | 0.001046
47 | 0.0088446 | 0.0022167
48 | 0.0071301 | 0.001787
49 | 0.0060663 | 0.0015203
50 | 0.004434 | 0.0011113
51 | 0.0053769 | 0.0013476
52 | 0.0039998 | 0.0010024
53 | 0.0020904 | 0.00052391
54 | 0.002348 | 0.00058845
55 | 0.0039623 | 0.00099304
56 | 0.0042833 | 0.0010735
57 | 0.022263 | 0.0055796
58 | 0.0026848 | 0.00067287
59 | 0.0086516 | 0.0021683
60 | 0.020839 | 0.0052228
61 | 0.019167 | 0.0048037
62 | 0.0043662 | 0.0010943
63 | 0.0077958 | 0.0019538
64 | 0.0024408 | 0.00061173
65 | 0.014398 | 0.0036085
66 | 0.0072388 | 0.0018142
67 | 0.00016741 | 4.1957e-05
68 | 0.00014261 | 3.5742e-05
69 | 0.00052961 | 0.00013273
70 | 0.00023646 | 5.9262e-05
71 | 0.00036479 | 9.1425e-05
72 | 0.00022691 | 5.6869e-05
73 | 0.0012152 | 0.00030455
74 | 0.00032446 | 8.1317e-05
75 | 0.00037336 | 9.3574e-05
76 | 0.00038856 | 9.7383e-05
77 | 0.00017102 | 4.2862e-05
78 | 0.00035037 | 8.7812e-05
79 | 0.00035387 | 8.8687e-05
80 | 0.00066089 | 0.00016563
81 | 0.0085911 | 0.0021531
82 | 0.0023952 | 0.0006003
83 | 0.0065849 | 0.0016503
84 | 0.0033741 | 0.00084564
85 | 0.0037372 | 0.00093664
86 | 0.0011223 | 0.00028129
87 | 0.0032647 | 0.00081822
88 | 0.0077608 | 0.001945
89 | 0.0076401 | 0.0019148
90 | 0.0081673 | 0.0020469
91 | 0.0048385 | 0.0012127
92 | 0.0027526 | 0.00068987
93 | 0.0012203 | 0.00030584
94 | 0.0007503 | 0.00018804
95 | 0.0019432 | 0.00048701
96 | 0.0055564 | 0.0013926
97 | 0.0071067 | 0.0017811
98 | 0.0012083 | 0.00030283
99 | 0.0031095 | 0.00077931
100 | 0.0026698 | 0.00066911

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1