## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1407-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1407-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1407-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1407-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1407-5_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1407-5_0_4_node_231 | 0.4 | n |  | TRUE
6 | bus_LV_1407-5_0_4_node_259 | 0.4 | n |  | TRUE
7 | bus_LV_1407-5_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1407-5_0_4_node_260 | 0.4 | n |  | TRUE
9 | bus_LV_1407-5_0_4_node_182 | 0.4 | n |  | TRUE
10 | bus_LV_1407-5_0_4_node_232 | 0.4 | n |  | TRUE
11 | bus_LV_1407-5_0_4_node_230 | 0.4 | n |  | TRUE
12 | bus_LV_1407-5_0_4_node_258 | 0.4 | n |  | TRUE
13 | bus_LV_1407-5_0_4_node_180 | 0.4 | n |  | TRUE
14 | bus_LV_1407-5_0_4_node_181 | 0.4 | n |  | TRUE
15 | bus_LV_1407-5_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1407-5_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1407-5_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1407-5_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1407-5_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1407-5_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1407-5_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1407-5_0_4_node_190 | 0.4 | n |  | TRUE
23 | bus_LV_1407-5_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1407-5_0_4_node_252 | 0.4 | n |  | TRUE
25 | bus_LV_1407-5_0_4_node_254 | 0.4 | n |  | TRUE
26 | bus_LV_1407-5_0_4_node_272 | 0.4 | n |  | TRUE
27 | bus_LV_1407-5_0_4_node_249 | 0.4 | n |  | TRUE
28 | bus_LV_1407-5_0_4_node_255 | 0.4 | n |  | TRUE
29 | bus_LV_1407-5_0_4_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_1407-5_0_4_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_1407-5_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_1407-5_0_4_node_265 | 0.4 | n |  | TRUE
33 | bus_LV_1407-5_0_4_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_1407-5_0_4_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_1407-5_0_4_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1407-5_0_4_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_1407-5_0_4_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1407-5_0_4_node_58 | 0.4 | n |  | TRUE
39 | bus_LV_1407-5_0_4_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1407-5_0_4_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_1407-5_0_4_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_1407-5_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_1407-5_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1407-5_0_4_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_1407-5_0_4_node_24 | 0.4 | n |  | TRUE
46 | bus_LV_1407-5_0_4_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_1407-5_0_4_node_21 | 0.4 | n |  | TRUE
48 | bus_LV_1407-5_0_4_node_194 | 0.4 | n |  | TRUE
49 | bus_LV_1407-5_0_4_node_203 | 0.4 | n |  | TRUE
50 | bus_LV_1407-5_0_4_node_191 | 0.4 | n |  | TRUE
51 | bus_LV_1407-5_0_4_node_189 | 0.4 | n |  | TRUE
52 | bus_LV_1407-5_0_4_node_19 | 0.4 | n |  | TRUE
53 | bus_LV_1407-5_0_4_node_193 | 0.4 | n |  | TRUE
54 | bus_LV_1407-5_0_4_node_201 | 0.4 | n |  | TRUE
55 | bus_LV_1407-5_0_4_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_1407-5_0_4_node_199 | 0.4 | n |  | TRUE
57 | bus_LV_1407-5_0_4_node_198 | 0.4 | n |  | TRUE
58 | bus_LV_1407-5_0_4_node_130 | 0.4 | n |  | TRUE
59 | bus_LV_1407-5_0_4_node_129 | 0.4 | n |  | TRUE
60 | bus_LV_1407-5_0_4_node_132 | 0.4 | n |  | TRUE
61 | bus_LV_1407-5_0_4_node_131 | 0.4 | n |  | TRUE
62 | bus_LV_1407-5_0_4_node_218 | 0.4 | n |  | TRUE
63 | bus_LV_1407-5_0_4_node_133 | 0.4 | n |  | TRUE
64 | bus_LV_1407-5_0_4_node_135 | 0.4 | n |  | TRUE
65 | bus_LV_1407-5_0_4_node_134 | 0.4 | n |  | TRUE
66 | bus_LV_1407-5_0_4_node_216 | 0.4 | n |  | TRUE
67 | bus_LV_1407-5_0_4_node_214 | 0.4 | n |  | TRUE
68 | bus_LV_1407-5_0_4_node_161 | 0.4 | n |  | TRUE
69 | bus_LV_1407-5_0_4_node_162 | 0.4 | n |  | TRUE
70 | bus_LV_1407-5_0_4_node_163 | 0.4 | n |  | TRUE
71 | bus_LV_1407-5_0_4_node_164 | 0.4 | n |  | TRUE
72 | bus_LV_1407-5_0_4_node_165 | 0.4 | n |  | TRUE
73 | bus_LV_1407-5_0_4_node_173 | 0.4 | n |  | TRUE
74 | bus_LV_1407-5_0_4_node_170 | 0.4 | n |  | TRUE
75 | bus_LV_1407-5_0_4_node_166 | 0.4 | n |  | TRUE
76 | bus_LV_1407-5_0_4_node_169 | 0.4 | n |  | TRUE
77 | bus_LV_1407-5_0_4_node_167 | 0.4 | n |  | TRUE
78 | bus_LV_1407-5_0_4_node_168 | 0.4 | n |  | TRUE
79 | bus_LV_1407-5_0_4_node_174 | 0.4 | n |  | TRUE
80 | bus_LV_1407-5_0_4_node_171 | 0.4 | n |  | TRUE
81 | bus_LV_1407-5_0_4_node_172 | 0.4 | n |  | TRUE
82 | bus_LV_1407-5_0_4_node_206 | 0.4 | n |  | TRUE
83 | bus_LV_1407-5_0_4_node_179 | 0.4 | n |  | TRUE
84 | bus_LV_1407-5_0_4_node_178 | 0.4 | n |  | TRUE
85 | bus_LV_1407-5_0_4_node_175 | 0.4 | n |  | TRUE
86 | bus_LV_1407-5_0_4_node_176 | 0.4 | n |  | TRUE
87 | bus_LV_1407-5_0_4_node_177 | 0.4 | n |  | TRUE
88 | bus_LV_1407-5_0_4_node_270 | 0.4 | n |  | TRUE
89 | bus_LV_1407-5_0_4_node_205 | 0.4 | n |  | TRUE
90 | bus_LV_1407-5_0_4_node_183 | 0.4 | n |  | TRUE
91 | bus_LV_1407-5_0_4_node_184 | 0.4 | n |  | TRUE
92 | bus_LV_1407-5_0_4_node_185 | 0.4 | n |  | TRUE
93 | bus_LV_1407-5_0_4_node_186 | 0.4 | n |  | TRUE
94 | bus_LV_1407-5_0_4_node_187 | 0.4 | n |  | TRUE
95 | bus_LV_1407-5_0_4_node_188 | 0.4 | n |  | TRUE
96 | bus_LV_1407-5_0_4_node_192 | 0.4 | n |  | TRUE
97 | bus_LV_1407-5_0_4_node_195 | 0.4 | n |  | TRUE
98 | bus_LV_1407-5_0_4_node_196 | 0.4 | n |  | TRUE
99 | bus_LV_1407-5_0_4_node_197 | 0.4 | n |  | TRUE
100 | bus_LV_1407-5_0_4_node_204 | 0.4 | n |  | TRUE
101 | bus_LV_1407-5_0_4_node_202 | 0.4 | n |  | TRUE
102 | bus_LV_1407-5_0_4_node_200 | 0.4 | n |  | TRUE
103 | bus_LV_1407-5_0_4_node_207 | 0.4 | n |  | TRUE
104 | bus_LV_1407-5_0_4_node_208 | 0.4 | n |  | TRUE
105 | bus_LV_1407-5_0_4_node_209 | 0.4 | n |  | TRUE
106 | bus_LV_1407-5_0_4_node_210 | 0.4 | n |  | TRUE
107 | bus_LV_1407-5_0_4_node_211 | 0.4 | n |  | TRUE
108 | bus_LV_1407-5_0_4_node_212 | 0.4 | n |  | TRUE
109 | bus_LV_1407-5_0_4_node_213 | 0.4 | n |  | TRUE
110 | bus_LV_1407-5_0_4_node_215 | 0.4 | n |  | TRUE
111 | bus_LV_1407-5_0_4_node_221 | 0.4 | n |  | TRUE
112 | bus_LV_1407-5_0_4_node_217 | 0.4 | n |  | TRUE
113 | bus_LV_1407-5_0_4_node_227 | 0.4 | n |  | TRUE
114 | bus_LV_1407-5_0_4_node_222 | 0.4 | n |  | TRUE
115 | bus_LV_1407-5_0_4_node_219 | 0.4 | n |  | TRUE
116 | bus_LV_1407-5_0_4_node_225 | 0.4 | n |  | TRUE
117 | bus_LV_1407-5_0_4_node_220 | 0.4 | n |  | TRUE
118 | bus_LV_1407-5_0_4_node_262 | 0.4 | n |  | TRUE
119 | bus_LV_1407-5_0_4_node_223 | 0.4 | n |  | TRUE
120 | bus_LV_1407-5_0_4_node_224 | 0.4 | n |  | TRUE
121 | bus_LV_1407-5_0_4_node_226 | 0.4 | n |  | TRUE
122 | bus_LV_1407-5_0_4_node_229 | 0.4 | n |  | TRUE
123 | bus_LV_1407-5_0_4_node_228 | 0.4 | n |  | TRUE
124 | bus_LV_1407-5_0_4_node_233 | 0.4 | n |  | TRUE
125 | bus_LV_1407-5_0_4_node_234 | 0.4 | n |  | TRUE
126 | bus_LV_1407-5_0_4_node_235 | 0.4 | n |  | TRUE
127 | bus_LV_1407-5_0_4_node_236 | 0.4 | n |  | TRUE
128 | bus_LV_1407-5_0_4_node_237 | 0.4 | n |  | TRUE
129 | bus_LV_1407-5_0_4_node_238 | 0.4 | n |  | TRUE
130 | bus_LV_1407-5_0_4_node_239 | 0.4 | n |  | TRUE
131 | bus_LV_1407-5_0_4_node_240 | 0.4 | n |  | TRUE
132 | bus_LV_1407-5_0_4_node_241 | 0.4 | n |  | TRUE
133 | bus_LV_1407-5_0_4_node_242 | 0.4 | n |  | TRUE
134 | bus_LV_1407-5_0_4_node_243 | 0.4 | n |  | TRUE
135 | bus_LV_1407-5_0_4_node_244 | 0.4 | n |  | TRUE
136 | bus_LV_1407-5_0_4_node_245 | 0.4 | n |  | TRUE
137 | bus_LV_1407-5_0_4_node_246 | 0.4 | n |  | TRUE
138 | bus_LV_1407-5_0_4_node_247 | 0.4 | n |  | TRUE
139 | bus_LV_1407-5_0_4_node_257 | 0.4 | n |  | TRUE
140 | bus_LV_1407-5_0_4_node_256 | 0.4 | n |  | TRUE
141 | bus_LV_1407-5_0_4_node_248 | 0.4 | n |  | TRUE
142 | bus_LV_1407-5_0_4_node_250 | 0.4 | n |  | TRUE
143 | bus_LV_1407-5_0_4_node_251 | 0.4 | n |  | TRUE
144 | bus_LV_1407-5_0_4_node_253 | 0.4 | n |  | TRUE
145 | bus_LV_1407-5_0_4_node_261 | 0.4 | n |  | TRUE
146 | bus_MV_138_3_node_223 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1407-5_0_4_load_0 | 0 | 0.011953 | 0.0029957 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1407-5_0_4_load_1 | 1 | 0.0052078 | 0.0013052 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1407-5_0_4_load_4 | 4 | 0.0095952 | 0.0024048 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1407-5_0_4_load_260 | 8 | 0.0039878 | 0.00099945 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1407-5_0_4_load_232 | 10 | 0.0036209 | 0.00090749 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1407-5_0_4_load_230 | 11 | 0.0049707 | 0.0012458 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1407-5_0_4_load_258 | 12 | 0.0022827 | 0.00057209 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1407-5_0_4_load_180 | 13 | 0.0055473 | 0.0013903 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1407-5_0_4_load_181 | 14 | 0.0028981 | 0.00072633 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1407-5_0_4_load_6 | 15 | 0.00032462 | 8.1358e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1407-5_0_4_load_7 | 16 | 0.00040014 | 0.00010029 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1407-5_0_4_load_8 | 17 | 0.00032963 | 8.2613e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1407-5_0_4_load_9 | 18 | 0.00098212 | 0.00024614 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1407-5_0_4_load_10 | 19 | 0.0014264 | 0.0003575 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1407-5_0_4_load_190 | 22 | 0.00079914 | 0.00020028 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1407-5_0_4_load_254 | 25 | 0.0015994 | 0.00040086 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1407-5_0_4_load_272 | 26 | 0.021039 | 0.0052728 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1407-5_0_4_load_13 | 29 | 0.00017938 | 4.4956e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1407-5_0_4_load_14 | 30 | 0.00042188 | 0.00010573 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1407-5_0_4_load_265 | 32 | 0.0003377 | 8.4635e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1407-5_0_4_load_17 | 34 | 0.00050473 | 0.0001265 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1407-5_0_4_load_34 | 35 | 0.00016312 | 4.0881e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1407-5_0_4_load_36 | 36 | 0.00057353 | 0.00014374 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1407-5_0_4_load_33 | 37 | 0.00026579 | 6.6613e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1407-5_0_4_load_58 | 38 | 0.00010301 | 2.5817e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1407-5_0_4_load_37 | 39 | 0.00023323 | 5.8453e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1407-5_0_4_load_22 | 40 | 0.00019224 | 4.818e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1407-5_0_4_load_23 | 41 | 0.0013783 | 0.00034544 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1407-5_0_4_load_26 | 42 | 0.00094903 | 0.00023785 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1407-5_0_4_load_24 | 45 | 0.0010776 | 0.00027007 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1407-5_0_4_load_25 | 46 | 0.00018744 | 4.6976e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1407-5_0_4_load_203 | 49 | 0.0012274 | 0.00030762 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1407-5_0_4_load_191 | 50 | 0.00024871 | 6.2331e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1407-5_0_4_load_189 | 51 | 0.00050862 | 0.00012747 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1407-5_0_4_load_19 | 52 | 0.0011465 | 0.00028734 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1407-5_0_4_load_193 | 53 | 0.001411 | 0.00035362 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1407-5_0_4_load_201 | 54 | 0.00091711 | 0.00022985 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1407-5_0_4_load_27 | 55 | 0.00059631 | 0.00014945 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1407-5_0_4_load_198 | 57 | 0.00016258 | 4.0746e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1407-5_0_4_load_130 | 58 | 0.00053151 | 0.00013321 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1407-5_0_4_load_129 | 59 | 0.00063647 | 0.00015952 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1407-5_0_4_load_132 | 60 | 0.0010775 | 0.00027004 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1407-5_0_4_load_131 | 61 | 0.00044376 | 0.00011122 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1407-5_0_4_load_218 | 62 | 0.00086867 | 0.00021771 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1407-5_0_4_load_134 | 65 | 0.0012688 | 0.00031798 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1407-5_0_4_load_216 | 66 | 0.00030002 | 7.5192e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1407-5_0_4_load_161 | 68 | 0.0012003 | 0.00030082 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1407-5_0_4_load_163 | 70 | 0.003219 | 0.00080676 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1407-5_0_4_load_165 | 72 | 0.001377 | 0.00034511 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1407-5_0_4_load_173 | 73 | 0.0012843 | 0.00032187 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1407-5_0_4_load_170 | 74 | 0.00079715 | 0.00019978 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1407-5_0_4_load_166 | 75 | 0.0011144 | 0.00027929 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1407-5_0_4_load_169 | 76 | 0.00094395 | 0.00023658 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1407-5_0_4_load_167 | 77 | 0.00071749 | 0.00017982 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1407-5_0_4_load_168 | 78 | 0.0012569 | 0.00031502 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1407-5_0_4_load_174 | 79 | 0.00034222 | 8.5769e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1407-5_0_4_load_171 | 80 | 0.0018034 | 0.00045198 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1407-5_0_4_load_206 | 82 | 0.00071598 | 0.00017944 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1407-5_0_4_load_178 | 84 | 0.0011167 | 0.00027988 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1407-5_0_4_load_175 | 85 | 0.0010251 | 0.00025691 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1407-5_0_4_load_176 | 86 | 0.00091748 | 0.00022994 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1407-5_0_4_load_177 | 87 | 0.0013932 | 0.00034918 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1407-5_0_4_load_270 | 88 | 0.0044172 | 0.001107 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1407-5_0_4_load_183 | 90 | 0.00038526 | 9.6555e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1407-5_0_4_load_184 | 91 | 0.00043429 | 0.00010884 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1407-5_0_4_load_185 | 92 | 0.00033363 | 8.3615e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1407-5_0_4_load_186 | 93 | 0.00027237 | 6.8262e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1407-5_0_4_load_187 | 94 | 0.00014527 | 3.6407e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1407-5_0_4_load_188 | 95 | 0.00032925 | 8.2518e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1407-5_0_4_load_192 | 96 | 0.00030383 | 7.6148e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1407-5_0_4_load_195 | 97 | 0.0031187 | 0.00078161 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1407-5_0_4_load_196 | 98 | 0.0013019 | 0.00032629 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1407-5_0_4_load_202 | 101 | 0.0019859 | 0.00049771 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1407-5_0_4_load_200 | 102 | 0.0018426 | 0.0004618 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1407-5_0_4_load_207 | 103 | 0.00083066 | 0.00020818 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1407-5_0_4_load_208 | 104 | 0.00030792 | 7.7173e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1407-5_0_4_load_209 | 105 | 0.014489 | 0.0036313 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1407-5_0_4_load_210 | 106 | 0.0010911 | 0.00027345 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1407-5_0_4_load_211 | 107 | 0.00042515 | 0.00010655 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1407-5_0_4_load_215 | 110 | 0.0094773 | 0.0023752 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1407-5_0_4_load_221 | 111 | 0.00082102 | 0.00020577 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1407-5_0_4_load_217 | 112 | 0.0018319 | 0.00045912 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1407-5_0_4_load_227 | 113 | 0.0065634 | 0.0016449 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1407-5_0_4_load_222 | 114 | 0.00048672 | 0.00012198 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1407-5_0_4_load_225 | 116 | 0.0041415 | 0.0010379 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1407-5_0_4_load_220 | 117 | 0.001606 | 0.00040249 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1407-5_0_4_load_262 | 118 | 0.0001513 | 3.7919e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1407-5_0_4_load_223 | 119 | 0.0063882 | 0.001601 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1407-5_0_4_load_224 | 120 | 0.0035673 | 0.00089404 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1407-5_0_4_load_226 | 121 | 0.0020829 | 0.00052201 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1407-5_0_4_load_229 | 122 | 0.0037585 | 0.00094197 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1407-5_0_4_load_228 | 123 | 0.0035935 | 0.00090062 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1407-5_0_4_load_233 | 124 | 0.0021993 | 0.00055119 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1407-5_0_4_load_234 | 125 | 0.0033686 | 0.00084425 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1407-5_0_4_load_235 | 126 | 0.0043435 | 0.0010886 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1407-5_0_4_load_236 | 127 | 0.0026262 | 0.00065818 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1407-5_0_4_load_237 | 128 | 0.0034857 | 0.00087361 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1407-5_0_4_load_238 | 129 | 0.0083971 | 0.0021045 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1407-5_0_4_load_239 | 130 | 0.0034857 | 0.00087361 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1407-5_0_4_load_240 | 131 | 0.0064028 | 0.0016047 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1407-5_0_4_load_241 | 132 | 0.0011067 | 0.00027737 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1407-5_0_4_load_242 | 133 | 0.0030806 | 0.00077208 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1407-5_0_4_load_243 | 134 | 0.0023946 | 0.00060014 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1407-5_0_4_load_244 | 135 | 0.0043046 | 0.0010788 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1407-5_0_4_load_245 | 136 | 0.0010167 | 0.00025482 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1407-5_0_4_load_247 | 138 | 0.0031737 | 0.0007954 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1407-5_0_4_load_257 | 139 | 0.0034393 | 0.00086198 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1407-5_0_4_load_248 | 141 | 0.0011742 | 0.00029428 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1407-5_0_4_load_250 | 142 | 0.0029782 | 0.00074641 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1407-5_0_4_load_251 | 143 | 0.0021134 | 0.00052966 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1407-5_0_4_load_253 | 144 | 0.003764 | 0.00094334 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1407-5_0_4_load_261 | 145 | 0.0052163 | 0.0013073 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 25 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1407-5_0_4_line_0 |  | 0 | 1 | 0.025832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1407-5_0_4_line_1 |  | 0 | 2 | 0.0024527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1407-5_0_4_line_2 |  | 1 | 3 | 0.0064032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1407-5_0_4_line_3 |  | 2 | 4 | 0.061579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1407-5_0_4_line_4 |  | 3 | 5 | 0.044186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1407-5_0_4_line_5 |  | 4 | 6 | 0.018809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1407-5_0_4_line_6 |  | 5 | 10 | 0.010807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1407-5_0_4_line_7 |  | 5 | 11 | 0.019592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1407-5_0_4_line_8 |  | 6 | 8 | 0.031605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1407-5_0_4_line_9 |  | 6 | 12 | 0.043382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1407-5_0_4_line_10 |  | 7 | 8 | 0.045526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1407-5_0_4_line_11 |  | 7 | 9 | 0.28516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1407-5_0_4_line_12 |  | 9 | 13 | 0.012489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1407-5_0_4_line_13 |  | 10 | 124 | 0.020936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1407-5_0_4_line_14 |  | 10 | 123 | 0.049184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1407-5_0_4_line_15 |  | 12 | 140 | 0.0013727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1407-5_0_4_line_16 |  | 13 | 14 | 0.095429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1407-5_0_4_line_17 |  | 15 | 16 | 0.020877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1407-5_0_4_line_18 |  | 15 | 17 | 0.023679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1407-5_0_4_line_19 |  | 16 | 18 | 0.024953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1407-5_0_4_line_20 |  | 17 | 19 | 0.035236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1407-5_0_4_line_21 |  | 18 | 20 | 0.056515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1407-5_0_4_line_22 |  | 19 | 21 | 0.021309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1407-5_0_4_line_23 |  | 20 | 22 | 0.032161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1407-5_0_4_line_24 |  | 21 | 23 | 0.072337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_1407-5_0_4_line_25 |  | 22 | 50 | 0.009953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_1407-5_0_4_line_26 |  | 22 | 51 | 0.046334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1407-5_0_4_line_27 |  | 23 | 24 | 0.027297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1407-5_0_4_line_28 |  | 23 | 25 | 0.035642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1407-5_0_4_line_29 |  | 24 | 26 | 0.052186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1407-5_0_4_line_30 |  | 24 | 27 | 0.032094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1407-5_0_4_line_31 |  | 25 | 28 | 0.042552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_1407-5_0_4_line_32 |  | 27 | 143 | 0.0023664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1407-5_0_4_line_33 |  | 27 | 141 | 0.010967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1407-5_0_4_line_34 |  | 28 | 140 | 0.040145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_1407-5_0_4_line_35 |  | 28 | 137 | 0.014211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1407-5_0_4_line_36 |  | 29 | 30 | 0.17375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1407-5_0_4_line_37 |  | 29 | 31 | 0.013257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1407-5_0_4_line_38 |  | 29 | 32 | 0.15172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1407-5_0_4_line_39 |  | 30 | 33 | 0.0089159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_1407-5_0_4_line_40 |  | 31 | 34 | 0.097602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1407-5_0_4_line_41 |  | 32 | 39 | 0.061894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1407-5_0_4_line_42 |  | 33 | 40 | 0.030153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_1407-5_0_4_line_43 |  | 33 | 41 | 0.073982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1407-5_0_4_line_44 |  | 34 | 42 | 0.061308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_1407-5_0_4_line_45 |  | 35 | 36 | 0.0092377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1407-5_0_4_line_46 |  | 35 | 37 | 0.034269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1407-5_0_4_line_47 |  | 36 | 38 | 0.014196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1407-5_0_4_line_48 |  | 37 | 43 | 0.049738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1407-5_0_4_line_49 |  | 39 | 43 | 0.063148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1407-5_0_4_line_50 |  | 40 | 44 | 0.027357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_1407-5_0_4_line_51 |  | 41 | 45 | 0.050382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1407-5_0_4_line_52 |  | 42 | 46 | 0.0035464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_1407-5_0_4_line_53 |  | 44 | 47 | 0.077899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_1407-5_0_4_line_54 |  | 44 | 52 | 0.042622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1407-5_0_4_line_55 |  | 46 | 55 | 0.042766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_1407-5_0_4_line_56 |  | 47 | 48 | 0.019247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_1407-5_0_4_line_57 |  | 47 | 49 | 0.12344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1407-5_0_4_line_58 |  | 48 | 53 | 0.030814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_1407-5_0_4_line_59 |  | 49 | 54 | 0.018879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1407-5_0_4_line_60 |  | 50 | 96 | 0.012467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_1407-5_0_4_line_61 |  | 51 | 95 | 0.015657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1407-5_0_4_line_62 |  | 53 | 96 | 0.018896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_1407-5_0_4_line_63 |  | 54 | 102 | 0.01133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1407-5_0_4_line_64 |  | 55 | 56 | 0.30936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_1407-5_0_4_line_65 |  | 56 | 57 | 0.13316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1407-5_0_4_line_66 |  | 57 | 83 | 0.21719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1407-5_0_4_line_67 |  | 58 | 59 | 0.080635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1407-5_0_4_line_68 |  | 59 | 62 | 0.14051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1407-5_0_4_line_69 |  | 60 | 61 | 0.037672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1407-5_0_4_line_70 |  | 61 | 63 | 0.17828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1407-5_0_4_line_71 |  | 62 | 64 | 0.075904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1407-5_0_4_line_72 |  | 63 | 65 | 0.035846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1407-5_0_4_line_73 |  | 63 | 64 | 0.095681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1407-5_0_4_line_74 |  | 64 | 66 | 0.05116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1407-5_0_4_line_75 |  | 66 | 67 | 0.10831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1407-5_0_4_line_76 |  | 67 | 112 | 0.11991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1407-5_0_4_line_77 |  | 67 | 108 | 0.043182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1407-5_0_4_line_78 |  | 68 | 69 | 0.013264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1407-5_0_4_line_79 |  | 68 | 70 | 0.014215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1407-5_0_4_line_80 |  | 69 | 71 | 0.007201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1407-5_0_4_line_81 |  | 69 | 72 | 0.036607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1407-5_0_4_line_82 |  | 71 | 73 | 0.017921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1407-5_0_4_line_83 |  | 71 | 74 | 0.0040037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1407-5_0_4_line_84 |  | 72 | 75 | 0.064735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1407-5_0_4_line_85 |  | 74 | 76 | 0.016488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1407-5_0_4_line_86 |  | 75 | 77 | 0.0080914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1407-5_0_4_line_87 |  | 76 | 80 | 0.04778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1407-5_0_4_line_88 |  | 77 | 78 | 0.032882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1407-5_0_4_line_89 |  | 78 | 79 | 0.010146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1407-5_0_4_line_90 |  | 80 | 81 | 0.092428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1407-5_0_4_line_91 |  | 81 | 82 | 0.078367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1407-5_0_4_line_92 |  | 81 | 83 | 0.16215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1407-5_0_4_line_93 |  | 83 | 84 | 0.17364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1407-5_0_4_line_94 |  | 84 | 86 | 0.097463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1407-5_0_4_line_95 |  | 85 | 86 | 0.0324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1407-5_0_4_line_96 |  | 85 | 87 | 0.0028183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1407-5_0_4_line_97 |  | 88 | 89 | 0.055702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1407-5_0_4_line_98 |  | 89 | 100 | 0.15415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1407-5_0_4_line_99 |  | 90 | 91 | 0.036688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1407-5_0_4_line_100 |  | 90 | 92 | 0.0021977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1407-5_0_4_line_101 |  | 91 | 93 | 0.0262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1407-5_0_4_line_102 |  | 93 | 94 | 0.0044122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1407-5_0_4_line_103 |  | 94 | 95 | 0.0023536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1407-5_0_4_line_104 |  | 97 | 98 | 0.019013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1407-5_0_4_line_105 |  | 98 | 99 | 0.034717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1407-5_0_4_line_106 |  | 99 | 100 | 0.014175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1407-5_0_4_line_107 |  | 100 | 101 | 0.036347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1407-5_0_4_line_108 |  | 101 | 102 | 0.037092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1407-5_0_4_line_109 |  | 103 | 104 | 0.024161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1407-5_0_4_line_110 |  | 103 | 105 | 0.076805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1407-5_0_4_line_111 |  | 104 | 106 | 0.027462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1407-5_0_4_line_112 |  | 106 | 107 | 0.019917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1407-5_0_4_line_113 |  | 107 | 108 | 0.047927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1407-5_0_4_line_114 |  | 108 | 109 | 0.11684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1407-5_0_4_line_115 |  | 108 | 110 | 0.077397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1407-5_0_4_line_116 |  | 109 | 111 | 0.050422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1407-5_0_4_line_117 |  | 110 | 113 | 0.023958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1407-5_0_4_line_118 |  | 111 | 114 | 0.001266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1407-5_0_4_line_119 |  | 112 | 115 | 0.011327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1407-5_0_4_line_120 |  | 113 | 116 | 0.022315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1407-5_0_4_line_121 |  | 115 | 117 | 0.079546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1407-5_0_4_line_122 |  | 115 | 118 | 0.16187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1407-5_0_4_line_123 |  | 116 | 119 | 0.010208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1407-5_0_4_line_124 |  | 119 | 120 | 0.0092753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1407-5_0_4_line_125 |  | 120 | 121 | 0.018006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1407-5_0_4_line_126 |  | 121 | 122 | 0.0232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
127 | LV_1407-5_0_4_line_127 |  | 122 | 123 | 0.0045613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
128 | LV_1407-5_0_4_line_128 |  | 124 | 125 | 0.023414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1407-5_0_4_line_129 |  | 125 | 126 | 0.022321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1407-5_0_4_line_130 |  | 126 | 127 | 0.01392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1407-5_0_4_line_131 |  | 127 | 128 | 0.021958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1407-5_0_4_line_132 |  | 128 | 129 | 0.0048992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1407-5_0_4_line_133 |  | 129 | 130 | 0.0040938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1407-5_0_4_line_134 |  | 130 | 131 | 0.01341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1407-5_0_4_line_135 |  | 132 | 133 | 0.042609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1407-5_0_4_line_136 |  | 132 | 134 | 0.023404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1407-5_0_4_line_137 |  | 133 | 135 | 0.024011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1407-5_0_4_line_138 |  | 134 | 136 | 0.032054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1407-5_0_4_line_139 |  | 135 | 137 | 0.0046108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1407-5_0_4_line_140 |  | 136 | 138 | 0.007928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1407-5_0_4_line_141 |  | 137 | 139 | 0.019308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1407-5_0_4_line_142 |  | 140 | 145 | 0.029493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1407-5_0_4_line_143 |  | 141 | 142 | 0.011818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1407-5_0_4_line_144 |  | 143 | 144 | 0.018028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1407-5_0_4_trafo_254 | 0.63 MVA 20/0.4 kV | 146 | 25 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2658584.486 | 1192984.8445 | 2658608.8379 | 1192993.4615
1 | 2658582.1738 | 1192984.0263 | 2658584.486 | 1192984.8445
2 | 2658614.8743 | 1192995.5975 | 2658608.8379 | 1192993.4615
3 | 2658582.1738 | 1192984.0263 | 2658524.816 | 1192961.6208
4 | 2658614.8743 | 1192995.5975 | 2658612.3566 | 1193002.8436 | 2658608.2876 | 1193007.3842 | 2658600.077 | 1193017.643 | 2658592.5689 | 1193033.234
5 | 2658507.2966 | 1192954.7773 | 2658524.816 | 1192961.6208
6 | 2658592.5689 | 1193033.234 | 2658589.8589 | 1193033.6522 | 2658582.286 | 1193030.8773
7 | 2658592.5689 | 1193033.234 | 2658607.0822 | 1193046.3948
8 | 2658507.2966 | 1192954.7773 | 2658512.4077 | 1192940.3189 | 2658517.2052 | 1192926.7581 | 2658517.8734 | 1192924.9946
9 | 2658507.2966 | 1192954.7773 | 2658466.8879 | 1192938.9934
10 | 2658516.4551 | 1192883.437 | 2658517.2135 | 1192886.9464 | 2658518.4601 | 1192892.7508 | 2658519.1455 | 1192895.9371 | 2658525.0749 | 1192902.2543 | 2658525.1626 | 1192905.7571 | 2658517.8734 | 1192924.9946
11 | 2658516.4551 | 1192883.437 | 2658706.4491 | 1192670.7864
12 | 2658706.4491 | 1192670.7864 | 2658704.5028 | 1192667.9323 | 2658703.3482 | 1192658.9714
13 | 2658582.286 | 1193030.8773 | 2658562.6284 | 1193023.6744
14 | 2658582.286 | 1193030.8773 | 2658569.6802 | 1193078.4189
15 | 2658465.6092 | 1192938.494 | 2658466.8879 | 1192938.9934
16 | 2658715.662 | 1192573.2097 | 2658724.838 | 1192585.0398 | 2658729.0401 | 1192599.6005 | 2658727.3609 | 1192612.2468 | 2658716.2905 | 1192634.9957 | 2658703.3482 | 1192658.9714
17 | 2658213.099 | 1192840.1254 | 2658193.6308 | 1192832.5853
18 | 2658213.099 | 1192840.1254 | 2658235.1794 | 1192848.6773
19 | 2658170.3616 | 1192823.573 | 2658193.6308 | 1192832.5853
20 | 2658268.0373 | 1192861.4033 | 2658235.1794 | 1192848.6773
21 | 2658117.6611 | 1192803.1618 | 2658170.3616 | 1192823.573
22 | 2658287.9075 | 1192869.0992 | 2658268.0373 | 1192861.4033
23 | 2658125.2404 | 1192834.2865 | 2658123.0314 | 1192819.2231 | 2658117.6611 | 1192803.1618
24 | 2658287.9075 | 1192869.0992 | 2658337.0982 | 1192888.3115 | 2658337.6675 | 1192888.5506 | 2658347.9695 | 1192892.8201 | 2658355.136 | 1192895.7916
25 | 2658125.2404 | 1192834.2865 | 2658116.0298 | 1192830.5147
26 | 2658125.2404 | 1192834.2865 | 2658123.0037 | 1192850.3184 | 2658122.0368 | 1192857.2686 | 2658108.5611 | 1192876.0668
27 | 2658355.136 | 1192895.7916 | 2658330.9251 | 1192908.5296
28 | 2658355.136 | 1192895.7916 | 2658388.4037 | 1192908.5824
29 | 2658330.9251 | 1192908.5296 | 2658315.3969 | 1192917.2834 | 2658299.7393 | 1192947.9262
30 | 2658330.9251 | 1192908.5296 | 2658329.1431 | 1192916.9616 | 2658329.8972 | 1192919.3592 | 2658349.3403 | 1192927.331
31 | 2658428.1207 | 1192923.8529 | 2658388.4037 | 1192908.5824
32 | 2658349.3403 | 1192927.331 | 2658351.5623 | 1192928.1448
33 | 2658349.3403 | 1192927.331 | 2658345.593 | 1192937.6383
34 | 2658428.1207 | 1192923.8529 | 2658465.6092 | 1192938.494
35 | 2658428.1207 | 1192923.8529 | 2658422.3609 | 1192936.8486
36 | 2657921.2473 | 1192767.0222 | 2657889.2052 | 1192758.4783 | 2657836.1741 | 1192731.7839 | 2657768.7354 | 1192686.5279
37 | 2657757.7276 | 1192679.1409 | 2657768.7354 | 1192686.5279
38 | 2657768.7354 | 1192686.5279 | 2657679.3487 | 1192809.1151
39 | 2657929.9774 | 1192768.8009 | 2657923.7301 | 1192767.6842 | 2657921.2473 | 1192767.0222
40 | 2657757.7276 | 1192679.1409 | 2657759.8835 | 1192672.1688 | 2657757.0542 | 1192659.6677 | 2657731.4445 | 1192618.3304 | 2657724.6997 | 1192605.5469 | 2657723.0697 | 1192596.7262 | 2657724.6868 | 1192591.5367
41 | 2657679.3487 | 1192809.1151 | 2657660.8217 | 1192805.6124 | 2657626.5466 | 1192806.0715 | 2657618.0559 | 1192808.2284
42 | 2657929.9774 | 1192768.8009 | 2657956.8764 | 1192773.6195 | 2657959.685 | 1192773.9288
43 | 2657929.9774 | 1192768.8009 | 2657929.9462 | 1192759.4285 | 2657927.1461 | 1192753.398 | 2657909.8895 | 1192733.6197 | 2657907.8669 | 1192729.1643 | 2657907.1185 | 1192724.5766 | 2657916.354 | 1192704.4211
44 | 2657724.6868 | 1192591.5367 | 2657726.8691 | 1192584.5336 | 2657737.595 | 1192566.2933 | 2657744.7654 | 1192560.2479 | 2657756.0797 | 1192557.6667 | 2657767.694 | 1192559.9076
45 | 2657643.2765 | 1192902.5709 | 2657651.7638 | 1192906.2181
46 | 2657620.1818 | 1192878.8963 | 2657623.8644 | 1192886.7029 | 2657634.7156 | 1192898.8921 | 2657643.2765 | 1192902.5709
47 | 2657657.9332 | 1192916.3034 | 2657657.9463 | 1192914.9472 | 2657658.0046 | 1192908.8999 | 2657651.7638 | 1192906.2181
48 | 2657578.6673 | 1192852.2706 | 2657595.4716 | 1192866.8517 | 2657620.1818 | 1192878.8963 | 2657620.1818 | 1192878.8963
49 | 2657578.6673 | 1192852.2706 | 2657585.8942 | 1192843.4795 | 2657590.9593 | 1192828.0305 | 2657595.1649 | 1192819.5328 | 2657602.6813 | 1192813.1236 | 2657612.7161 | 1192809.5848 | 2657618.0559 | 1192808.2284
50 | 2657986.8771 | 1192776.923 | 2657959.685 | 1192773.9288
51 | 2657956.1524 | 1192674.4447 | 2657935.7236 | 1192687.0542 | 2657919.4228 | 1192699.2367 | 2657916.354 | 1192704.4211
52 | 2657767.694 | 1192559.9076 | 2657771.1762 | 1192560.5795
53 | 2657986.8771 | 1192776.923 | 2658034.4855 | 1192781.0534 | 2658064.5554 | 1192785.0695
54 | 2657986.8771 | 1192776.923 | 2657985.5915 | 1192751.4849 | 2657986.0005 | 1192742.317 | 2657987.966 | 1192734.5888
55 | 2657805.9486 | 1192551.2999 | 2657800.1972 | 1192562.7398 | 2657794.7771 | 1192565.1333 | 2657771.1762 | 1192560.5795
56 | 2658060.6832 | 1192803.9205 | 2658064.5554 | 1192785.0695
57 | 2658064.5554 | 1192785.0695 | 2658067.6088 | 1192774.4152 | 2658146.7983 | 1192694.7109
58 | 2658060.6832 | 1192803.9205 | 2658086.7381 | 1192811.6443 | 2658089.6964 | 1192813.7626
59 | 2658146.7983 | 1192694.7109 | 2658160.1045 | 1192681.3183
60 | 2658116.0298 | 1192830.5147 | 2658109.1676 | 1192827.7045 | 2658105.0604 | 1192824.7637
61 | 2658097.8941 | 1192887.366 | 2658104.419 | 1192881.845 | 2658108.5611 | 1192876.0668
62 | 2658089.6964 | 1192813.7626 | 2658105.0604 | 1192824.7637
63 | 2658168.09 | 1192673.2808 | 2658160.1045 | 1192681.3183
64 | 2657805.9486 | 1192551.2999 | 2657802.8233 | 1192241.9596
65 | 2657802.8233 | 1192241.9596 | 2657899.2334 | 1192333.8047
66 | 2658087.9552 | 1192441.2998 | 2657899.2334 | 1192333.8047
67 | 2658125.0922 | 1193295.2142 | 2658130.1169 | 1193299.6894 | 2658175.2219 | 1193346.0541 | 2658183.8159 | 1193349.3971
68 | 2658240.6176 | 1193215.2372 | 2658125.0922 | 1193295.2142
69 | 2657978.1165 | 1193101.1311 | 2657955.192 | 1193101.7354 | 2657940.4699 | 1193101.0247
70 | 2658155.0269 | 1193113.6692 | 2658130.7439 | 1193106.507 | 2658089.78 | 1193102.0735 | 2658043.0669 | 1193099.4188 | 2657978.1165 | 1193101.1311
71 | 2658246.6733 | 1193142.032 | 2658238.725 | 1193157.5413 | 2658244.3646 | 1193187.3577 | 2658240.6176 | 1193215.2372
72 | 2658155.0269 | 1193113.6692 | 2658133.737 | 1193084.7903
73 | 2658246.6733 | 1193142.032 | 2658158.5839 | 1193114.7154 | 2658155.0269 | 1193113.6692
74 | 2658246.6733 | 1193142.032 | 2658295.8824 | 1193156.0246
75 | 2658402.4721 | 1193164.296 | 2658389.8169 | 1193164.5616 | 2658373.2657 | 1193161.0426 | 2658361.2621 | 1193160.9255 | 2658334.3845 | 1193164.2877 | 2658323.7312 | 1193164.0504 | 2658311.3274 | 1193160.4164 | 2658295.8824 | 1193156.0246
76 | 2658402.4721 | 1193164.296 | 2658440.8743 | 1193249.1083 | 2658454.2243 | 1193272.3565
77 | 2658402.4721 | 1193164.296 | 2658401.3697 | 1193153.8571 | 2658402.0755 | 1193143.2356 | 2658406.3526 | 1193130.6257 | 2658410.6873 | 1193123.0525
78 | 2658285.6428 | 1192305.7658 | 2658283.9938 | 1192301.3139 | 2658282.8016 | 1192299.2789 | 2658279.9194 | 1192297.7722 | 2658277.025 | 1192297.5157
79 | 2658262.8659 | 1192296.2609 | 2658277.025 | 1192297.5157
80 | 2658285.6428 | 1192305.7658 | 2658279.8606 | 1192310.0787
81 | 2658285.6428 | 1192305.7658 | 2658301.1439 | 1192306.9952 | 2658307.2872 | 1192306.3102 | 2658321.55 | 1192302.0833
82 | 2658279.8606 | 1192310.0787 | 2658286.5194 | 1192312.0335 | 2658297.0139 | 1192315.4265
83 | 2658279.8606 | 1192310.0787 | 2658276.0359 | 1192311.2625
84 | 2658385.3367 | 1192292.3259 | 2658337.4323 | 1192297.3765 | 2658321.55 | 1192302.0833
85 | 2658259.8531 | 1192313.895 | 2658270.2493 | 1192313.0535 | 2658276.0359 | 1192311.2625
86 | 2658385.3367 | 1192292.3259 | 2658393.3835 | 1192291.4776
87 | 2658259.8531 | 1192313.895 | 2658252.8396 | 1192314.4626 | 2658228.1205 | 1192311.0536 | 2658212.7831 | 1192307.3003
88 | 2658426.069 | 1192290.0886 | 2658416.9626 | 1192288.9916 | 2658393.3835 | 1192291.4776
89 | 2658426.069 | 1192290.0886 | 2658436.1423 | 1192291.302
90 | 2658122.8507 | 1192288.5178 | 2658126.9086 | 1192287.4788 | 2658132.837 | 1192287.7365 | 2658212.7831 | 1192307.3003
91 | 2658122.8507 | 1192288.5178 | 2658121.4229 | 1192280.1102 | 2658123.6558 | 1192260.5652 | 2658128.7548 | 1192241.0369 | 2658126.4587 | 1192224.7163 | 2658120.853 | 1192212.4327
92 | 2658087.9552 | 1192441.2998 | 2658088.2659 | 1192430.4967 | 2658091.6624 | 1192417.4888 | 2658117.0251 | 1192368.7293 | 2658121.193 | 1192354.7951 | 2658122.2136 | 1192346.2557 | 2658117.6157 | 1192320.4741 | 2658116.439 | 1192309.7677 | 2658118.0431 | 1192296.8759 | 2658119.7144 | 1192291.9782 | 2658122.8507 | 1192288.5178
93 | 2658087.9552 | 1192441.2998 | 2658110.7542 | 1192463.4115 | 2658145.1614 | 1192473.8849 | 2658194.1793 | 1192487.7246 | 2658223.215 | 1192488.5074 | 2658240.1607 | 1192482.2353 | 2658245.1595 | 1192476.1592
94 | 2658328.7959 | 1192427.8838 | 2658287.3525 | 1192454.2341 | 2658250.4592 | 1192469.7172 | 2658245.1595 | 1192476.1592
95 | 2658350.291 | 1192404.7006 | 2658341.1527 | 1192410.7109 | 2658331.8183 | 1192425.9621 | 2658328.7959 | 1192427.8838
96 | 2658352.6457 | 1192403.152 | 2658350.291 | 1192404.7006
97 | 2658363.0982 | 1192673.4085 | 2658376.3416 | 1192662.1868 | 2658394.7098 | 1192645.2562 | 2658401.5686 | 1192633.7054
98 | 2658219.8506 | 1192621.1839 | 2658224.7983 | 1192625.0453 | 2658229.719 | 1192623.0587 | 2658363.0982 | 1192673.4085
99 | 2658116.841 | 1192939.0102 | 2658107.4859 | 1192923.9433 | 2658093.0117 | 1192911.7077
100 | 2658118.0003 | 1192940.8773 | 2658116.841 | 1192939.0102
101 | 2658093.0117 | 1192911.7077 | 2658087.0504 | 1192906.6684 | 2658084.8653 | 1192901.6999 | 2658087.6491 | 1192896.0348 | 2658092.7292 | 1192891.7363
102 | 2658092.7292 | 1192891.7363 | 2658096.0974 | 1192888.8862
103 | 2658097.8941 | 1192887.366 | 2658096.0974 | 1192888.8862
104 | 2658162.917 | 1192584.1871 | 2658178.995 | 1192594.336
105 | 2658208.3525 | 1192612.8673 | 2658178.995 | 1192594.336
106 | 2658208.3525 | 1192612.8673 | 2658214.2448 | 1192616.7935 | 2658219.8506 | 1192621.1839
107 | 2658219.8506 | 1192621.1839 | 2658194.2329 | 1192646.968
108 | 2658168.09 | 1192673.2808 | 2658194.2329 | 1192646.968
109 | 2658311.456 | 1193072.3273 | 2658331.3514 | 1193086.0359
110 | 2658248.2106 | 1193028.7487 | 2658311.456 | 1193072.3273
111 | 2658331.3514 | 1193086.0359 | 2658341.2851 | 1193092.8807 | 2658353.9939 | 1193100.42 | 2658354.5404 | 1193100.7165
112 | 2658354.5404 | 1193100.7165 | 2658368.1798 | 1193108.1183 | 2658371.4279 | 1193111.0846
113 | 2658410.6873 | 1193123.0525 | 2658387.7832 | 1193127.7095 | 2658383.4984 | 1193127.0563 | 2658381.2569 | 1193125.5558 | 2658379.4948 | 1193123.3484 | 2658371.859 | 1193111.4783 | 2658371.4279 | 1193111.0846
114 | 2658410.6873 | 1193123.0525 | 2658508.7992 | 1193186.9362
115 | 2658410.6873 | 1193123.0525 | 2658435.9671 | 1193078.8517 | 2658440.194 | 1193074.5127 | 2658448.2271 | 1193069.8996 | 2658457.3987 | 1193068.1215 | 2658459.2134 | 1193068.1304
116 | 2658508.7992 | 1193186.9362 | 2658526.7127 | 1193181.297 | 2658556.2061 | 1193169.8375
117 | 2658483.1712 | 1193068.2479 | 2658459.2134 | 1193068.1304
118 | 2658557.3861 | 1193169.379 | 2658556.2061 | 1193169.8375
119 | 2658459.8651 | 1193282.1794 | 2658454.2243 | 1193272.3565
120 | 2658505.4858 | 1193068.3573 | 2658483.1712 | 1193068.2479
121 | 2658459.8651 | 1193282.1794 | 2658451.6684 | 1193280.1649 | 2658437.495 | 1193272.0218 | 2658411.9417 | 1193256.1077 | 2658398.9237 | 1193247.4869 | 2658391.2757 | 1193242.3538
122 | 2658459.8651 | 1193282.1794 | 2658465.9072 | 1193443.9408
123 | 2658515.6937 | 1193068.4074 | 2658505.4858 | 1193068.3573
124 | 2658515.6937 | 1193068.4074 | 2658516.742 | 1193068.4125 | 2658524.9353 | 1193069.1566
125 | 2658542.6654 | 1193072.0261 | 2658534.029 | 1193069.9824 | 2658524.9353 | 1193069.1566
126 | 2658565.2415 | 1193077.3685 | 2658542.6654 | 1193072.0261
127 | 2658569.6802 | 1193078.4189 | 2658565.2415 | 1193077.3685
128 | 2658562.6284 | 1193023.6744 | 2658557.3448 | 1193021.7383 | 2658548.3762 | 1193019.894 | 2658539.7606 | 1193019.386
129 | 2658539.7606 | 1193019.386 | 2658534.3594 | 1193019.0676 | 2658517.4514 | 1193018.8022
130 | 2658517.4514 | 1193018.8022 | 2658503.5335 | 1193018.5838
131 | 2658503.5335 | 1193018.5838 | 2658481.5781 | 1193018.2393
132 | 2658476.6795 | 1193018.1624 | 2658481.5781 | 1193018.2393
133 | 2658476.6795 | 1193018.1624 | 2658472.5862 | 1193018.0982
134 | 2658459.1777 | 1193017.8878 | 2658472.5862 | 1193018.0982
135 | 2658444.7449 | 1192995.4503 | 2658443.0425 | 1192991.2483 | 2658418.3448 | 1192965.6481 | 2658416.8969 | 1192963.6055
136 | 2658444.7449 | 1192995.4503 | 2658444.9553 | 1192995.9697 | 2658444.3637 | 1193001.9118 | 2658440.6637 | 1193006.923 | 2658435.9182 | 1193009.7227 | 2658430.7917 | 1193009.9811
137 | 2658416.8969 | 1192963.6055 | 2658416.0516 | 1192962.4128 | 2658414.8673 | 1192957.2316 | 2658415.853 | 1192951.5268 | 2658420.492 | 1192941.0637
138 | 2658430.7917 | 1193009.9811 | 2658428.5286 | 1193010.0952 | 2658399.2274 | 1193004.734
139 | 2658422.3609 | 1192936.8486 | 2658420.492 | 1192941.0637
140 | 2658391.4288 | 1193003.3071 | 2658399.2274 | 1193004.734
141 | 2658422.3609 | 1192936.8486 | 2658436.8632 | 1192949.6419
142 | 2658456.4553 | 1192966.5207 | 2658460.1119 | 1192956.5951 | 2658465.6092 | 1192938.494
143 | 2658341.5549 | 1192948.7452 | 2658345.593 | 1192937.6383
144 | 2658364.6476 | 1192938.8868 | 2658363.8619 | 1192935.8219 | 2658362.1471 | 1192933.4593 | 2658357.8849 | 1192930.4605 | 2658351.5623 | 1192928.1448

## bus_geodata
| x | y | coords
0 | 2658584.486 | 1192984.8445
1 | 2658608.8379 | 1192993.4615
2 | 2658582.1738 | 1192984.0263
3 | 2658614.8743 | 1192995.5975
4 | 2658524.816 | 1192961.6208
5 | 2658592.5689 | 1193033.234
6 | 2658507.2966 | 1192954.7773
7 | 2658516.4551 | 1192883.437
8 | 2658517.8734 | 1192924.9946
9 | 2658706.4491 | 1192670.7864
10 | 2658582.286 | 1193030.8773
11 | 2658607.0822 | 1193046.3948
12 | 2658466.8878 | 1192938.9934
13 | 2658703.3482 | 1192658.9714
14 | 2658715.662 | 1192573.2097
15 | 2658213.099 | 1192840.1254
16 | 2658193.6308 | 1192832.5853
17 | 2658235.1794 | 1192848.6773
18 | 2658170.3616 | 1192823.573
19 | 2658268.0373 | 1192861.4033
20 | 2658117.6611 | 1192803.1618
21 | 2658287.9075 | 1192869.0992
22 | 2658125.2404 | 1192834.2865
23 | 2658355.136 | 1192895.7916
24 | 2658330.9251 | 1192908.5296
25 | 2658388.4037 | 1192908.5824
26 | 2658299.7393 | 1192947.9262
27 | 2658349.3403 | 1192927.331
28 | 2658428.1207 | 1192923.8529
29 | 2657768.7354 | 1192686.5279
30 | 2657921.2473 | 1192767.0222
31 | 2657757.7276 | 1192679.1409
32 | 2657679.3487 | 1192809.1151
33 | 2657929.9774 | 1192768.8009
34 | 2657724.6868 | 1192591.5367
35 | 2657643.2765 | 1192902.5709
36 | 2657651.7638 | 1192906.2181
37 | 2657620.1818 | 1192878.8963
38 | 2657657.9332 | 1192916.3034
39 | 2657618.0559 | 1192808.2284
40 | 2657959.685 | 1192773.9288
41 | 2657916.354 | 1192704.4211
42 | 2657767.694 | 1192559.9076
43 | 2657578.6673 | 1192852.2706
44 | 2657986.8771 | 1192776.923
45 | 2657956.1524 | 1192674.4447
46 | 2657771.1762 | 1192560.5795
47 | 2658064.5554 | 1192785.0695
48 | 2658060.6832 | 1192803.9205
49 | 2658146.7983 | 1192694.7109
50 | 2658116.0298 | 1192830.5147
51 | 2658108.5611 | 1192876.0668
52 | 2657987.966 | 1192734.5888
53 | 2658089.6964 | 1192813.7626
54 | 2658160.1045 | 1192681.3183
55 | 2657805.9486 | 1192551.2999
56 | 2657802.8233 | 1192241.9596
57 | 2657899.2334 | 1192333.8047
58 | 2658183.8159 | 1193349.3971
59 | 2658125.0922 | 1193295.2143
60 | 2657940.4699 | 1193101.0247
61 | 2657978.1165 | 1193101.1311
62 | 2658240.6176 | 1193215.2372
63 | 2658155.0269 | 1193113.6692
64 | 2658246.6733 | 1193142.032
65 | 2658133.737 | 1193084.7903
66 | 2658295.8824 | 1193156.0246
67 | 2658402.4721 | 1193164.296
68 | 2658277.025 | 1192297.5157
69 | 2658285.6428 | 1192305.7658
70 | 2658262.8659 | 1192296.2609
71 | 2658279.8606 | 1192310.0786
72 | 2658321.55 | 1192302.0833
73 | 2658297.0139 | 1192315.4265
74 | 2658276.0359 | 1192311.2625
75 | 2658385.3367 | 1192292.3259
76 | 2658259.8531 | 1192313.895
77 | 2658393.3835 | 1192291.4776
78 | 2658426.069 | 1192290.0886
79 | 2658436.1423 | 1192291.302
80 | 2658212.7831 | 1192307.3003
81 | 2658122.8507 | 1192288.5178
82 | 2658120.853 | 1192212.4327
83 | 2658087.9552 | 1192441.2998
84 | 2658245.1595 | 1192476.1592
85 | 2658350.291 | 1192404.7006
86 | 2658328.7959 | 1192427.8838
87 | 2658352.6457 | 1192403.152
88 | 2658401.5686 | 1192633.7054
89 | 2658363.0982 | 1192673.4085
90 | 2658116.841 | 1192939.0102
91 | 2658093.0117 | 1192911.7077
92 | 2658118.0003 | 1192940.8773
93 | 2658092.7292 | 1192891.7363
94 | 2658096.0974 | 1192888.8862
95 | 2658097.8941 | 1192887.366
96 | 2658105.0604 | 1192824.7637
97 | 2658162.917 | 1192584.1871
98 | 2658178.995 | 1192594.336
99 | 2658208.3525 | 1192612.8673
100 | 2658219.8506 | 1192621.1839
101 | 2658194.2329 | 1192646.968
102 | 2658168.09 | 1192673.2808
103 | 2658311.456 | 1193072.3273
104 | 2658331.3514 | 1193086.0359
105 | 2658248.2106 | 1193028.7487
106 | 2658354.5404 | 1193100.7165
107 | 2658371.4279 | 1193111.0846
108 | 2658410.6873 | 1193123.0525
109 | 2658508.7992 | 1193186.9362
110 | 2658459.2134 | 1193068.1304
111 | 2658556.2061 | 1193169.8375
112 | 2658454.2243 | 1193272.3565
113 | 2658483.1712 | 1193068.2479
114 | 2658557.3861 | 1193169.379
115 | 2658459.8651 | 1193282.1794
116 | 2658505.4858 | 1193068.3573
117 | 2658391.2757 | 1193242.3538
118 | 2658465.9072 | 1193443.9408
119 | 2658515.6937 | 1193068.4074
120 | 2658524.9353 | 1193069.1566
121 | 2658542.6654 | 1193072.0261
122 | 2658565.2415 | 1193077.3685
123 | 2658569.6802 | 1193078.4189
124 | 2658562.6284 | 1193023.6744
125 | 2658539.7606 | 1193019.386
126 | 2658517.4514 | 1193018.8022
127 | 2658503.5335 | 1193018.5838
128 | 2658481.5781 | 1193018.2393
129 | 2658476.6795 | 1193018.1624
130 | 2658472.5862 | 1193018.0982
131 | 2658459.1777 | 1193017.8878
132 | 2658444.7449 | 1192995.4503
133 | 2658416.8969 | 1192963.6055
134 | 2658430.7917 | 1193009.9811
135 | 2658420.492 | 1192941.0637
136 | 2658399.2274 | 1193004.734
137 | 2658422.3609 | 1192936.8486
138 | 2658391.4288 | 1193003.3071
139 | 2658436.8632 | 1192949.6419
140 | 2658465.6092 | 1192938.494
141 | 2658345.593 | 1192937.6383
142 | 2658341.5549 | 1192948.7452
143 | 2658351.5623 | 1192928.1448
144 | 2658364.6476 | 1192938.8868
145 | 2658456.4553 | 1192966.5207
146 | 2658355.136 | 1192895.7916

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9856 | -0.27483 | 0.011953 | 0.0029957
1 | 0.98423 | -0.3015 | 0.0052078 | 0.0013052
2 | 0.98575 | -0.27204 | 0 | 0
3 | 0.9839 | -0.30782 | 0 | 0
4 | 0.98937 | -0.20223 | 0.0095952 | 0.0024048
5 | 0.98165 | -0.35156 | 0 | 0
6 | 0.99056 | -0.1794 | 0 | 0
7 | 0.98985 | -0.19324 | 0 | 0
8 | 0.9902 | -0.1864 | 0.0039878 | 0.00099945
9 | 0.98764 | -0.23622 | 0 | 0
10 | 0.98113 | -0.3618 | 0.0036209 | 0.00090749
11 | 0.98156 | -0.35332 | 0.0049707 | 0.0012458
12 | 0.99356 | -0.1222 | 0.0022827 | 0.00057209
13 | 0.98754 | -0.23811 | 0.0055473 | 0.0013903
14 | 0.98729 | -0.24306 | 0.0028981 | 0.00072633
15 | 0.99509 | -0.093445 | 0.00032462 | 8.1358e-05
16 | 0.99462 | -0.10249 | 0.00040014 | 0.00010029
17 | 0.99563 | -0.083128 | 0.00032963 | 8.2613e-05
18 | 0.99406 | -0.11323 | 0.00098212 | 0.00024614
19 | 0.99644 | -0.067692 | 0.0014264 | 0.0003575
20 | 0.99281 | -0.13709 | 0 | 0
21 | 0.99695 | -0.058103 | 0 | 0
22 | 0.9921 | -0.1507 | 0.00079914 | 0.00020028
23 | 0.99865 | -0.025621 | 0 | 0
24 | 0.99788 | -0.040456 | 0 | 0
25 | 1 | 0 | -0.26262 | -0.066822
26 | 0.99688 | -0.059694 | 0.021039 | 0.0052728
27 | 0.99759 | -0.046094 | 0 | 0
28 | 0.99656 | -0.0651 | 0 | 0
29 | 0.98657 | -0.25725 | 0.00017938 | 4.4956e-05
30 | 0.98847 | -0.22065 | 0.00042188 | 0.00010573
31 | 0.98644 | -0.25983 | 0 | 0
32 | 0.98634 | -0.26184 | 0.0003377 | 8.4635e-05
33 | 0.98857 | -0.21874 | 0 | 0
34 | 0.98545 | -0.27881 | 0.00050473 | 0.0001265
35 | 0.98612 | -0.26609 | 0.00016312 | 4.0881e-05
36 | 0.98611 | -0.2662 | 0.00057353 | 0.00014374
37 | 0.98614 | -0.26557 | 0.00026579 | 6.6613e-05
38 | 0.98611 | -0.26623 | 0.00010301 | 2.5817e-05
39 | 0.98626 | -0.26333 | 0.00023323 | 5.8453e-05
40 | 0.98894 | -0.21163 | 0.00019224 | 4.818e-05
41 | 0.9884 | -0.22199 | 0.0013783 | 0.00034544
42 | 0.98485 | -0.29047 | 0.00094903 | 0.00023785
43 | 0.9862 | -0.26458 | 0 | 0
44 | 0.98927 | -0.20513 | 0 | 0
45 | 0.98835 | -0.22296 | 0.0010776 | 0.00027007
46 | 0.98481 | -0.29112 | 0.00018744 | 4.6976e-05
47 | 0.99028 | -0.18586 | 0 | 0
48 | 0.99066 | -0.17857 | 0 | 0
49 | 0.9886 | -0.21844 | 0.0012274 | 0.00030762
50 | 0.9919 | -0.15463 | 0.00024871 | 6.2331e-05
51 | 0.992 | -0.15268 | 0.00050862 | 0.00012747
52 | 0.98923 | -0.206 | 0.0011465 | 0.00028734
53 | 0.99126 | -0.16691 | 0.001411 | 0.00035362
54 | 0.98836 | -0.22302 | 0.00091711 | 0.00022985
55 | 0.98442 | -0.29883 | 0.00059631 | 0.00014945
56 | 0.98162 | -0.35306 | 0 | 0
57 | 0.97921 | -0.39996 | 0.00016258 | 4.0746e-05
58 | 0.97183 | -0.54442 | 0.00053151 | 0.00013321
59 | 0.97187 | -0.54363 | 0.00063647 | 0.00015952
60 | 0.97163 | -0.54844 | 0.0010775 | 0.00027004
61 | 0.97167 | -0.54769 | 0.00044376 | 0.00011122
62 | 0.97202 | -0.54059 | 0.00086867 | 0.00021771
63 | 0.97192 | -0.54267 | 0 | 0
64 | 0.97217 | -0.53773 | 0 | 0
65 | 0.97188 | -0.54351 | 0.0012688 | 0.00031798
66 | 0.9724 | -0.53315 | 0.00030002 | 7.5192e-05
67 | 0.97292 | -0.52288 | 0 | 0
68 | 0.97099 | -0.56164 | 0.0012003 | 0.00030082
69 | 0.97104 | -0.56056 | 0 | 0
70 | 0.97094 | -0.56249 | 0.003219 | 0.00080676
71 | 0.9711 | -0.55933 | 0 | 0
72 | 0.97088 | -0.56382 | 0.001377 | 0.00034511
73 | 0.97108 | -0.55976 | 0.0012843 | 0.00032187
74 | 0.97114 | -0.55855 | 0.00079715 | 0.00019978
75 | 0.97067 | -0.56793 | 0.0011144 | 0.00027929
76 | 0.97132 | -0.55511 | 0.00094395 | 0.00023658
77 | 0.97065 | -0.56828 | 0.00071749 | 0.00017982
78 | 0.9706 | -0.56925 | 0.0012569 | 0.00031502
79 | 0.9706 | -0.56931 | 0.00034222 | 8.5769e-05
80 | 0.97186 | -0.54429 | 0.0018034 | 0.00045198
81 | 0.97308 | -0.52033 | 0 | 0
82 | 0.97302 | -0.52136 | 0.00071598 | 0.00017944
83 | 0.97531 | -0.47629 | 0 | 0
84 | 0.97459 | -0.49049 | 0.0011167 | 0.00027988
85 | 0.97422 | -0.4979 | 0.0010251 | 0.00025691
86 | 0.97429 | -0.49646 | 0.00091748 | 0.00022994
87 | 0.97421 | -0.49797 | 0.0013932 | 0.00034918
88 | 0.98672 | -0.2551 | 0.0044172 | 0.001107
89 | 0.98694 | -0.25069 | 0 | 0
90 | 0.99191 | -0.15439 | 0.00038526 | 9.6555e-05
91 | 0.99194 | -0.15392 | 0.00043429 | 0.00010884
92 | 0.99191 | -0.1544 | 0.00033363 | 8.3615e-05
93 | 0.99197 | -0.15338 | 0.00027237 | 6.8262e-05
94 | 0.99197 | -0.15327 | 0.00014527 | 3.6407e-05
95 | 0.99198 | -0.15321 | 0.00032925 | 8.2518e-05
96 | 0.99164 | -0.15953 | 0.00030383 | 7.6148e-05
97 | 0.98731 | -0.24343 | 0.0031187 | 0.00078161
98 | 0.98737 | -0.24237 | 0.0013019 | 0.00032629
99 | 0.98751 | -0.23963 | 0 | 0
100 | 0.98757 | -0.2385 | 0 | 0
101 | 0.98786 | -0.23276 | 0.0019859 | 0.00049771
102 | 0.98823 | -0.22558 | 0.0018426 | 0.0004618
103 | 0.97144 | -0.55195 | 0.00083066 | 0.00020818
104 | 0.97179 | -0.54511 | 0.00030792 | 7.7173e-05
105 | 0.9704 | -0.57253 | 0.014489 | 0.0036313
106 | 0.97219 | -0.53719 | 0.0010911 | 0.00027345
107 | 0.9725 | -0.53105 | 0.00042515 | 0.00010655
108 | 0.97327 | -0.51592 | 0 | 0
109 | 0.97313 | -0.51874 | 0 | 0
110 | 0.97523 | -0.47723 | 0.0094773 | 0.0023752
111 | 0.97306 | -0.51995 | 0.00082102 | 0.00020577
112 | 0.97252 | -0.53083 | 0.0018319 | 0.00045912
113 | 0.97605 | -0.46113 | 0.0065634 | 0.0016449
114 | 0.97306 | -0.51996 | 0.00048672 | 0.00012198
115 | 0.9725 | -0.53119 | 0 | 0
116 | 0.97695 | -0.44349 | 0.0041415 | 0.0010379
117 | 0.97238 | -0.53355 | 0.001606 | 0.00040249
118 | 0.97247 | -0.53165 | 0.0001513 | 3.7919e-05
119 | 0.9774 | -0.43466 | 0.0063882 | 0.001601
120 | 0.97786 | -0.42556 | 0.0035673 | 0.00089404
121 | 0.97882 | -0.40675 | 0.0020829 | 0.00052201
122 | 0.97946 | -0.39421 | 0.0037585 | 0.00094197
123 | 0.9796 | -0.39159 | 0.0035935 | 0.00090062
124 | 0.98046 | -0.37482 | 0.0021993 | 0.00055119
125 | 0.97976 | -0.38846 | 0.0033686 | 0.00084425
126 | 0.97917 | -0.40012 | 0.0043435 | 0.0010886
127 | 0.97885 | -0.40629 | 0.0026262 | 0.00065818
128 | 0.97841 | -0.41499 | 0.0034857 | 0.00087361
129 | 0.97833 | -0.41663 | 0.0083971 | 0.0021045
130 | 0.97829 | -0.41736 | 0.0034857 | 0.00087361
131 | 0.97821 | -0.41893 | 0.0064028 | 0.0016047
132 | 0.99572 | -0.081248 | 0.0011067 | 0.00027737
133 | 0.99602 | -0.075486 | 0.0030806 | 0.00077208
134 | 0.99558 | -0.083958 | 0.0023946 | 0.00060014
135 | 0.99626 | -0.070941 | 0.0043046 | 0.0010788
136 | 0.99546 | -0.086321 | 0.0010167 | 0.00025482
137 | 0.99632 | -0.06972 | 0 | 0
138 | 0.99544 | -0.086764 | 0.0031737 | 0.0007954
139 | 0.99626 | -0.070886 | 0.0034393 | 0.00086198
140 | 0.99365 | -0.12037 | 0 | 0
141 | 0.99755 | -0.046891 | 0.0011742 | 0.00029428
142 | 0.99752 | -0.047508 | 0.0029782 | 0.00074641
143 | 0.99758 | -0.046337 | 0.0021134 | 0.00052966
144 | 0.99752 | -0.047526 | 0.003764 | 0.00094334
145 | 0.99351 | -0.12308 | 0.0052163 | 0.0013073
146 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.11579 | 0.02936 | -0.11564 | -0.029266 | 0.00014823 | 9.4207e-05 | 0.17494 | 0.17494 | 0.17494 | 0.9856 | -0.27483 | 0.98423 | -0.3015 | 24.0301
1 | -0.12775 | -0.032356 | 0.12776 | 0.032367 | 1.7127e-05 | 1.0899e-05 | 0.19298 | 0.19298 | 0.19298 | 0.9856 | -0.27483 | 0.98575 | -0.27204 | 26.5089
2 | 0.11044 | 0.027961 | -0.1104 | -0.027939 | 3.351e-05 | 2.1284e-05 | 0.16707 | 0.16707 | 0.16707 | 0.98423 | -0.3015 | 0.9839 | -0.30782 | 22.9486
3 | -0.12776 | -0.032367 | 0.12819 | 0.03264 | 0.00043001 | 0.00027363 | 0.19298 | 0.19298 | 0.19298 | 0.98575 | -0.27204 | 0.98937 | -0.20223 | 26.5089
4 | 0.1104 | 0.027939 | -0.11017 | -0.027793 | 0.00023124 | 0.00014687 | 0.16707 | 0.16707 | 0.16707 | 0.9839 | -0.30782 | 0.98165 | -0.35156 | 22.9486
5 | -0.13779 | -0.035045 | 0.13794 | 0.035142 | 0.00015172 | 9.6616e-05 | 0.20742 | 0.20741 | 0.20742 | 0.98937 | -0.20223 | 0.99056 | -0.1794 | 28.4911
6 | 0.1052 | 0.026547 | -0.10515 | -0.026514 | 5.1571e-05 | 3.2733e-05 | 0.15953 | 0.15953 | 0.15953 | 0.98165 | -0.35156 | 0.98113 | -0.3618 | 21.9136
7 | 0.0049711 | 0.0012458 | -0.0049707 | -0.0012458 | 4.1718e-07 | 1.9333e-08 | 0.0075354 | 0.0075355 | 0.0075355 | 0.98165 | -0.35156 | 0.98156 | -0.35332 | 2.0702
8 | 0.012459 | 0.0031265 | -0.012455 | -0.0031242 | 4.1522e-06 | 2.2507e-06 | 0.018717 | 0.018717 | 0.018717 | 0.99056 | -0.1794 | 0.9902 | -0.1864 | 5.1421
9 | -0.1504 | -0.038268 | 0.15081 | 0.038533 | 0.00041594 | 0.00026508 | 0.22613 | 0.22613 | 0.22613 | 0.99056 | -0.1794 | 0.99356 | -0.1222 | 31.0621
10 | -0.0084642 | -0.0021236 | 0.0084669 | 0.0021248 | 2.7643e-06 | 1.1837e-06 | 0.012725 | 0.012725 | 0.012725 | 0.98985 | -0.19324 | 0.9902 | -0.1864 | 3.4958
11 | 0.0084642 | 0.0021236 | -0.0084469 | -0.0021162 | 1.7317e-05 | 7.4254e-06 | 0.012725 | 0.012726 | 0.012726 | 0.98985 | -0.19324 | 0.98764 | -0.23622 | 3.4962
12 | 0.0084469 | 0.0021162 | -0.0084461 | -0.0021158 | 7.5852e-07 | 3.2564e-07 | 0.012726 | 0.012726 | 0.012726 | 0.98764 | -0.23622 | 0.98754 | -0.23811 | 3.4962
13 | 0.034386 | 0.0086462 | -0.034364 | -0.0086328 | 2.136e-05 | 1.3406e-05 | 0.052161 | 0.052161 | 0.052161 | 0.98113 | -0.3618 | 0.98046 | -0.37482 | 14.3299
14 | 0.067142 | 0.01696 | -0.067046 | -0.0169 | 9.5718e-05 | 6.0019e-05 | 0.10188 | 0.10188 | 0.10188 | 0.98113 | -0.3618 | 0.9796 | -0.39159 | 13.9943
15 | -0.1531 | -0.039105 | 0.15311 | 0.039114 | 1.3563e-05 | 8.6445e-06 | 0.22955 | 0.22955 | 0.22955 | 0.99356 | -0.1222 | 0.99365 | -0.12037 | 31.5316
16 | 0.0028988 | 0.00072554 | -0.0028981 | -0.00072633 | 6.8268e-07 | -7.8373e-07 | 0.0043675 | 0.0043679 | 0.0043679 | 0.98754 | -0.23811 | 0.98729 | -0.24306 | 1.2
17 | 0.049667 | 0.012625 | -0.049645 | -0.012612 | 2.1629e-05 | 1.3301e-05 | 0.074333 | 0.074333 | 0.074333 | 0.99509 | -0.093445 | 0.99462 | -0.10249 | 10.2106
18 | -0.049992 | -0.012707 | 0.050017 | 0.012722 | 2.4853e-05 | 1.529e-05 | 0.074818 | 0.074818 | 0.074818 | 0.99509 | -0.093445 | 0.99563 | -0.083128 | 10.2772
19 | 0.049245 | 0.012512 | -0.04922 | -0.012496 | 2.5438e-05 | 1.5633e-05 | 0.073734 | 0.073735 | 0.073735 | 0.99462 | -0.10249 | 0.99406 | -0.11323 | 10.1284
20 | -0.050346 | -0.012804 | 0.050384 | 0.012828 | 3.7472e-05 | 2.3065e-05 | 0.075311 | 0.07531 | 0.075311 | 0.99563 | -0.083128 | 0.99644 | -0.067692 | 10.3449
21 | 0.048238 | 0.01225 | -0.048182 | -0.012216 | 5.5338e-05 | 3.3953e-05 | 0.072265 | 0.072265 | 0.072265 | 0.99406 | -0.11323 | 0.99281 | -0.13709 | 9.9265
22 | -0.05181 | -0.013185 | 0.051834 | 0.0132 | 2.396e-05 | 1.4779e-05 | 0.077441 | 0.07744 | 0.077441 | 0.99644 | -0.067692 | 0.99695 | -0.058103 | 10.6374
23 | 0.048182 | 0.012216 | -0.048151 | -0.012197 | 3.1491e-05 | 1.9323e-05 | 0.072265 | 0.072265 | 0.072265 | 0.99281 | -0.13709 | 0.9921 | -0.1507 | 9.9266
24 | -0.051834 | -0.0132 | 0.051915 | 0.01325 | 8.1338e-05 | 5.0166e-05 | 0.07744 | 0.07744 | 0.07744 | 0.99695 | -0.058103 | 0.99865 | -0.025621 | 10.6374
25 | 0.044943 | 0.011394 | -0.044934 | -0.011389 | 8.4913e-06 | 5.1774e-06 | 0.067454 | 0.067454 | 0.067454 | 0.9921 | -0.1507 | 0.9919 | -0.15463 | 9.2657
26 | 0.002409 | 0.00060216 | -0.0024088 | -0.00060261 | 2.2677e-07 | -4.5311e-07 | 0.0036126 | 0.0036128 | 0.0036128 | 0.9921 | -0.1507 | 0.992 | -0.15268 | 0.99253
27 | 0.031113 | 0.007813 | -0.031091 | -0.0077992 | 2.2005e-05 | 1.3726e-05 | 0.046364 | 0.046365 | 0.046365 | 0.99865 | -0.025621 | 0.99788 | -0.040456 | 12.7375
28 | -0.083028 | -0.021063 | 0.083131 | 0.021128 | 0.00010243 | 6.4622e-05 | 0.1238 | 0.1238 | 0.1238 | 0.99865 | -0.025621 | 1 | 0 | 17.006
29 | 0.021058 | 0.0052845 | -0.021039 | -0.0052728 | 1.93e-05 | 1.1671e-05 | 0.031404 | 0.031404 | 0.031404 | 0.99788 | -0.040456 | 0.99688 | -0.059694 | 8.6274
30 | 0.010033 | 0.0025148 | -0.01003 | -0.0025135 | 2.6939e-06 | 1.3049e-06 | 0.014961 | 0.014961 | 0.014961 | 0.99788 | -0.040456 | 0.99759 | -0.046094 | 4.1102
31 | 0.17784 | 0.045695 | -0.17728 | -0.045337 | 0.0005604 | 0.00035754 | 0.26503 | 0.26503 | 0.26503 | 1 | 0 | 0.99656 | -0.0651 | 36.4048
32 | 0.0058776 | 0.0014729 | -0.0058776 | -0.0014729 | 6.8206e-08 | 1.2757e-08 | 0.0087671 | 0.0087671 | 0.0087671 | 0.99759 | -0.046094 | 0.99758 | -0.046337 | 2.4085
33 | 0.0041527 | 0.0010406 | -0.0041525 | -0.0010406 | 1.5779e-07 | -4.2198e-08 | 0.0061941 | 0.0061941 | 0.0061941 | 0.99759 | -0.046094 | 0.99755 | -0.046891 | 1.7017
34 | 0.15875 | 0.040692 | -0.15833 | -0.040421 | 0.00042409 | 0.00027037 | 0.23736 | 0.23736 | 0.23736 | 0.99656 | -0.0651 | 0.99365 | -0.12037 | 32.6048
35 | 0.018527 | 0.0046454 | -0.018523 | -0.004643 | 4.0786e-06 | 2.4252e-06 | 0.027665 | 0.027665 | 0.027665 | 0.99656 | -0.0651 | 0.99632 | -0.06972 | 7.6002
36 | -0.023752 | -0.0060244 | 0.023794 | 0.0060468 | 4.1868e-05 | 2.235e-05 | 0.03585 | 0.035848 | 0.03585 | 0.98657 | -0.25725 | 0.98847 | -0.22065 | 4.9245
37 | 0.021896 | 0.0055639 | -0.021893 | -0.0055625 | 2.7154e-06 | 1.3993e-06 | 0.033052 | 0.033052 | 0.033052 | 0.98657 | -0.25725 | 0.98644 | -0.25983 | 4.5401
38 | 0.001677 | 0.00041562 | -0.0016766 | -0.00041732 | 3.636e-07 | -1.7041e-06 | 0.0025277 | 0.0025284 | 0.0025284 | 0.98657 | -0.25725 | 0.98634 | -0.26184 | 0.6946
39 | -0.024216 | -0.0061525 | 0.024218 | 0.0061537 | 2.2251e-06 | 1.1955e-06 | 0.036484 | 0.036483 | 0.036484 | 0.98847 | -0.22065 | 0.98857 | -0.21874 | 5.0115
40 | 0.021893 | 0.0055625 | -0.021873 | -0.0055522 | 1.9992e-05 | 1.0306e-05 | 0.033052 | 0.033053 | 0.033053 | 0.98644 | -0.25983 | 0.98545 | -0.27881 | 4.5402
41 | 0.0013389 | 0.00033269 | -0.0013388 | -0.00033342 | 9.4617e-08 | -7.2935e-07 | 0.0020189 | 0.0020192 | 0.0020192 | 0.98634 | -0.26184 | 0.98626 | -0.26333 | 0.55472
42 | -0.026674 | -0.0067679 | 0.026683 | 0.006773 | 9.1275e-06 | 5.0681e-06 | 0.04018 | 0.04018 | 0.04018 | 0.98857 | -0.21874 | 0.98894 | -0.21163 | 5.5193
43 | 0.0024564 | 0.0006142 | -0.002456 | -0.0006149 | 3.792e-07 | -7.0567e-07 | 0.0036969 | 0.0036972 | 0.0036972 | 0.98857 | -0.21874 | 0.9884 | -0.22199 | 1.0157
44 | 0.021368 | 0.0054257 | -0.021356 | -0.0054195 | 1.1986e-05 | 6.11e-06 | 0.032291 | 0.032291 | 0.032291 | 0.98545 | -0.27881 | 0.98485 | -0.29047 | 4.4356
45 | 0.00067654 | 0.00016926 | -0.00067654 | -0.00016937 | 3.6097e-09 | -1.1554e-07 | 0.0010208 | 0.0010208 | 0.0010208 | 0.98612 | -0.26609 | 0.98611 | -0.2662 | 0.28044
46 | -0.00083966 | -0.00021014 | 0.00083968 | 0.00020972 | 2.0624e-08 | -4.24e-07 | 0.0012669 | 0.0012668 | 0.0012669 | 0.98612 | -0.26609 | 0.98614 | -0.26557 | 0.34805
47 | 0.00010301 | 2.5636e-05 | -0.00010301 | -2.5817e-05 | 1.2857e-10 | -1.8103e-07 | 0.00015538 | 0.00015544 | 0.00015544 | 0.98611 | -0.2662 | 0.98611 | -0.26623 | 0.042703
48 | -0.0011055 | -0.00027633 | 0.0011055 | 0.00027573 | 5.1874e-08 | -6.014e-07 | 0.0016678 | 0.0016676 | 0.0016678 | 0.98614 | -0.26557 | 0.9862 | -0.26458 | 0.45819
49 | 0.0011056 | 0.00027496 | -0.0011055 | -0.00027573 | 6.584e-08 | -7.6365e-07 | 0.0016673 | 0.0016676 | 0.0016676 | 0.98626 | -0.26333 | 0.9862 | -0.26458 | 0.45813
50 | -0.026876 | -0.0068212 | 0.026884 | 0.0068258 | 8.4006e-06 | 4.6741e-06 | 0.040469 | 0.040469 | 0.040469 | 0.98894 | -0.21163 | 0.98927 | -0.20513 | 5.559
51 | 0.0010777 | 0.00026946 | -0.0010776 | -0.00027007 | 4.9723e-08 | -6.1387e-07 | 0.0016222 | 0.0016224 | 0.0016224 | 0.9884 | -0.22199 | 0.98835 | -0.22296 | 0.44571
52 | 0.020407 | 0.0051817 | -0.020407 | -0.0051814 | 6.3315e-07 | 3.1497e-07 | 0.030857 | 0.030857 | 0.030857 | 0.98485 | -0.29047 | 0.98481 | -0.29112 | 4.2387
53 | -0.028031 | -0.0071127 | 0.028057 | 0.0071273 | 2.6002e-05 | 1.4639e-05 | 0.042193 | 0.042193 | 0.042193 | 0.98927 | -0.20513 | 0.99028 | -0.18586 | 5.7958
54 | 0.0011465 | 0.00028682 | -0.0011465 | -0.00028734 | 4.7531e-08 | -5.1679e-07 | 0.0017244 | 0.0017246 | 0.0017246 | 0.98927 | -0.20513 | 0.98923 | -0.206 | 0.47379
55 | 0.020219 | 0.0051344 | -0.020212 | -0.0051307 | 7.4957e-06 | 3.7094e-06 | 0.030574 | 0.030575 | 0.030575 | 0.98481 | -0.29112 | 0.98442 | -0.29883 | 4.1998
56 | -0.042905 | -0.010857 | 0.042921 | 0.010866 | 1.5017e-05 | 9.1156e-06 | 0.064508 | 0.064508 | 0.064508 | 0.99028 | -0.18586 | 0.99066 | -0.17857 | 8.861
57 | 0.014849 | 0.0037299 | -0.014826 | -0.0037167 | 2.3052e-05 | 1.3168e-05 | 0.022315 | 0.022316 | 0.022316 | 0.99028 | -0.18586 | 0.9886 | -0.21844 | 6.1307
58 | -0.042921 | -0.010866 | 0.042945 | 0.010881 | 2.4042e-05 | 1.4593e-05 | 0.064508 | 0.064508 | 0.064508 | 0.99066 | -0.17857 | 0.99126 | -0.16691 | 8.861
59 | 0.013598 | 0.0034091 | -0.013595 | -0.0034074 | 2.9661e-06 | 1.6563e-06 | 0.020468 | 0.020468 | 0.020468 | 0.9886 | -0.21844 | 0.98836 | -0.22302 | 5.6232
60 | 0.044686 | 0.011327 | -0.044675 | -0.01132 | 1.0519e-05 | 6.4102e-06 | 0.067081 | 0.067081 | 0.067081 | 0.9919 | -0.15463 | 0.99164 | -0.15953 | 9.2145
61 | 0.0019002 | 0.00047514 | -0.0019001 | -0.00047531 | 4.7687e-08 | -1.7161e-07 | 0.0028499 | 0.00285 | 0.00285 | 0.992 | -0.15268 | 0.99198 | -0.15321 | 0.78296
62 | -0.044356 | -0.011234 | 0.044371 | 0.011244 | 1.5728e-05 | 9.5783e-06 | 0.066626 | 0.066625 | 0.066626 | 0.99126 | -0.16691 | 0.99164 | -0.15953 | 9.1519
63 | 0.012678 | 0.0031776 | -0.012677 | -0.0031767 | 1.548e-06 | 8.4554e-07 | 0.019088 | 0.019088 | 0.019088 | 0.98836 | -0.22302 | 0.98823 | -0.22558 | 5.2439
64 | 0.019615 | 0.0049812 | -0.019564 | -0.0049564 | 5.1078e-05 | 2.4846e-05 | 0.029673 | 0.029676 | 0.029676 | 0.98442 | -0.29883 | 0.98162 | -0.35306 | 4.0764
65 | 0.019564 | 0.0049564 | -0.01952 | -0.0049299 | 4.3976e-05 | 2.6465e-05 | 0.029676 | 0.029677 | 0.029677 | 0.98162 | -0.35306 | 0.97921 | -0.39996 | 8.1529
66 | 0.019358 | 0.0048892 | -0.019287 | -0.0048468 | 7.0543e-05 | 4.2426e-05 | 0.02943 | 0.029431 | 0.029431 | 0.97921 | -0.39996 | 0.97531 | -0.47629 | 8.0853
67 | -0.00053151 | -0.00013321 | 0.00053153 | 0.00013222 | 2.0018e-08 | -9.8635e-07 | 0.00081382 | 0.00081346 | 0.00081382 | 0.97183 | -0.54442 | 0.97187 | -0.54363 | 0.22358
68 | -0.001168 | -0.00029174 | 0.0011682 | 0.0002901 | 1.6838e-07 | -1.6336e-06 | 0.001788 | 0.0017873 | 0.001788 | 0.97187 | -0.54363 | 0.97202 | -0.54059 | 0.4912
69 | -0.0010775 | -0.00027004 | 0.0010775 | 0.0002696 | 3.8461e-08 | -4.4198e-07 | 0.0016501 | 0.0016499 | 0.0016501 | 0.97163 | -0.54844 | 0.97167 | -0.54769 | 0.45332
70 | -0.0015213 | -0.00038081 | 0.0015216 | 0.00037884 | 3.6267e-07 | -1.9767e-06 | 0.0023295 | 0.0023287 | 0.0023295 | 0.97167 | -0.54769 | 0.97192 | -0.54267 | 0.63997
71 | -0.0020368 | -0.00050781 | 0.0020371 | 0.00050705 | 2.7654e-07 | -7.6402e-07 | 0.0031171 | 0.0031168 | 0.0031171 | 0.97202 | -0.54059 | 0.97217 | -0.53773 | 0.85635
72 | 0.0012688 | 0.00031757 | -0.0012688 | -0.00031798 | 5.0722e-08 | -4.1175e-07 | 0.0019424 | 0.0019426 | 0.0019426 | 0.97192 | -0.54267 | 0.97188 | -0.54351 | 0.53368
73 | -0.0027904 | -0.00069641 | 0.0027911 | 0.00069564 | 6.5449e-07 | -7.6719e-07 | 0.0042711 | 0.0042707 | 0.0042711 | 0.97192 | -0.54267 | 0.97217 | -0.53773 | 1.1734
74 | -0.0048282 | -0.0012027 | 0.0048293 | 0.0012027 | 1.047e-06 | 3.558e-08 | 0.0073875 | 0.0073873 | 0.0073875 | 0.97217 | -0.53773 | 0.9724 | -0.53315 | 2.0295
75 | -0.0051293 | -0.0012779 | 0.0051318 | 0.0012782 | 2.5004e-06 | 2.5595e-07 | 0.0078464 | 0.0078459 | 0.0078464 | 0.9724 | -0.53315 | 0.97292 | -0.52288 | 2.1556
76 | 0.0035907 | 0.00089591 | -0.0035894 | -0.00089653 | 1.3556e-06 | -6.2089e-07 | 0.0054903 | 0.0054909 | 0.0054909 | 0.97292 | -0.52288 | 0.97252 | -0.53083 | 1.5085
77 | -0.0087225 | -0.0021741 | 0.0087254 | 0.0021754 | 2.88e-06 | 1.3068e-06 | 0.013336 | 0.013336 | 0.013336 | 0.97292 | -0.52288 | 0.97327 | -0.51592 | 3.6638
78 | -0.0044194 | -0.0011075 | 0.0044197 | 0.0011075 | 2.2815e-07 | -1.8056e-08 | 0.0067727 | 0.0067726 | 0.0067727 | 0.97099 | -0.56164 | 0.97104 | -0.56056 | 1.8606
79 | 0.0032192 | 0.00080667 | -0.003219 | -0.00080676 | 1.2973e-07 | -9.2786e-08 | 0.0049332 | 0.0049333 | 0.0049333 | 0.97099 | -0.56164 | 0.97094 | -0.56249 | 1.3553
80 | -0.0092292 | -0.0023116 | 0.0092298 | 0.0023118 | 5.4008e-07 | 2.5657e-07 | 0.014142 | 0.014142 | 0.014142 | 0.97104 | -0.56056 | 0.9711 | -0.55933 | 3.8852
81 | 0.0048095 | 0.0012041 | -0.0048088 | -0.0012041 | 7.4559e-07 | 2.4408e-08 | 0.0073696 | 0.0073698 | 0.0073698 | 0.97104 | -0.56056 | 0.97088 | -0.56382 | 2.0247
82 | 0.0012843 | 0.00032167 | -0.0012843 | -0.00032187 | 2.6026e-08 | -2.0506e-07 | 0.0019679 | 0.001968 | 0.001968 | 0.9711 | -0.55933 | 0.97108 | -0.55976 | 0.54065
83 | -0.010514 | -0.0026335 | 0.010514 | 0.0026337 | 3.8967e-07 | 1.9985e-07 | 0.01611 | 0.01611 | 0.01611 | 0.9711 | -0.55933 | 0.97114 | -0.55855 | 4.4258
84 | 0.0034318 | 0.00085896 | -0.0034311 | -0.00085933 | 6.7152e-07 | -3.7059e-07 | 0.0052593 | 0.0052596 | 0.0052596 | 0.97088 | -0.56382 | 0.97067 | -0.56793 | 1.445
85 | -0.011312 | -0.0028335 | 0.011313 | 0.0028345 | 1.8572e-06 | 9.8457e-07 | 0.017331 | 0.017331 | 0.017331 | 0.97114 | -0.55855 | 0.97132 | -0.55511 | 4.7614
86 | 0.0023168 | 0.00058005 | -0.0023167 | -0.00058012 | 3.8268e-08 | -7.5523e-08 | 0.0035513 | 0.0035514 | 0.0035514 | 0.97067 | -0.56793 | 0.97065 | -0.56828 | 0.97565
87 | -0.012257 | -0.003071 | 0.012264 | 0.0030745 | 6.3175e-06 | 3.4515e-06 | 0.018778 | 0.018777 | 0.018778 | 0.97132 | -0.55511 | 0.97186 | -0.54429 | 5.1587
88 | 0.0015992 | 0.0004003 | -0.0015992 | -0.00040066 | 7.4108e-08 | -3.5899e-07 | 0.0024515 | 0.0024516 | 0.0024516 | 0.97065 | -0.56828 | 0.9706 | -0.56925 | 0.67352
89 | 0.00034222 | 8.5644e-05 | -0.00034222 | -8.5769e-05 | 1.0472e-09 | -1.2473e-07 | 0.00052461 | 0.00052466 | 0.00052466 | 0.9706 | -0.56925 | 0.9706 | -0.56931 | 0.14414
90 | -0.014067 | -0.0035265 | 0.014083 | 0.0035356 | 1.6079e-05 | 9.1438e-06 | 0.021539 | 0.021538 | 0.021539 | 0.97186 | -0.54429 | 0.97308 | -0.52033 | 5.9172
91 | 0.00071601 | 0.00017849 | -0.00071598 | -0.00017944 | 3.522e-08 | -9.509e-07 | 0.0010946 | 0.0010949 | 0.0010949 | 0.97308 | -0.52033 | 0.97302 | -0.52136 | 0.3008
92 | -0.014799 | -0.0037141 | 0.01483 | 0.003732 | 3.1147e-05 | 1.7915e-05 | 0.022633 | 0.022632 | 0.022633 | 0.97308 | -0.52033 | 0.97531 | -0.47629 | 6.2178
93 | 0.0044567 | 0.0011147 | -0.0044537 | -0.001115 | 3.0102e-06 | -2.3888e-07 | 0.0067987 | 0.0067995 | 0.0067995 | 0.97531 | -0.47629 | 0.97459 | -0.49049 | 1.868
94 | 0.0033369 | 0.0008351 | -0.003336 | -0.0008357 | 9.4863e-07 | -6.07e-07 | 0.0050944 | 0.0050949 | 0.0050949 | 0.97459 | -0.49049 | 0.97429 | -0.49646 | 1.3997
95 | -0.0024183 | -0.00060606 | 0.0024185 | 0.00060576 | 1.6577e-07 | -2.9737e-07 | 0.0036937 | 0.0036936 | 0.0036937 | 0.97422 | -0.4979 | 0.97429 | -0.49646 | 1.0148
96 | 0.0013933 | 0.00034915 | -0.0013932 | -0.00034918 | 4.7861e-09 | -3.2029e-08 | 0.002128 | 0.0021281 | 0.0021281 | 0.97422 | -0.4979 | 0.97421 | -0.49797 | 0.58463
97 | -0.0044172 | -0.001107 | 0.0044181 | 0.0011069 | 9.2684e-07 | -1.1847e-07 | 0.0066613 | 0.006661 | 0.0066613 | 0.98672 | -0.2551 | 0.98694 | -0.25069 | 1.83
98 | -0.0044181 | -0.0011069 | 0.0044207 | 0.0011066 | 2.5646e-06 | -3.2979e-07 | 0.006661 | 0.0066603 | 0.006661 | 0.98694 | -0.25069 | 0.98757 | -0.2385 | 1.83
99 | -0.00071889 | -0.00018014 | 0.0007189 | 0.00017968 | 1.5998e-08 | -4.6334e-07 | 0.0010784 | 0.0010783 | 0.0010784 | 0.99191 | -0.15439 | 0.99194 | -0.15392 | 0.29627
100 | 0.00033363 | 8.3587e-05 | -0.00033363 | -8.3615e-05 | 2.0645e-10 | -2.8236e-08 | 0.00050048 | 0.00050049 | 0.00050049 | 0.99191 | -0.15439 | 0.99191 | -0.1544 | 0.1375
101 | -0.0011532 | -0.00028852 | 0.0011532 | 0.0002882 | 2.9395e-08 | -3.1941e-07 | 0.0017297 | 0.0017296 | 0.0017297 | 0.99194 | -0.15392 | 0.99197 | -0.15338 | 0.4752
102 | -0.0014256 | -0.00035646 | 0.0014256 | 0.00035641 | 7.5644e-09 | -5.2118e-08 | 0.0021382 | 0.0021382 | 0.0021382 | 0.99197 | -0.15338 | 0.99197 | -0.15327 | 0.58741
103 | -0.0015709 | -0.00039282 | 0.0015709 | 0.00039279 | 4.8993e-09 | -2.7248e-08 | 0.0023561 | 0.0023561 | 0.0023561 | 0.99197 | -0.15327 | 0.99198 | -0.15321 | 0.64727
104 | -0.0031187 | -0.00078161 | 0.0031188 | 0.00078147 | 1.5751e-07 | -1.4236e-07 | 0.0047002 | 0.0047002 | 0.0047002 | 0.98731 | -0.24343 | 0.98737 | -0.24237 | 1.2913
105 | -0.0044207 | -0.0011078 | 0.0044213 | 0.0011077 | 5.7783e-07 | -7.4285e-08 | 0.0066622 | 0.006662 | 0.0066622 | 0.98737 | -0.24237 | 0.98751 | -0.23963 | 1.8303
106 | -0.0044213 | -0.0011077 | 0.0044215 | 0.0011076 | 2.3592e-07 | -3.0372e-08 | 0.006662 | 0.006662 | 0.006662 | 0.98751 | -0.23963 | 0.98757 | -0.2385 | 1.8302
107 | -0.0088422 | -0.0022142 | 0.0088446 | 0.0022153 | 2.4191e-06 | 1.083e-06 | 0.013322 | 0.013322 | 0.013322 | 0.98757 | -0.2385 | 0.98786 | -0.23276 | 3.66
108 | -0.01083 | -0.002713 | 0.010834 | 0.0027149 | 3.7017e-06 | 1.894e-06 | 0.016313 | 0.016313 | 0.016313 | 0.98786 | -0.23276 | 0.98823 | -0.22558 | 4.4817
109 | -0.015334 | -0.0038477 | 0.015339 | 0.0038506 | 4.9992e-06 | 2.9003e-06 | 0.02349 | 0.02349 | 0.02349 | 0.97144 | -0.55195 | 0.97179 | -0.54511 | 6.4532
110 | 0.014503 | 0.0036395 | -0.014489 | -0.0036313 | 1.4217e-05 | 8.1492e-06 | 0.022217 | 0.022218 | 0.022218 | 0.97144 | -0.55195 | 0.9704 | -0.57253 | 6.1038
111 | -0.015647 | -0.0039277 | 0.015653 | 0.0039312 | 5.9126e-06 | 3.4437e-06 | 0.023961 | 0.023961 | 0.023961 | 0.97179 | -0.54511 | 0.97219 | -0.53719 | 6.5827
112 | -0.016744 | -0.0042046 | 0.016749 | 0.0042075 | 4.9067e-06 | 2.8932e-06 | 0.025631 | 0.025631 | 0.025631 | 0.97219 | -0.53719 | 0.9725 | -0.53105 | 7.0415
113 | -0.017174 | -0.0043141 | 0.017186 | 0.0043214 | 1.2414e-05 | 7.3497e-06 | 0.026281 | 0.026281 | 0.026281 | 0.9725 | -0.53105 | 0.97327 | -0.51592 | 7.2202
114 | 0.001308 | 0.00032582 | -0.0013078 | -0.00032716 | 1.7515e-07 | -1.3397e-06 | 0.0019991 | 0.0019996 | 0.0019996 | 0.97327 | -0.51592 | 0.97313 | -0.51874 | 0.54934
115 | -0.02722 | -0.0068226 | 0.02727 | 0.0068538 | 5.0267e-05 | 3.1207e-05 | 0.041616 | 0.041616 | 0.041616 | 0.97327 | -0.51592 | 0.97523 | -0.47723 | 11.433
116 | 0.0013078 | 0.00032716 | -0.0013077 | -0.00032774 | 7.5609e-08 | -5.7799e-07 | 0.0019996 | 0.0019998 | 0.0019998 | 0.97313 | -0.51874 | 0.97306 | -0.51995 | 0.5494
117 | -0.036747 | -0.0092291 | 0.036776 | 0.0092468 | 2.8252e-05 | 1.7782e-05 | 0.056076 | 0.056076 | 0.056076 | 0.97523 | -0.47723 | 0.97605 | -0.46113 | 15.4056
118 | 0.00048672 | 0.00012197 | -0.00048672 | -0.00012198 | 2.6299e-10 | -1.5557e-08 | 0.0007443 | 0.0007443 | 0.0007443 | 0.97306 | -0.51995 | 0.97306 | -0.51996 | 0.20448
119 | 0.0017575 | 0.00043741 | -0.0017574 | -0.00043753 | 3.0691e-08 | -1.2091e-07 | 0.0026879 | 0.002688 | 0.002688 | 0.97252 | -0.53083 | 0.9725 | -0.53119 | 0.73846
120 | -0.043339 | -0.010892 | 0.043376 | 0.010915 | 3.6542e-05 | 2.3108e-05 | 0.066082 | 0.066082 | 0.066082 | 0.97605 | -0.46113 | 0.97695 | -0.44349 | 18.1545
121 | 0.0016061 | 0.00040162 | -0.001606 | -0.00040249 | 1.8013e-07 | -8.7157e-07 | 0.0024572 | 0.0024576 | 0.0024576 | 0.9725 | -0.53119 | 0.97238 | -0.53355 | 0.67515
122 | 0.0001513 | 3.5913e-05 | -0.0001513 | -3.7919e-05 | 3.2433e-09 | -2.0063e-06 | 0.0002308 | 0.00023151 | 0.00023151 | 0.9725 | -0.53119 | 0.97247 | -0.53165 | 0.063601
123 | -0.047517 | -0.011953 | 0.047537 | 0.011966 | 2.006e-05 | 1.2711e-05 | 0.07239 | 0.07239 | 0.07239 | 0.97695 | -0.44349 | 0.9774 | -0.43466 | 19.8874
124 | -0.053925 | -0.013567 | 0.053949 | 0.013581 | 2.3454e-05 | 1.4894e-05 | 0.082116 | 0.082116 | 0.082116 | 0.9774 | -0.43466 | 0.97786 | -0.42556 | 22.5593
125 | -0.057516 | -0.014476 | 0.057568 | 0.014508 | 5.1749e-05 | 3.2893e-05 | 0.087544 | 0.087544 | 0.087544 | 0.97786 | -0.42556 | 0.97882 | -0.40675 | 24.0506
126 | -0.059651 | -0.01503 | 0.059686 | 0.015053 | 3.5793e-05 | 2.2324e-05 | 0.09071 | 0.09071 | 0.09071 | 0.97882 | -0.40675 | 0.97946 | -0.39421 | 12.4602
127 | -0.063445 | -0.015995 | 0.063453 | 0.016 | 7.9511e-06 | 4.9739e-06 | 0.09642 | 0.09642 | 0.09642 | 0.97946 | -0.39421 | 0.9796 | -0.39159 | 13.2445
128 | 0.032165 | 0.0080816 | -0.032144 | -0.0080685 | 2.0929e-05 | 1.31e-05 | 0.048823 | 0.048823 | 0.048823 | 0.98046 | -0.37482 | 0.97976 | -0.38846 | 13.413
129 | 0.028775 | 0.0072242 | -0.028759 | -0.0072143 | 1.599e-05 | 9.9526e-06 | 0.043707 | 0.043707 | 0.043707 | 0.97976 | -0.38846 | 0.97917 | -0.40012 | 12.0075
130 | 0.024416 | 0.0061257 | -0.024409 | -0.0061213 | 7.1872e-06 | 4.4248e-06 | 0.037107 | 0.037107 | 0.037107 | 0.97917 | -0.40012 | 0.97885 | -0.40629 | 10.1941
131 | 0.021783 | 0.0054631 | -0.021774 | -0.0054576 | 9.0295e-06 | 5.503e-06 | 0.033114 | 0.033115 | 0.033115 | 0.97885 | -0.40629 | 0.97841 | -0.41499 | 9.0974
132 | 0.018288 | 0.004584 | -0.018286 | -0.0045831 | 1.4212e-06 | 8.4806e-07 | 0.027813 | 0.027813 | 0.027813 | 0.97841 | -0.41499 | 0.97833 | -0.41663 | 7.641
133 | 0.0098893 | 0.0024786 | -0.009889 | -0.0024784 | 3.4733e-07 | 1.7089e-07 | 0.015041 | 0.015042 | 0.015042 | 0.97833 | -0.41663 | 0.97829 | -0.41736 | 4.1323
134 | 0.0064032 | 0.0016048 | -0.0064028 | -0.0016047 | 4.7703e-07 | 1.3694e-07 | 0.0097396 | 0.0097396 | 0.0097396 | 0.97829 | -0.41736 | 0.97821 | -0.41893 | 2.6757
135 | -0.0076931 | -0.0019278 | 0.0076952 | 0.0019286 | 2.1118e-06 | 7.9717e-07 | 0.011496 | 0.011496 | 0.011496 | 0.99572 | -0.081248 | 0.99602 | -0.075486 | 3.1584
136 | 0.0065864 | 0.0016504 | -0.0065855 | -0.0016502 | 8.5024e-07 | 2.3978e-07 | 0.0098426 | 0.0098427 | 0.0098427 | 0.99572 | -0.081248 | 0.99558 | -0.083958 | 2.704
137 | -0.010776 | -0.0027007 | 0.010778 | 0.0027018 | 2.3336e-06 | 1.1809e-06 | 0.016099 | 0.016099 | 0.016099 | 0.99602 | -0.075486 | 0.99626 | -0.070941 | 4.4227
138 | 0.0041909 | 0.00105 | -0.0041905 | -0.0010502 | 4.7162e-07 | -1.1493e-07 | 0.0062638 | 0.0062639 | 0.0062639 | 0.99558 | -0.083958 | 0.99546 | -0.086321 | 1.7209
139 | -0.015083 | -0.0037807 | 0.015084 | 0.0037812 | 8.7751e-07 | 5.0156e-07 | 0.022528 | 0.022528 | 0.022528 | 0.99626 | -0.070941 | 0.99632 | -0.06972 | 6.189
140 | 0.0031737 | 0.00079534 | -0.0031737 | -0.0007954 | 6.6912e-08 | -6.0242e-08 | 0.0047441 | 0.0047441 | 0.0047441 | 0.99546 | -0.086321 | 0.99544 | -0.086764 | 1.3033
141 | 0.0034395 | 0.00086185 | -0.0034393 | -0.00086198 | 1.9106e-07 | -1.2915e-07 | 0.0051369 | 0.005137 | 0.005137 | 0.99632 | -0.06972 | 0.99626 | -0.070886 | 1.4113
142 | 0.005217 | 0.0013074 | -0.0052163 | -0.0013073 | 6.7505e-07 | 5.0055e-08 | 0.0078125 | 0.0078126 | 0.0078126 | 0.99365 | -0.12037 | 0.99351 | -0.12308 | 2.1463
143 | 0.0029783 | 0.00074631 | -0.0029782 | -0.00074641 | 8.7469e-08 | -9.8301e-08 | 0.0044426 | 0.0044426 | 0.0044426 | 0.99755 | -0.046891 | 0.99752 | -0.047508 | 1.2205
144 | 0.0037642 | 0.00094324 | -0.003764 | -0.00094334 | 2.1313e-07 | -9.8953e-08 | 0.0056147 | 0.0056148 | 0.0056148 | 0.99758 | -0.046337 | 0.99752 | -0.047526 | 1.5425

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26422 | 0.067223

## res_load
| p_mw | q_mvar
0 | 0.011953 | 0.0029957
1 | 0.0052078 | 0.0013052
2 | 0.0095952 | 0.0024048
3 | 0.0039878 | 0.00099945
4 | 0.0036209 | 0.00090749
5 | 0.0049707 | 0.0012458
6 | 0.0022827 | 0.00057209
7 | 0.0055473 | 0.0013903
8 | 0.0028981 | 0.00072633
9 | 0.00032462 | 8.1358e-05
10 | 0.00040014 | 0.00010029
11 | 0.00032963 | 8.2613e-05
12 | 0.00098212 | 0.00024614
13 | 0.0014264 | 0.0003575
14 | 0.00079914 | 0.00020028
15 | 0.0015994 | 0.00040086
16 | 0.021039 | 0.0052728
17 | 0.00017938 | 4.4956e-05
18 | 0.00042188 | 0.00010573
19 | 0.0003377 | 8.4635e-05
20 | 0.00050473 | 0.0001265
21 | 0.00016312 | 4.0881e-05
22 | 0.00057353 | 0.00014374
23 | 0.00026579 | 6.6613e-05
24 | 0.00010301 | 2.5817e-05
25 | 0.00023323 | 5.8453e-05
26 | 0.00019224 | 4.818e-05
27 | 0.0013783 | 0.00034544
28 | 0.00094903 | 0.00023785
29 | 0.0010776 | 0.00027007
30 | 0.00018744 | 4.6976e-05
31 | 0.0012274 | 0.00030762
32 | 0.00024871 | 6.2331e-05
33 | 0.00050862 | 0.00012747
34 | 0.0011465 | 0.00028734
35 | 0.001411 | 0.00035362
36 | 0.00091711 | 0.00022985
37 | 0.00059631 | 0.00014945
38 | 0.00016258 | 4.0746e-05
39 | 0.00053151 | 0.00013321
40 | 0.00063647 | 0.00015952
41 | 0.0010775 | 0.00027004
42 | 0.00044376 | 0.00011122
43 | 0.00086867 | 0.00021771
44 | 0.0012688 | 0.00031798
45 | 0.00030002 | 7.5192e-05
46 | 0.0012003 | 0.00030082
47 | 0.003219 | 0.00080676
48 | 0.001377 | 0.00034511
49 | 0.0012843 | 0.00032187
50 | 0.00079715 | 0.00019978
51 | 0.0011144 | 0.00027929
52 | 0.00094395 | 0.00023658
53 | 0.00071749 | 0.00017982
54 | 0.0012569 | 0.00031502
55 | 0.00034222 | 8.5769e-05
56 | 0.0018034 | 0.00045198
57 | 0.00071598 | 0.00017944
58 | 0.0011167 | 0.00027988
59 | 0.0010251 | 0.00025691
60 | 0.00091748 | 0.00022994
61 | 0.0013932 | 0.00034918
62 | 0.0044172 | 0.001107
63 | 0.00038526 | 9.6555e-05
64 | 0.00043429 | 0.00010884
65 | 0.00033363 | 8.3615e-05
66 | 0.00027237 | 6.8262e-05
67 | 0.00014527 | 3.6407e-05
68 | 0.00032925 | 8.2518e-05
69 | 0.00030383 | 7.6148e-05
70 | 0.0031187 | 0.00078161
71 | 0.0013019 | 0.00032629
72 | 0.0019859 | 0.00049771
73 | 0.0018426 | 0.0004618
74 | 0.00083066 | 0.00020818
75 | 0.00030792 | 7.7173e-05
76 | 0.014489 | 0.0036313
77 | 0.0010911 | 0.00027345
78 | 0.00042515 | 0.00010655
79 | 0.0094773 | 0.0023752
80 | 0.00082102 | 0.00020577
81 | 0.0018319 | 0.00045912
82 | 0.0065634 | 0.0016449
83 | 0.00048672 | 0.00012198
84 | 0.0041415 | 0.0010379
85 | 0.001606 | 0.00040249
86 | 0.0001513 | 3.7919e-05
87 | 0.0063882 | 0.001601
88 | 0.0035673 | 0.00089404
89 | 0.0020829 | 0.00052201
90 | 0.0037585 | 0.00094197
91 | 0.0035935 | 0.00090062
92 | 0.0021993 | 0.00055119
93 | 0.0033686 | 0.00084425
94 | 0.0043435 | 0.0010886
95 | 0.0026262 | 0.00065818
96 | 0.0034857 | 0.00087361
97 | 0.0083971 | 0.0021045
98 | 0.0034857 | 0.00087361
99 | 0.0064028 | 0.0016047
100 | 0.0011067 | 0.00027737
101 | 0.0030806 | 0.00077208
102 | 0.0023946 | 0.00060014
103 | 0.0043046 | 0.0010788
104 | 0.0010167 | 0.00025482
105 | 0.0031737 | 0.0007954
106 | 0.0034393 | 0.00086198
107 | 0.0011742 | 0.00029428
108 | 0.0029782 | 0.00074641
109 | 0.0021134 | 0.00052966
110 | 0.003764 | 0.00094334
111 | 0.0052163 | 0.0013073

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1