## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1509-15_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1509-15_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1509-15_0_2_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1509-15_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1509-15_0_2_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_1509-15_0_2_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1509-15_0_2_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1509-15_0_2_node_25 | 0.4 | n |  | TRUE
8 | bus_LV_1509-15_0_2_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_1509-15_0_2_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1509-15_0_2_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1509-15_0_2_node_40 | 0.4 | n |  | TRUE
12 | bus_LV_1509-15_0_2_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_1509-15_0_2_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1509-15_0_2_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_1509-15_0_2_node_36 | 0.4 | n |  | TRUE
16 | bus_LV_1509-15_0_2_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_1509-15_0_2_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1509-15_0_2_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1509-15_0_2_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_1509-15_0_2_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_1509-15_0_2_node_35 | 0.4 | n |  | TRUE
22 | bus_LV_1509-15_0_2_node_8 | 0.4 | n |  | TRUE
23 | bus_LV_1509-15_0_2_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_1509-15_0_2_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_1509-15_0_2_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_1509-15_0_2_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_1509-15_0_2_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1509-15_0_2_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1509-15_0_2_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_1509-15_0_2_node_13 | 0.4 | n |  | TRUE
31 | bus_LV_1509-15_0_2_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_1509-15_0_2_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1509-15_0_2_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_1509-15_0_2_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1509-15_0_2_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_1509-15_0_2_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_1509-15_0_2_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_1509-15_0_2_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_1509-15_0_2_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1509-15_0_2_node_37 | 0.4 | n |  | TRUE
41 | bus_MV_136_1_node_193 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1509-15_0_2_load_0 | 0 | 0.0017635 | 0.00044198 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1509-15_0_2_load_3 | 2 | 0.0014351 | 0.00035968 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1509-15_0_2_load_7 | 6 | 0.0065225 | 0.0016347 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1509-15_0_2_load_22 | 8 | 0.0051349 | 0.0012869 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1509-15_0_2_load_19 | 9 | 0.009774 | 0.0024496 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1509-15_0_2_load_40 | 11 | 0.0061159 | 0.0015328 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1509-15_0_2_load_39 | 12 | 0.0025464 | 0.0006382 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1509-15_0_2_load_23 | 14 | 0.011144 | 0.002793 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1509-15_0_2_load_36 | 15 | 0.0035669 | 0.00089396 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1509-15_0_2_load_17 | 17 | 0.0045519 | 0.0011408 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1509-15_0_2_load_20 | 18 | 0.0010245 | 0.00025677 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1509-15_0_2_load_38 | 19 | 0.00591 | 0.0014812 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1509-15_0_2_load_24 | 20 | 0.025123 | 0.0062965 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1509-15_0_2_load_35 | 21 | 0.0032703 | 0.00081962 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1509-15_0_2_load_8 | 22 | 0.0052295 | 0.0013106 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1509-15_0_2_load_9 | 23 | 0.0025299 | 0.00063406 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1509-15_0_2_load_10 | 24 | 0.0054866 | 0.0013751 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1509-15_0_2_load_11 | 25 | 0.0024876 | 0.00062346 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1509-15_0_2_load_12 | 26 | 0.0039943 | 0.0010011 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1509-15_0_2_load_18 | 27 | 0.0024579 | 0.00061601 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1509-15_0_2_load_16 | 28 | 0.0078385 | 0.0019645 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1509-15_0_2_load_14 | 29 | 0.0059582 | 0.0014933 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1509-15_0_2_load_13 | 30 | 0.0041854 | 0.001049 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1509-15_0_2_load_15 | 31 | 0.0038382 | 0.00096194 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1509-15_0_2_load_32 | 34 | 0.0037497 | 0.00093975 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1509-15_0_2_load_28 | 35 | 0.0084659 | 0.0021217 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1509-15_0_2_load_33 | 36 | 0.00094627 | 0.00023716 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1509-15_0_2_load_29 | 37 | 0.0041142 | 0.0010311 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1509-15_0_2_load_31 | 38 | 0.004041 | 0.0010128 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1509-15_0_2_load_37 | 40 | 0.01797 | 0.0045038 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1509-15_0_2_line_0 |  | 0 | 1 | 0.016707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1509-15_0_2_line_1 |  | 1 | 2 | 0.01498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1509-15_0_2_line_2 |  | 1 | 3 | 0.04986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1509-15_0_2_line_3 |  | 2 | 7 | 0.0017465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1509-15_0_2_line_4 |  | 3 | 8 | 0.043182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1509-15_0_2_line_5 |  | 3 | 9 | 0.021985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1509-15_0_2_line_6 |  | 4 | 5 | 0.024537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1509-15_0_2_line_7 |  | 4 | 6 | 0.013672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1509-15_0_2_line_8 |  | 5 | 13 | 0.047277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1509-15_0_2_line_9 |  | 5 | 14 | 0.022047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1509-15_0_2_line_10 |  | 6 | 15 | 0.0061754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1509-15_0_2_line_11 |  | 7 | 16 | 0.033797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1509-15_0_2_line_12 |  | 8 | 17 | 0.016404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1509-15_0_2_line_13 |  | 9 | 18 | 0.0099086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1509-15_0_2_line_14 |  | 10 | 11 | 0.023775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1509-15_0_2_line_15 |  | 10 | 12 | 0.0069758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1509-15_0_2_line_16 |  | 12 | 19 | 0.029816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1509-15_0_2_line_17 |  | 13 | 18 | 0.063561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1509-15_0_2_line_18 |  | 14 | 20 | 0.0016255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1509-15_0_2_line_19 |  | 15 | 21 | 0.077081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1509-15_0_2_line_20 |  | 16 | 19 | 0.042841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1509-15_0_2_line_21 |  | 17 | 31 | 0.0017214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1509-15_0_2_line_22 |  | 21 | 39 | 0.0070615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1509-15_0_2_line_23 |  | 22 | 23 | 0.024022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1509-15_0_2_line_24 |  | 22 | 24 | 0.012859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1509-15_0_2_line_25 |  | 23 | 25 | 0.0051201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1509-15_0_2_line_26 |  | 24 | 26 | 0.0076113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1509-15_0_2_line_27 |  | 25 | 27 | 0.0052328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1509-15_0_2_line_28 |  | 26 | 28 | 0.007086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1509-15_0_2_line_29 |  | 28 | 29 | 0.019411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1509-15_0_2_line_30 |  | 29 | 30 | 0.010164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1509-15_0_2_line_31 |  | 30 | 31 | 0.0079218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1509-15_0_2_line_32 |  | 32 | 33 | 0.065881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1509-15_0_2_line_33 |  | 32 | 34 | 0.079265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1509-15_0_2_line_34 |  | 33 | 35 | 0.028268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1509-15_0_2_line_35 |  | 34 | 36 | 0.015203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1509-15_0_2_line_36 |  | 35 | 37 | 0.025586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1509-15_0_2_line_37 |  | 36 | 39 | 0.020919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1509-15_0_2_line_38 |  | 37 | 38 | 0.018738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1509-15_0_2_line_39 |  | 39 | 40 | 0.013487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1509-15_0_2_trafo_20 | 0.63 MVA 20/0.4 kV | 41 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2671260.0884 | 1201620.7678 | 2671250.4541 | 1201634.4168
1 | 2671260.0884 | 1201620.7678 | 2671271.4238 | 1201630.5614
2 | 2671220.5194 | 1201590.4444 | 2671225.115 | 1201593.7901 | 2671234.2612 | 1201600.4253 | 2671260.0884 | 1201620.7678
3 | 2671272.7454 | 1201631.7032 | 2671271.4238 | 1201630.5614
4 | 2671220.5194 | 1201590.4444 | 2671186.0408 | 1201564.4459
5 | 2671220.5194 | 1201590.4444 | 2671213.2904 | 1201599.8529 | 2671207.0886 | 1201607.8498
6 | 2671215.6879 | 1201679.6634 | 2671198.392 | 1201697.1124
7 | 2671215.6879 | 1201679.6634 | 2671224.9677 | 1201689.7033
8 | 2671198.392 | 1201697.1124 | 2671195.2666 | 1201694.9516 | 2671162.5215 | 1201666.2331
9 | 2671198.392 | 1201697.1124 | 2671186.8262 | 1201715.8818
10 | 2671229.1593 | 1201694.2383 | 2671224.9677 | 1201689.7033
11 | 2671272.7454 | 1201631.7032 | 2671298.0108 | 1201609.1797
12 | 2671186.0408 | 1201564.4459 | 2671172.9427 | 1201554.5693
13 | 2671207.0886 | 1201607.8498 | 2671201.0163 | 1201615.6797
14 | 2671223.8836 | 1201546.4132 | 2671231.6655 | 1201544.2713 | 2671246.2936 | 1201550.1492
15 | 2671246.2936 | 1201550.1492 | 2671251.0634 | 1201555.2395
16 | 2671271.4506 | 1201576.9967 | 2671251.0634 | 1201555.2395
17 | 2671162.5215 | 1201666.2331 | 2671166.4905 | 1201660.1989 | 2671201.0163 | 1201615.6797
18 | 2671185.9734 | 1201717.2657 | 2671186.8262 | 1201715.8818
19 | 2671253.4281 | 1201763.8193 | 2671251.0191 | 1201761.4677 | 2671249.0604 | 1201757.8533 | 2671247.2715 | 1201753.407 | 2671245.9562 | 1201748.177 | 2671243.3552 | 1201735.2381 | 2671239.4299 | 1201713.9895 | 2671240.9131 | 1201710.2493 | 2671240.8542 | 1201706.891 | 2671229.1593 | 1201694.2383
20 | 2671298.0108 | 1201609.1797 | 2671279.0815 | 1201591.243 | 2671277.3421 | 1201583.2841 | 2671271.4506 | 1201576.9967
21 | 2671171.5683 | 1201553.5328 | 2671172.9427 | 1201554.5693
22 | 2671259.3649 | 1201767.5376 | 2671254.7434 | 1201765.1032 | 2671253.4281 | 1201763.8193
23 | 2671119.627 | 1201514.3666 | 2671100.4469 | 1201499.9039
24 | 2671119.627 | 1201514.3666 | 2671129.894 | 1201522.1084
25 | 2671100.4469 | 1201499.9039 | 2671096.3588 | 1201496.8213
26 | 2671129.894 | 1201522.1084 | 2671135.9712 | 1201526.6909
27 | 2671096.3588 | 1201496.8213 | 2671092.1807 | 1201493.6708
28 | 2671141.629 | 1201530.9572 | 2671135.9712 | 1201526.6909
29 | 2671141.629 | 1201530.9572 | 2671157.1274 | 1201542.6437
30 | 2671165.2431 | 1201548.7634 | 2671157.1274 | 1201542.6437
31 | 2671171.5683 | 1201553.5328 | 2671165.2431 | 1201548.7634
32 | 2671339.6001 | 1201685.7004 | 2671355.8123 | 1201696.5672 | 2671394.8699 | 1201721.7935
33 | 2671339.6001 | 1201685.7004 | 2671319.1383 | 1201703.7228 | 2671293.4093 | 1201724.9398 | 2671280.6027 | 1201738.4966
34 | 2671394.8699 | 1201721.7935 | 2671404.3628 | 1201708.9435 | 2671412.1884 | 1201703.1335 | 2671413.5951 | 1201701.0124
35 | 2671280.6027 | 1201738.4966 | 2671272.2331 | 1201747.3565 | 2671270.612 | 1201749.8988
36 | 2671413.5951 | 1201701.0124 | 2671421.0249 | 1201689.8087 | 2671419.2769 | 1201681.9497 | 2671415.7343 | 1201679.903
37 | 2671259.3649 | 1201767.5376 | 2671270.612 | 1201749.8988
38 | 2671399.5092 | 1201670.5288 | 2671415.7343 | 1201679.903
39 | 2671259.3649 | 1201767.5376 | 2671257.1282 | 1201775.1044 | 2671258.1968 | 1201780.5983

## bus_geodata
| x | y | coords
0 | 2671250.4541 | 1201634.4168
1 | 2671260.0884 | 1201620.7678
2 | 2671271.4238 | 1201630.5614
3 | 2671220.5194 | 1201590.4444
4 | 2671215.6879 | 1201679.6634
5 | 2671198.392 | 1201697.1124
6 | 2671224.9677 | 1201689.7033
7 | 2671272.7454 | 1201631.7032
8 | 2671186.0408 | 1201564.4459
9 | 2671207.0886 | 1201607.8498
10 | 2671246.2936 | 1201550.1492
11 | 2671223.8836 | 1201546.4132
12 | 2671251.0634 | 1201555.2395
13 | 2671162.5215 | 1201666.2331
14 | 2671186.8262 | 1201715.8818
15 | 2671229.1593 | 1201694.2383
16 | 2671298.0108 | 1201609.1797
17 | 2671172.9427 | 1201554.5693
18 | 2671201.0163 | 1201615.6797
19 | 2671271.4506 | 1201576.9967
20 | 2671185.9734 | 1201717.2657
21 | 2671253.4281 | 1201763.8193
22 | 2671119.627 | 1201514.3666
23 | 2671100.4469 | 1201499.9039
24 | 2671129.894 | 1201522.1084
25 | 2671096.3588 | 1201496.8213
26 | 2671135.9712 | 1201526.6909
27 | 2671092.1807 | 1201493.6708
28 | 2671141.629 | 1201530.9572
29 | 2671157.1274 | 1201542.6437
30 | 2671165.2431 | 1201548.7634
31 | 2671171.5683 | 1201553.5328
32 | 2671339.6001 | 1201685.7004
33 | 2671394.8699 | 1201721.7935
34 | 2671280.6027 | 1201738.4966
35 | 2671413.5951 | 1201701.0124
36 | 2671270.612 | 1201749.8988
37 | 2671415.7343 | 1201679.903
38 | 2671399.5092 | 1201670.5288
39 | 2671259.3649 | 1201767.5376
40 | 2671258.1968 | 1201780.5983
41 | 2671220.5194 | 1201590.4444

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.997 | -0.057557 | 0.0017635 | 0.00044198
1 | 0.99703 | -0.05704 | 0 | 0
2 | 0.99681 | -0.061247 | 0.0014351 | 0.00035968
3 | 0.99783 | -0.041511 | 0 | 0
4 | 0.98975 | -0.19633 | 0 | 0
5 | 0.99094 | -0.17337 | 0 | 0
6 | 0.98909 | -0.20915 | 0.0065225 | 0.0016347
7 | 0.99679 | -0.061693 | 0 | 0
8 | 0.99572 | -0.082188 | 0.0051349 | 0.0012869
9 | 0.99927 | -0.014043 | 0.009774 | 0.0024496
10 | 0.99549 | -0.086601 | 0 | 0
11 | 0.99536 | -0.089159 | 0.0061159 | 0.0015328
12 | 0.99553 | -0.08585 | 0.0025464 | 0.0006382
13 | 0.9948 | -0.099035 | 0 | 0
14 | 0.99021 | -0.18757 | 0.011144 | 0.002793
15 | 0.98883 | -0.21423 | 0.0035669 | 0.00089396
16 | 0.99634 | -0.070339 | 0 | 0
17 | 0.99499 | -0.096203 | 0.0045519 | 0.0011408
18 | 1 | 0 | -0.17323 | -0.043548
19 | 0.99577 | -0.081309 | 0.00591 | 0.0014812
20 | 0.99017 | -0.1883 | 0.025123 | 0.0062965
21 | 0.9858 | -0.27289 | 0.0032703 | 0.00081962
22 | 0.99335 | -0.12797 | 0.0052295 | 0.0013106
23 | 0.99318 | -0.13115 | 0.0025299 | 0.00063406
24 | 0.9935 | -0.12509 | 0.0054866 | 0.0013751
25 | 0.99316 | -0.13159 | 0.0024876 | 0.00062346
26 | 0.99362 | -0.12264 | 0.0039943 | 0.0010011
27 | 0.99315 | -0.13182 | 0.0024579 | 0.00061601
28 | 0.99377 | -0.11987 | 0.0078385 | 0.0019645
29 | 0.9943 | -0.10959 | 0.0059582 | 0.0014933
30 | 0.99463 | -0.10314 | 0.0041854 | 0.001049
31 | 0.99492 | -0.097536 | 0.0038382 | 0.00096194
32 | 0.98363 | -0.31516 | 0 | 0
33 | 0.98262 | -0.33491 | 0 | 0
34 | 0.98485 | -0.29145 | 0.0037497 | 0.00093975
35 | 0.98219 | -0.3434 | 0.0084659 | 0.0021217
36 | 0.98514 | -0.28588 | 0.00094627 | 0.00023716
37 | 0.982 | -0.34717 | 0.0041142 | 0.0010311
38 | 0.98193 | -0.34854 | 0.004041 | 0.0010128
39 | 0.98555 | -0.27787 | 0 | 0
40 | 0.98532 | -0.28222 | 0.01797 | 0.0045038
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0017635 | -0.00044198 | 0.0017636 | 0.00044179 | 4.3401e-08 | -1.901e-07 | 0.0026321 | 0.002632 | 0.0026321 | 0.997 | -0.057557 | 0.99703 | -0.05704 | 0.72309
1 | 0.016027 | 0.0040227 | -0.016024 | -0.0040208 | 3.2148e-06 | 1.8622e-06 | 0.023922 | 0.023922 | 0.023922 | 0.99703 | -0.05704 | 0.99681 | -0.061247 | 6.5721
2 | -0.017791 | -0.0044644 | 0.017804 | 0.0044722 | 1.3184e-05 | 7.7871e-06 | 0.026554 | 0.026554 | 0.026554 | 0.99703 | -0.05704 | 0.99783 | -0.041511 | 7.2951
3 | 0.014589 | 0.0036611 | -0.014589 | -0.0036609 | 3.1068e-07 | 1.7607e-07 | 0.02178 | 0.02178 | 0.02178 | 0.99681 | -0.061247 | 0.99679 | -0.061693 | 5.9835
4 | 0.053878 | 0.013573 | -0.053773 | -0.013506 | 0.0001046 | 6.6379e-05 | 0.080369 | 0.080369 | 0.080369 | 0.99783 | -0.041511 | 0.99572 | -0.082188 | 22.0795
5 | -0.071682 | -0.018045 | 0.071776 | 0.018105 | 9.4254e-05 | 6.0035e-05 | 0.10692 | 0.10692 | 0.10692 | 0.99783 | -0.041511 | 0.99927 | -0.014043 | 29.3745
6 | -0.05288 | -0.013339 | 0.052938 | 0.013376 | 5.8202e-05 | 3.6933e-05 | 0.079532 | 0.079532 | 0.079532 | 0.98975 | -0.19633 | 0.99094 | -0.17337 | 21.8495
7 | 0.05288 | 0.013339 | -0.052848 | -0.013318 | 3.2429e-05 | 2.0579e-05 | 0.079532 | 0.079532 | 0.079532 | 0.98975 | -0.19633 | 0.98909 | -0.20915 | 21.8495
8 | -0.089231 | -0.022481 | 0.08955 | 0.022685 | 0.0003185 | 0.00020323 | 0.13403 | 0.13403 | 0.13403 | 0.99094 | -0.17337 | 0.9948 | -0.099035 | 36.8224
9 | 0.036293 | 0.0091055 | -0.036268 | -0.00909 | 2.4558e-05 | 1.5433e-05 | 0.054502 | 0.054502 | 0.054502 | 0.99094 | -0.17337 | 0.99021 | -0.18757 | 14.973
10 | 0.046325 | 0.011684 | -0.046314 | -0.011677 | 1.1257e-05 | 7.125e-06 | 0.069719 | 0.069719 | 0.069719 | 0.98909 | -0.20915 | 0.98883 | -0.21423 | 19.1537
11 | 0.014589 | 0.0036609 | -0.014583 | -0.0036575 | 6.0122e-06 | 3.4074e-06 | 0.02178 | 0.02178 | 0.02178 | 0.99679 | -0.061693 | 0.99634 | -0.070339 | 5.9836
12 | 0.048638 | 0.012219 | -0.048606 | -0.012199 | 3.251e-05 | 2.0593e-05 | 0.072696 | 0.072696 | 0.072696 | 0.99572 | -0.082188 | 0.99499 | -0.096203 | 19.9714
13 | -0.08155 | -0.020555 | 0.081605 | 0.02059 | 5.4832e-05 | 3.4963e-05 | 0.12148 | 0.12148 | 0.12148 | 0.99927 | -0.014043 | 1 | 0 | 33.373
14 | 0.0061167 | 0.001533 | -0.0061159 | -0.0015328 | 7.4529e-07 | 1.6792e-07 | 0.0091429 | 0.009143 | 0.009143 | 0.99549 | -0.086601 | 0.99536 | -0.089159 | 2.5118
15 | -0.0061167 | -0.001533 | 0.0061169 | 0.001533 | 2.1867e-07 | 4.9251e-08 | 0.0091429 | 0.0091429 | 0.0091429 | 0.99549 | -0.086601 | 0.99553 | -0.08585 | 2.5118
16 | -0.0086633 | -0.0021712 | 0.0086652 | 0.002172 | 1.8748e-06 | 8.121e-07 | 0.012949 | 0.012949 | 0.012949 | 0.99553 | -0.08585 | 0.99577 | -0.081309 | 3.5574
17 | -0.08955 | -0.022685 | 0.089978 | 0.022958 | 0.0004282 | 0.00027322 | 0.13403 | 0.13403 | 0.13403 | 0.9948 | -0.099035 | 1 | 0 | 36.8223
18 | 0.025124 | 0.006297 | -0.025123 | -0.0062965 | 8.6889e-07 | 5.3518e-07 | 0.037755 | 0.037755 | 0.037755 | 0.99021 | -0.18757 | 0.99017 | -0.1883 | 10.3722
19 | 0.042747 | 0.010783 | -0.042627 | -0.010707 | 0.0001197 | 7.5624e-05 | 0.064352 | 0.064352 | 0.064352 | 0.98883 | -0.21423 | 0.9858 | -0.27289 | 17.6792
20 | 0.014583 | 0.0036575 | -0.014575 | -0.0036532 | 7.6211e-06 | 4.3199e-06 | 0.02178 | 0.02178 | 0.02178 | 0.99634 | -0.070339 | 0.99577 | -0.081309 | 5.9836
21 | 0.044054 | 0.011058 | -0.044051 | -0.011056 | 2.8025e-06 | 1.7712e-06 | 0.065888 | 0.065888 | 0.065888 | 0.99499 | -0.096203 | 0.99492 | -0.097536 | 18.1012
22 | 0.039357 | 0.0098875 | -0.039348 | -0.0098816 | 9.3483e-06 | 5.8929e-06 | 0.059416 | 0.059416 | 0.059416 | 0.9858 | -0.27289 | 0.98555 | -0.27787 | 16.323
23 | 0.0074767 | 0.0018739 | -0.0074756 | -0.0018735 | 1.13e-06 | 4.1228e-07 | 0.0112 | 0.0112 | 0.0112 | 0.99335 | -0.12797 | 0.99318 | -0.13115 | 3.077
24 | -0.012706 | -0.0031845 | 0.012708 | 0.0031855 | 1.7469e-06 | 9.5154e-07 | 0.019034 | 0.019034 | 0.019034 | 0.99335 | -0.12797 | 0.9935 | -0.12509 | 5.229
25 | 0.0049457 | 0.0012394 | -0.0049456 | -0.0012394 | 1.0542e-07 | 1.2095e-09 | 0.0074097 | 0.0074097 | 0.0074097 | 0.99318 | -0.13115 | 0.99316 | -0.13159 | 2.0356
26 | -0.018195 | -0.0045606 | 0.018197 | 0.0045618 | 2.1196e-06 | 1.258e-06 | 0.027251 | 0.027251 | 0.027251 | 0.9935 | -0.12509 | 0.99362 | -0.12264 | 7.4866
27 | 0.0024579 | 0.00061596 | -0.0024579 | -0.00061601 | 2.6612e-08 | -5.0682e-08 | 0.0036826 | 0.0036826 | 0.0036826 | 0.99316 | -0.13159 | 0.99315 | -0.13182 | 1.0117
28 | -0.022191 | -0.0055629 | 0.022194 | 0.0055647 | 2.9347e-06 | 1.7864e-06 | 0.033233 | 0.033233 | 0.033233 | 0.99362 | -0.12264 | 0.99377 | -0.11987 | 9.1299
29 | -0.030032 | -0.0075292 | 0.030047 | 0.0075384 | 1.472e-05 | 9.1694e-06 | 0.04497 | 0.04497 | 0.04497 | 0.99377 | -0.11987 | 0.9943 | -0.10959 | 12.3544
30 | -0.036005 | -0.0090316 | 0.036016 | 0.0090386 | 1.1068e-05 | 6.9517e-06 | 0.053887 | 0.053887 | 0.053887 | 0.9943 | -0.10959 | 0.99463 | -0.10314 | 14.804
31 | -0.040202 | -0.010088 | 0.040213 | 0.010094 | 1.0747e-05 | 6.7755e-06 | 0.060148 | 0.060148 | 0.060148 | 0.99463 | -0.10314 | 0.99492 | -0.097536 | 16.5242
32 | 0.016645 | 0.0041793 | -0.01663 | -0.0041701 | 1.5668e-05 | 9.1922e-06 | 0.025183 | 0.025183 | 0.025183 | 0.98363 | -0.31516 | 0.98262 | -0.33491 | 6.9185
33 | -0.016645 | -0.0041793 | 0.016664 | 0.0041904 | 1.8851e-05 | 1.1057e-05 | 0.025183 | 0.025183 | 0.025183 | 0.98363 | -0.31516 | 0.98485 | -0.29145 | 6.9184
34 | 0.01663 | 0.0041701 | -0.016623 | -0.0041662 | 6.7229e-06 | 3.9447e-06 | 0.025183 | 0.025184 | 0.025184 | 0.98262 | -0.33491 | 0.98219 | -0.3434 | 6.9186
35 | -0.020414 | -0.0051301 | 0.020419 | 0.0051334 | 5.4253e-06 | 3.2787e-06 | 0.030848 | 0.030848 | 0.030848 | 0.98485 | -0.29145 | 0.98514 | -0.28588 | 8.4748
36 | 0.0081569 | 0.0020444 | -0.0081555 | -0.0020438 | 1.4653e-06 | 6.1401e-07 | 0.012358 | 0.012358 | 0.012358 | 0.98219 | -0.3434 | 0.982 | -0.34717 | 3.395
37 | -0.021365 | -0.0053706 | 0.021374 | 0.0053755 | 8.1729e-06 | 4.9642e-06 | 0.032277 | 0.032277 | 0.032277 | 0.98514 | -0.28588 | 0.98555 | -0.27787 | 8.8674
38 | 0.0040413 | 0.0010127 | -0.004041 | -0.0010128 | 2.6351e-07 | -6.8398e-08 | 0.0061237 | 0.0061238 | 0.0061238 | 0.982 | -0.34717 | 0.98193 | -0.34854 | 1.6824
39 | 0.017974 | 0.004506 | -0.01797 | -0.0045038 | 3.725e-06 | 2.2121e-06 | 0.027139 | 0.027139 | 0.027139 | 0.98555 | -0.27787 | 0.98532 | -0.28222 | 7.4557

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.17426 | 0.043804

## res_load
| p_mw | q_mvar
0 | 0.0017635 | 0.00044198
1 | 0.0014351 | 0.00035968
2 | 0.0065225 | 0.0016347
3 | 0.0051349 | 0.0012869
4 | 0.009774 | 0.0024496
5 | 0.0061159 | 0.0015328
6 | 0.0025464 | 0.0006382
7 | 0.011144 | 0.002793
8 | 0.0035669 | 0.00089396
9 | 0.0045519 | 0.0011408
10 | 0.0010245 | 0.00025677
11 | 0.00591 | 0.0014812
12 | 0.025123 | 0.0062965
13 | 0.0032703 | 0.00081962
14 | 0.0052295 | 0.0013106
15 | 0.0025299 | 0.00063406
16 | 0.0054866 | 0.0013751
17 | 0.0024876 | 0.00062346
18 | 0.0039943 | 0.0010011
19 | 0.0024579 | 0.00061601
20 | 0.0078385 | 0.0019645
21 | 0.0059582 | 0.0014933
22 | 0.0041854 | 0.001049
23 | 0.0038382 | 0.00096194
24 | 0.0037497 | 0.00093975
25 | 0.0084659 | 0.0021217
26 | 0.00094627 | 0.00023716
27 | 0.0041142 | 0.0010311
28 | 0.004041 | 0.0010128
29 | 0.01797 | 0.0045038

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1