## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1509-22_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1509-22_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1509-22_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1509-22_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1509-22_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1509-22_0_3_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_1509-22_0_3_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_1509-22_0_3_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_1509-22_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1509-22_0_3_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1509-22_0_3_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1509-22_0_3_node_28 | 0.4 | n |  | TRUE
12 | bus_LV_1509-22_0_3_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_1509-22_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1509-22_0_3_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1509-22_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1509-22_0_3_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1509-22_0_3_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_1509-22_0_3_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1509-22_0_3_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_1509-22_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1509-22_0_3_node_7 | 0.4 | n |  | TRUE
22 | bus_LV_1509-22_0_3_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_1509-22_0_3_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_1509-22_0_3_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1509-22_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_1509-22_0_3_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1509-22_0_3_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1509-22_0_3_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1509-22_0_3_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_1509-22_0_3_node_33 | 0.4 | n |  | TRUE
31 | bus_MV_143_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1509-22_0_3_load_0 | 0 | 0.025805 | 0.0064673 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1509-22_0_3_load_1 | 1 | 0.068917 | 0.017272 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1509-22_0_3_load_20 | 9 | 0.0060672 | 0.0015206 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1509-22_0_3_load_28 | 11 | 0.013199 | 0.003308 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1509-22_0_3_load_31 | 12 | 0.033956 | 0.0085102 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1509-22_0_3_load_29 | 17 | 0.037057 | 0.0092874 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1509-22_0_3_load_34 | 18 | 0.0096977 | 0.0024305 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1509-22_0_3_load_30 | 19 | 0.012433 | 0.0031159 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1509-22_0_3_load_16 | 20 | 0.042978 | 0.010771 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1509-22_0_3_load_7 | 21 | 0.019947 | 0.0049992 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1509-22_0_3_load_35 | 22 | 0.0055336 | 0.0013868 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1509-22_0_3_load_36 | 23 | 0.0045499 | 0.0011403 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1509-22_0_3_load_19 | 24 | 0.021304 | 0.0053392 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1509-22_0_3_load_26 | 25 | 0.020359 | 0.0051024 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1509-22_0_3_load_22 | 26 | 0.036967 | 0.0092649 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1509-22_0_3_load_27 | 28 | 0.0072109 | 0.0018072 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1509-22_0_3_load_33 | 30 | 0.011124 | 0.0027879 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1509-22_0_3_line_0 |  | 0 | 1 | 0.059812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1509-22_0_3_line_1 |  | 0 | 2 | 0.047283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1509-22_0_3_line_2 |  | 1 | 3 | 0.042134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1509-22_0_3_line_3 |  | 2 | 4 | 0.026954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1509-22_0_3_line_4 |  | 3 | 5 | 0.059507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1509-22_0_3_line_5 |  | 3 | 6 | 0.17539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1509-22_0_3_line_6 |  | 4 | 7 | 0.015435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1509-22_0_3_line_7 |  | 4 | 8 | 0.056881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1509-22_0_3_line_8 |  | 4 | 9 | 0.021495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1509-22_0_3_line_9 |  | 5 | 12 | 0.039173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1509-22_0_3_line_10 |  | 6 | 19 | 0.039955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1509-22_0_3_line_11 |  | 7 | 22 | 0.039703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1509-22_0_3_line_12 |  | 7 | 23 | 0.002006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1509-22_0_3_line_13 |  | 8 | 10 | 0.033636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1509-22_0_3_line_14 |  | 8 | 11 | 0.019164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1509-22_0_3_line_15 |  | 10 | 20 | 0.055642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1509-22_0_3_line_16 |  | 10 | 21 | 0.070425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1509-22_0_3_line_17 |  | 11 | 16 | 0.048862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_1509-22_0_3_line_18 |  | 12 | 13 | 0.014593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1509-22_0_3_line_19 |  | 13 | 14 | 0.033845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1509-22_0_3_line_20 |  | 14 | 18 | 0.033433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1509-22_0_3_line_21 |  | 15 | 16 | 0.0067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1509-22_0_3_line_22 |  | 15 | 17 | 0.016683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1509-22_0_3_line_23 |  | 17 | 25 | 0.022384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1509-22_0_3_line_24 |  | 20 | 24 | 0.075363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1509-22_0_3_line_25 |  | 25 | 27 | 0.024799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1509-22_0_3_line_26 |  | 26 | 27 | 0.0063421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1509-22_0_3_line_27 |  | 27 | 28 | 0.023887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1509-22_0_3_line_28 |  | 28 | 29 | 0.02884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1509-22_0_3_line_29 |  | 29 | 30 | 0.032006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1509-22_0_3_trafo_29 | 0.63 MVA 20/0.4 kV | 31 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2669826.5876 | 1201758.5476 | 2669839.8209 | 1201758.5866 | 2669846.4965 | 1201760.5102 | 2669854.0383 | 1201771.0158 | 2669856.5266 | 1201773.6687 | 2669858.9079 | 1201775.7089 | 2669862.5534 | 1201777.6972 | 2669866.3429 | 1201779.0756 | 2669870.6379 | 1201780.1932 | 2669877.8419 | 1201781.3911
1 | 2669780.1469 | 1201752.1301 | 2669797.0922 | 1201754.5405 | 2669807.7945 | 1201758.3901 | 2669819.4764 | 1201758.5266 | 2669826.5876 | 1201758.5476
2 | 2669919.6561 | 1201781.4116 | 2669914.899 | 1201782.7123 | 2669908.8232 | 1201783.5195 | 2669899.8299 | 1201783.2364 | 2669888.5572 | 1201782.6153 | 2669878.3332 | 1201781.4728 | 2669877.8419 | 1201781.3911
3 | 2669780.1469 | 1201752.1301 | 2669759.6095 | 1201762.719 | 2669758.6517 | 1201761.3069 | 2669758.1322 | 1201760.8228 | 2669757.496 | 1201760.5485 | 2669756.7578 | 1201760.5399
4 | 2669896.6479 | 1201829.4606 | 2669899.403 | 1201824.2674 | 2669911.0602 | 1201806.3484 | 2669917.91 | 1201797.2786 | 2669925.5685 | 1201788.0515 | 2669920.9239 | 1201782.9941 | 2669919.6561 | 1201781.4116
5 | 2669919.6561 | 1201781.4116 | 2669920.9239 | 1201782.9941 | 2669925.5685 | 1201788.0515 | 2669935.5021 | 1201777.5836 | 2669949.296 | 1201765.7045 | 2669955.9001 | 1201761.3791 | 2669968.9617 | 1201753.5384 | 2669988.5783 | 1201742.9728 | 2670004.1433 | 1201733.9162 | 2670007.4385 | 1201732.0092 | 2670010.7449 | 1201737.5958 | 2670015.3216 | 1201743.8977 | 2670017.3509 | 1201748.0462 | 2670024.0625 | 1201761.8221 | 2670026.6539 | 1201771.2582 | 2670028.2947 | 1201776.0803 | 2670034.7866 | 1201792.3663
6 | 2669742.9243 | 1201767.3715 | 2669755.5293 | 1201760.8035 | 2669756.7578 | 1201760.5399
7 | 2669743.7535 | 1201807.172 | 2669742.1618 | 1201802.684 | 2669739.8997 | 1201796.2982 | 2669739.6164 | 1201793.8379 | 2669739.5093 | 1201790.6235 | 2669739.8202 | 1201787.4586 | 2669740.5778 | 1201783.8541 | 2669741.8313 | 1201780.8002 | 2669743.9896 | 1201777.1677 | 2669749.085 | 1201771.0123 | 2669753.2163 | 1201767.2471 | 2669759.6095 | 1201762.719 | 2669758.6517 | 1201761.3069 | 2669758.1322 | 1201760.8228 | 2669757.496 | 1201760.5485 | 2669756.7578 | 1201760.5399
8 | 2669756.7578 | 1201760.5399 | 2669757.9256 | 1201759.6085 | 2669759.5977 | 1201758.5163 | 2669761.4424 | 1201757.6262 | 2669775.5514 | 1201750.1741
9 | 2669896.6479 | 1201829.4606 | 2669884.8294 | 1201830.6008 | 2669876.8808 | 1201834.0544 | 2669870.3032 | 1201851.4886
10 | 2670034.7866 | 1201792.3663 | 2670014.704 | 1201801.7811 | 2670005.1675 | 1201805.6384 | 2669998.0476 | 1201803.3203
11 | 2669742.9243 | 1201767.3715 | 2669721.9117 | 1201778.244 | 2669716.0865 | 1201768.0255 | 2669712.2121 | 1201770.0037
12 | 2669741.9936 | 1201765.5929 | 2669742.9243 | 1201767.3715
13 | 2669743.7535 | 1201807.172 | 2669739.9228 | 1201808.0056 | 2669736.5681 | 1201809.8009 | 2669733.1557 | 1201812.6294 | 2669730.8071 | 1201815.6038 | 2669729.1837 | 1201818.3977 | 2669727.982 | 1201821.5856 | 2669727.35 | 1201824.8691 | 2669727.3228 | 1201827.8484 | 2669728.1281 | 1201832.5384
14 | 2669743.7535 | 1201807.172 | 2669749.3022 | 1201807.1701 | 2669753.439 | 1201808.1412 | 2669757.126 | 1201809.8297 | 2669760.7839 | 1201812.7074 | 2669761.2141 | 1201813.2037
15 | 2669728.1281 | 1201832.5384 | 2669722.1716 | 1201834.8814 | 2669704.0566 | 1201864.8883 | 2669693.139 | 1201873.9538
16 | 2669728.1281 | 1201832.5384 | 2669728.5618 | 1201834.5113 | 2669728.5149 | 1201835.9227 | 2669728.0864 | 1201837.4187 | 2669727.4375 | 1201838.8898 | 2669725.9591 | 1201841.652 | 2669705.0651 | 1201875.6511 | 2669693.9362 | 1201893.2109
17 | 2669796.878 | 1201843.87 | 2669782.0129 | 1201836.7254 | 2669776.4414 | 1201833.4695 | 2669771.2635 | 1201829.7512 | 2669769.0092 | 1201827.2567 | 2669767.3724 | 1201824.6805 | 2669765.5338 | 1201820.4898 | 2669764.4991 | 1201817.8428 | 2669762.9843 | 1201815.2458 | 2669761.2141 | 1201813.2037
18 | 2669868.0872 | 1201864.8592 | 2669866.3318 | 1201862.0147 | 2669870.3032 | 1201851.4886
19 | 2669845.1842 | 1201882.4911 | 2669846.1126 | 1201880.5563 | 2669847.484 | 1201877.8374 | 2669849.8178 | 1201872.8727 | 2669850.6294 | 1201871.159 | 2669851.6904 | 1201868.9478 | 2669862.4348 | 1201870.4743 | 2669868.0872 | 1201864.8592
20 | 2669845.1842 | 1201882.4911 | 2669812.7823 | 1201890.7294
21 | 2669802.933 | 1201846.7758 | 2669796.878 | 1201843.87
22 | 2669802.933 | 1201846.7758 | 2669803.3233 | 1201845.2906 | 2669808.8442 | 1201831.185
23 | 2669816.7211 | 1201810.2336 | 2669811.3023 | 1201824.9047 | 2669808.8442 | 1201831.185
24 | 2669652.2292 | 1201935.5826 | 2669682.262 | 1201880.855 | 2669689.7305 | 1201876.7841 | 2669693.139 | 1201873.9538
25 | 2669821.4532 | 1201786.7112 | 2669822.943 | 1201793.3882 | 2669816.7211 | 1201810.2336
26 | 2669821.4532 | 1201786.7112 | 2669816.8578 | 1201787.8471 | 2669815.3137 | 1201788.2976
27 | 2669821.4532 | 1201786.7112 | 2669826.4156 | 1201786.7248 | 2669835.5832 | 1201787.0765 | 2669837.6112 | 1201787.4338 | 2669839.8856 | 1201788.2053 | 2669842.0701 | 1201789.5094 | 2669844.1198 | 1201791.2677 | 2669844.1515 | 1201791.2994
28 | 2669857.3327 | 1201812.1237 | 2669851.4392 | 1201810.376 | 2669849.4939 | 1201809.4527 | 2669848.1738 | 1201808.4366 | 2669847.4261 | 1201807.2828 | 2669847.2486 | 1201806.1911 | 2669847.5056 | 1201804.393 | 2669848.3499 | 1201801.8347 | 2669848.513 | 1201799.6019 | 2669848.1949 | 1201797.5192 | 2669847.1903 | 1201794.9058 | 2669846.0081 | 1201793.1576 | 2669844.1515 | 1201791.2994
29 | 2669879.28 | 1201801.3849 | 2669875.103 | 1201812.3093 | 2669874.3192 | 1201814.2458 | 2669873.492 | 1201815.3368 | 2669872.5341 | 1201815.8926 | 2669871.3899 | 1201816.1127 | 2669870.1966 | 1201815.9653 | 2669857.3327 | 1201812.1237

## bus_geodata
| x | y | coords
0 | 2669826.5876 | 1201758.5476
1 | 2669877.8419 | 1201781.3911
2 | 2669780.1469 | 1201752.1301
3 | 2669919.6561 | 1201781.4116
4 | 2669756.7578 | 1201760.5399
5 | 2669896.6479 | 1201829.4606
6 | 2670034.7866 | 1201792.3663
7 | 2669742.9243 | 1201767.3715
8 | 2669743.7535 | 1201807.172
9 | 2669775.5514 | 1201750.1741
10 | 2669728.1281 | 1201832.5384
11 | 2669761.2141 | 1201813.2037
12 | 2669870.3032 | 1201851.4886
13 | 2669868.0872 | 1201864.8592
14 | 2669845.1842 | 1201882.4911
15 | 2669802.933 | 1201846.7758
16 | 2669796.878 | 1201843.87
17 | 2669808.8442 | 1201831.185
18 | 2669812.7823 | 1201890.7294
19 | 2669998.0476 | 1201803.3203
20 | 2669693.139 | 1201873.9538
21 | 2669693.9362 | 1201893.2109
22 | 2669712.2121 | 1201770.0037
23 | 2669741.9936 | 1201765.5929
24 | 2669652.2292 | 1201935.5826
25 | 2669816.7211 | 1201810.2336
26 | 2669815.3137 | 1201788.2976
27 | 2669821.4532 | 1201786.7112
28 | 2669844.1515 | 1201791.2994
29 | 2669857.3327 | 1201812.1237
30 | 2669879.28 | 1201801.3849
31 | 2669802.933 | 1201846.7758

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97928 | -0.39702 | 0.025805 | 0.0064673
1 | 0.9758 | -0.46522 | 0.068917 | 0.017272
2 | 0.9826 | -0.33243 | 0 | 0
3 | 0.9747 | -0.48688 | 0 | 0
4 | 0.98449 | -0.29581 | 0 | 0
5 | 0.97348 | -0.51074 | 0 | 0
6 | 0.97266 | -0.52698 | 0 | 0
7 | 0.98435 | -0.29861 | 0 | 0
8 | 0.98891 | -0.21078 | 0 | 0
9 | 0.98437 | -0.29815 | 0.0060672 | 0.0015206
10 | 0.98629 | -0.26141 | 0 | 0
11 | 0.99114 | -0.16797 | 0.013199 | 0.003308
12 | 0.97189 | -0.54224 | 0.033956 | 0.0085102
13 | 0.97176 | -0.54486 | 0 | 0
14 | 0.97145 | -0.55092 | 0 | 0
15 | 0.99795 | -0.038524 | 0 | 0
16 | 0.99713 | -0.05404 | 0 | 0
17 | 1 | 0 | -0.34711 | -0.088667
18 | 0.97115 | -0.55691 | 0.0096977 | 0.0024305
19 | 0.9722 | -0.53613 | 0.012433 | 0.0031159
20 | 0.98299 | -0.32572 | 0.042978 | 0.010771
21 | 0.985 | -0.28662 | 0.019947 | 0.0049992
22 | 0.98414 | -0.30256 | 0.0055336 | 0.0013868
23 | 0.98434 | -0.29877 | 0.0045499 | 0.0011403
24 | 0.98151 | -0.35472 | 0.021304 | 0.0053392
25 | 0.99846 | -0.029566 | 0.020359 | 0.0051024
26 | 0.997 | -0.057684 | 0.036967 | 0.0092649
27 | 0.99721 | -0.053574 | 0 | 0
28 | 0.99681 | -0.061254 | 0.0072109 | 0.0018072
29 | 0.99652 | -0.066884 | 0 | 0
30 | 0.9962 | -0.073135 | 0.011124 | 0.0027879
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.12562 | 0.031716 | -0.12521 | -0.031456 | 0.00040898 | 0.00026025 | 0.19097 | 0.19097 | 0.19097 | 0.97928 | -0.39702 | 0.9758 | -0.46522 | 26.2317
1 | -0.15143 | -0.038184 | 0.1519 | 0.038483 | 0.00046971 | 0.00029942 | 0.23018 | 0.23018 | 0.23018 | 0.97928 | -0.39702 | 0.9826 | -0.33243 | 31.6177
2 | 0.056296 | 0.014184 | -0.056238 | -0.014148 | 5.8259e-05 | 3.6234e-05 | 0.085874 | 0.085874 | 0.085874 | 0.9758 | -0.46522 | 0.9747 | -0.48688 | 11.7959
3 | -0.1519 | -0.038483 | 0.15216 | 0.038654 | 0.00026776 | 0.00017068 | 0.23018 | 0.23018 | 0.23018 | 0.9826 | -0.33243 | 0.98449 | -0.29581 | 31.6176
4 | 0.043776 | 0.011016 | -0.043726 | -0.010985 | 4.9858e-05 | 3.0427e-05 | 0.066847 | 0.066847 | 0.066847 | 0.9747 | -0.48688 | 0.97348 | -0.51074 | 9.1823
5 | 0.012462 | 0.0031319 | -0.012438 | -0.0031189 | 2.3814e-05 | 1.3059e-05 | 0.019028 | 0.019029 | 0.019029 | 0.9747 | -0.48688 | 0.97266 | -0.52698 | 5.2276
6 | 0.010086 | 0.002528 | -0.010085 | -0.0025273 | 1.3451e-06 | 6.6465e-07 | 0.015245 | 0.015245 | 0.015245 | 0.98449 | -0.29581 | 0.98435 | -0.29861 | 4.1881
7 | -0.16832 | -0.042703 | 0.16901 | 0.043144 | 0.00069129 | 0.00044097 | 0.25459 | 0.25459 | 0.25459 | 0.98449 | -0.29581 | 0.98891 | -0.21078 | 34.9714
8 | 0.0060679 | 0.0015208 | -0.0060672 | -0.0015206 | 6.7804e-07 | 1.6065e-07 | 0.0091714 | 0.0091715 | 0.0091715 | 0.98449 | -0.29581 | 0.98437 | -0.29815 | 2.5197
9 | 0.043726 | 0.010985 | -0.04366 | -0.010944 | 6.5643e-05 | 4.1525e-05 | 0.066847 | 0.066847 | 0.066847 | 0.97348 | -0.51074 | 0.97189 | -0.54224 | 18.3646
10 | 0.012438 | 0.0031189 | -0.012433 | -0.0031159 | 5.4252e-06 | 2.9765e-06 | 0.019029 | 0.019029 | 0.019029 | 0.97266 | -0.52698 | 0.9722 | -0.53613 | 5.2277
11 | 0.0055346 | 0.001387 | -0.0055336 | -0.0013868 | 1.0422e-06 | 1.6242e-07 | 0.0083665 | 0.0083667 | 0.0083667 | 0.98435 | -0.29861 | 0.98414 | -0.30256 | 2.2985
12 | 0.0045499 | 0.0011403 | -0.0045499 | -0.0011403 | 3.5587e-08 | -2.7239e-09 | 0.006878 | 0.006878 | 0.006878 | 0.98435 | -0.29861 | 0.98434 | -0.29877 | 1.8896
13 | 0.084685 | 0.021399 | -0.08448 | -0.021268 | 0.00020501 | 0.00013078 | 0.12749 | 0.12749 | 0.12749 | 0.98891 | -0.21078 | 0.98629 | -0.26141 | 35.0243
14 | -0.25369 | -0.064542 | 0.25422 | 0.064878 | 0.00052456 | 0.00033523 | 0.38208 | 0.38208 | 0.38208 | 0.98891 | -0.21078 | 0.99114 | -0.16797 | 52.4834
15 | 0.064509 | 0.016254 | -0.064311 | -0.016128 | 0.00019777 | 0.00012586 | 0.097356 | 0.097356 | 0.097356 | 0.98629 | -0.26141 | 0.98299 | -0.32572 | 26.7461
16 | 0.019971 | 0.0050136 | -0.019947 | -0.0049992 | 2.398e-05 | 1.4449e-05 | 0.030133 | 0.030133 | 0.030133 | 0.98629 | -0.26141 | 0.985 | -0.28662 | 8.2784
17 | -0.26742 | -0.068186 | 0.2689 | 0.069131 | 0.0014798 | 0.0009458 | 0.4019 | 0.40189 | 0.4019 | 0.99114 | -0.16797 | 0.99713 | -0.05404 | 55.2054
18 | 0.0097045 | 0.0024338 | -0.0097033 | -0.0024332 | 1.2082e-06 | 5.9243e-07 | 0.014859 | 0.014859 | 0.014859 | 0.97189 | -0.54224 | 0.97176 | -0.54486 | 4.0821
19 | 0.0097033 | 0.0024332 | -0.0097005 | -0.0024318 | 2.8022e-06 | 1.3742e-06 | 0.014859 | 0.014859 | 0.014859 | 0.97176 | -0.54486 | 0.97145 | -0.55092 | 4.0821
20 | 0.0097005 | 0.0024318 | -0.0096977 | -0.0024305 | 2.7681e-06 | 1.3578e-06 | 0.014859 | 0.014859 | 0.014859 | 0.97145 | -0.55092 | 0.97115 | -0.55691 | 4.0822
21 | 0.2691 | 0.069261 | -0.2689 | -0.069131 | 0.00020291 | 0.00012969 | 0.40189 | 0.40189 | 0.40189 | 0.99795 | -0.038524 | 0.99713 | -0.05404 | 55.2053
22 | -0.2691 | -0.069261 | 0.26961 | 0.069584 | 0.00050525 | 0.00032292 | 0.40189 | 0.40189 | 0.40189 | 0.99795 | -0.038524 | 1 | 0 | 55.2053
23 | 0.075851 | 0.019083 | -0.075744 | -0.019014 | 0.00010698 | 6.8175e-05 | 0.11289 | 0.11289 | 0.11289 | 1 | 0 | 0.99846 | -0.029566 | 31.0148
24 | 0.021333 | 0.0053571 | -0.021304 | -0.0053392 | 2.9479e-05 | 1.7913e-05 | 0.032297 | 0.032297 | 0.032297 | 0.98299 | -0.32572 | 0.98151 | -0.35472 | 8.8729
25 | 0.055386 | 0.013912 | -0.055322 | -0.013872 | 6.3377e-05 | 4.0237e-05 | 0.082553 | 0.082553 | 0.082553 | 0.99846 | -0.029566 | 0.99721 | -0.053574 | 22.6794
26 | -0.036967 | -0.0092649 | 0.036975 | 0.0092694 | 7.2397e-06 | 4.5507e-06 | 0.055173 | 0.055173 | 0.055173 | 0.997 | -0.057684 | 0.99721 | -0.053574 | 15.1575
27 | 0.018348 | 0.0046024 | -0.018341 | -0.0045984 | 6.7151e-06 | 3.9862e-06 | 0.02738 | 0.02738 | 0.02738 | 0.99721 | -0.053574 | 0.99681 | -0.061254 | 7.5219
28 | 0.01113 | 0.0027912 | -0.011127 | -0.0027896 | 2.9858e-06 | 1.5351e-06 | 0.016616 | 0.016616 | 0.016616 | 0.99681 | -0.061254 | 0.99652 | -0.066884 | 4.5647
29 | 0.011127 | 0.0027896 | -0.011124 | -0.0027879 | 3.3136e-06 | 1.7039e-06 | 0.016616 | 0.016616 | 0.016616 | 0.99652 | -0.066884 | 0.9962 | -0.073135 | 4.5648

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38416 | 0.097954

## res_load
| p_mw | q_mvar
0 | 0.025805 | 0.0064673
1 | 0.068917 | 0.017272
2 | 0.0060672 | 0.0015206
3 | 0.013199 | 0.003308
4 | 0.033956 | 0.0085102
5 | 0.037057 | 0.0092874
6 | 0.0096977 | 0.0024305
7 | 0.012433 | 0.0031159
8 | 0.042978 | 0.010771
9 | 0.019947 | 0.0049992
10 | 0.0055336 | 0.0013868
11 | 0.0045499 | 0.0011403
12 | 0.021304 | 0.0053392
13 | 0.020359 | 0.0051024
14 | 0.036967 | 0.0092649
15 | 0.0072109 | 0.0018072
16 | 0.011124 | 0.0027879

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1