## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1509-28_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1509-28_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1509-28_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1509-28_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1509-28_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1509-28_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1509-28_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1509-28_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1509-28_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1509-28_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_1509-28_0_4_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1509-28_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1509-28_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1509-28_0_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1509-28_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_1509-28_0_4_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1509-28_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1509-28_0_4_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1509-28_0_4_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1509-28_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1509-28_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1509-28_0_4_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1509-28_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_MV_143_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1509-28_0_4_load_0 | 0 | 0.01211 | 0.0030351 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1509-28_0_4_load_1 | 1 | 0.0081399 | 0.0020401 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1509-28_0_4_load_3 | 3 | 0.011687 | 0.0029291 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1509-28_0_4_load_4 | 4 | 0.011607 | 0.0029091 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1509-28_0_4_load_8 | 5 | 0.0071037 | 0.0017804 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1509-28_0_4_load_6 | 6 | 0.012446 | 0.0031193 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1509-28_0_4_load_5 | 8 | 0.043869 | 0.010995 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1509-28_0_4_load_11 | 10 | 0.0029846 | 0.00074801 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1509-28_0_4_load_13 | 11 | 0.0059309 | 0.0014864 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1509-28_0_4_load_25 | 14 | 0.015528 | 0.0038918 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1509-28_0_4_load_24 | 15 | 0.041565 | 0.010417 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1509-28_0_4_load_17 | 16 | 0.095282 | 0.02388 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1509-28_0_4_load_19 | 18 | 0.028561 | 0.007158 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1509-28_0_4_load_22 | 21 | 0.030912 | 0.0077472 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1509-28_0_4_load_23 | 22 | 0.034084 | 0.0085423 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1509-28_0_4_line_0 |  | 0 | 1 | 0.0043362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1509-28_0_4_line_1 |  | 0 | 2 | 0.011911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1509-28_0_4_line_2 |  | 1 | 3 | 0.0073623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1509-28_0_4_line_3 |  | 2 | 4 | 0.015888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1509-28_0_4_line_4 |  | 3 | 5 | 0.026469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1509-28_0_4_line_5 |  | 4 | 6 | 0.031696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1509-28_0_4_line_6 |  | 5 | 7 | 0.018782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1509-28_0_4_line_7 |  | 6 | 8 | 0.036646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1509-28_0_4_line_8 |  | 7 | 9 | 0.019585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1509-28_0_4_line_9 |  | 7 | 10 | 0.000754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1509-28_0_4_line_10 |  | 9 | 11 | 0.0021176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1509-28_0_4_line_11 |  | 11 | 12 | 0.0055455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1509-28_0_4_line_12 |  | 12 | 13 | 0.13206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1509-28_0_4_line_13 |  | 13 | 14 | 0.081744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1509-28_0_4_line_14 |  | 14 | 15 | 0.10021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1509-28_0_4_line_15 |  | 15 | 22 | 0.040115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1509-28_0_4_line_16 |  | 16 | 17 | 0.037022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1509-28_0_4_line_17 |  | 17 | 18 | 0.004784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1509-28_0_4_line_18 |  | 18 | 19 | 0.027054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1509-28_0_4_line_19 |  | 19 | 20 | 0.019097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1509-28_0_4_line_20 |  | 20 | 21 | 0.020367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1509-28_0_4_line_21 |  | 21 | 22 | 0.015942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1509-28_0_4_trafo_24 | 0.63 MVA 20/0.4 kV | 23 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2670179.7122 | 1201464.0655 | 2670183.9249 | 1201463.0378
1 | 2670168.1401 | 1201466.8883 | 2670179.7122 | 1201464.0655
2 | 2670183.9249 | 1201463.0378 | 2670185.3158 | 1201462.6986 | 2670191.2345 | 1201462.3234 | 2670191.2345 | 1201462.3234
3 | 2670168.1401 | 1201466.8883 | 2670152.6765 | 1201470.5346
4 | 2670214.3752 | 1201475.1248 | 2670195.5131 | 1201464.2081 | 2670191.2345 | 1201462.3234
5 | 2670121.8263 | 1201477.8091 | 2670152.6765 | 1201470.5346
6 | 2670230.6308 | 1201484.533 | 2670214.3752 | 1201475.1248
7 | 2670086.1586 | 1201486.2195 | 2670121.8263 | 1201477.8091
8 | 2670230.6308 | 1201484.533 | 2670234.8954 | 1201477.2453 | 2670241.0183 | 1201467.9228
9 | 2670230.2585 | 1201485.1886 | 2670230.6308 | 1201484.533
10 | 2670241.0183 | 1201467.9228 | 2670241.966 | 1201466.0291
11 | 2670244.448 | 1201461.07 | 2670241.966 | 1201466.0291
12 | 2670240.2776 | 1201387.8543 | 2670262.3774 | 1201379.8759 | 2670268.5906 | 1201377.7699 | 2670272.5316 | 1201377.2937 | 2670274.1858 | 1201379.0253 | 2670276.2185 | 1201380.2944 | 2670278.5011 | 1201381.0217 | 2670280.8972 | 1201381.1611 | 2670280.2405 | 1201389.1026 | 2670271.342 | 1201411.1225 | 2670268.993 | 1201415.3863 | 2670244.448 | 1201461.07
13 | 2670240.2776 | 1201387.8543 | 2670228.8763 | 1201392.9234 | 2670181.7258 | 1201411.2807 | 2670164.204 | 1201417.7222
14 | 2670069.2489 | 1201449.6976 | 2670112.2042 | 1201436.1466 | 2670141.254 | 1201426.1591 | 2670164.204 | 1201417.7222
15 | 2670030.9598 | 1201461.6452 | 2670032.3196 | 1201461.3476 | 2670069.2489 | 1201449.6976
16 | 2669988.7322 | 1201423.8698 | 2669989.8377 | 1201421.7704 | 2669990.1469 | 1201420.7178 | 2669990.1203 | 1201419.7391 | 2669986.2854 | 1201394.9236 | 2669985.9529 | 1201393.4188 | 2669985.4379 | 1201391.9007 | 2669984.3344 | 1201389.9311 | 2669982.9582 | 1201388.503 | 2669982.8967 | 1201388.4542
17 | 2669988.7322 | 1201423.8698 | 2669989.2422 | 1201424.5206 | 2669989.667 | 1201425.9487 | 2669989.645 | 1201428.4159
18 | 2669983.4247 | 1201454.5819 | 2669984.1971 | 1201453.6237 | 2669984.6892 | 1201452.551 | 2669989.6428 | 1201428.6612 | 2669989.645 | 1201428.4159
19 | 2669995.4907 | 1201469.4099 | 2669983.4247 | 1201454.5819
20 | 2669995.4907 | 1201469.4099 | 2670015.3863 | 1201465.0545
21 | 2670030.9598 | 1201461.6452 | 2670015.3863 | 1201465.0545

## bus_geodata
| x | y | coords
0 | 2670179.7122 | 1201464.0655
1 | 2670183.9249 | 1201463.0378
2 | 2670168.1401 | 1201466.8883
3 | 2670191.2345 | 1201462.3234
4 | 2670152.6765 | 1201470.5346
5 | 2670214.3752 | 1201475.1248
6 | 2670121.8263 | 1201477.8091
7 | 2670230.6308 | 1201484.533
8 | 2670086.1586 | 1201486.2195
9 | 2670241.0183 | 1201467.9228
10 | 2670230.2585 | 1201485.1886
11 | 2670241.9661 | 1201466.0291
12 | 2670244.448 | 1201461.07
13 | 2670240.2776 | 1201387.8543
14 | 2670164.204 | 1201417.7222
15 | 2670069.2489 | 1201449.6976
16 | 2669982.8967 | 1201388.4542
17 | 2669988.7322 | 1201423.8698
18 | 2669989.645 | 1201428.4159
19 | 2669983.4247 | 1201454.5819
20 | 2669995.4907 | 1201469.4099
21 | 2670015.3863 | 1201465.0545
22 | 2670030.9598 | 1201461.6452
23 | 2669995.4907 | 1201469.4099

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97565 | -0.46693 | 0.01211 | 0.0030351
1 | 0.97597 | -0.46058 | 0.0081399 | 0.0020401
2 | 0.97489 | -0.48176 | 0 | 0
3 | 0.97658 | -0.44871 | 0.011687 | 0.0029291
4 | 0.97388 | -0.50157 | 0.011607 | 0.0029091
5 | 0.97904 | -0.40052 | 0.0071037 | 0.0017804
6 | 0.97222 | -0.53443 | 0.012446 | 0.0031193
7 | 0.98091 | -0.36406 | 0 | 0
8 | 0.97072 | -0.56412 | 0.043869 | 0.010995
9 | 0.98192 | -0.34458 | 0 | 0
10 | 0.98091 | -0.3641 | 0.0029846 | 0.00074801
11 | 0.98203 | -0.34247 | 0.0059309 | 0.0014864
12 | 0.98232 | -0.33667 | 0 | 0
13 | 0.98946 | -0.19945 | 0 | 0
14 | 0.99387 | -0.11549 | 0.015528 | 0.0038918
15 | 1 | 0 | -0.32678 | -0.083374
16 | 0.98413 | -0.30537 | 0.095282 | 0.02388
17 | 0.98738 | -0.2421 | 0 | 0
18 | 0.9878 | -0.23395 | 0.028561 | 0.007158
19 | 0.99089 | -0.17429 | 0 | 0
20 | 0.99307 | -0.1324 | 0 | 0
21 | 0.99539 | -0.087925 | 0.030912 | 0.0077472
22 | 0.99652 | -0.066249 | 0.034084 | 0.0085423
23 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.080296 | -0.020225 | 0.08032 | 0.020241 | 2.4402e-05 | 1.5563e-05 | 0.1225 | 0.1225 | 0.1225 | 0.97565 | -0.46693 | 0.97597 | -0.46058 | 33.6539
1 | 0.068186 | 0.01719 | -0.068137 | -0.01716 | 4.8341e-05 | 3.079e-05 | 0.10403 | 0.10403 | 0.10403 | 0.97565 | -0.46693 | 0.97489 | -0.48176 | 28.5799
2 | -0.08846 | -0.022281 | 0.08851 | 0.022313 | 5.025e-05 | 3.2068e-05 | 0.13491 | 0.13491 | 0.13491 | 0.97597 | -0.46058 | 0.97658 | -0.44871 | 37.0634
3 | 0.068137 | 0.01716 | -0.068073 | -0.017119 | 6.4478e-05 | 4.1068e-05 | 0.10403 | 0.10403 | 0.10403 | 0.97489 | -0.48176 | 0.97388 | -0.50157 | 28.5799
4 | -0.1002 | -0.025242 | 0.10043 | 0.02539 | 0.0002315 | 0.00014783 | 0.15272 | 0.15272 | 0.15272 | 0.97658 | -0.44871 | 0.97904 | -0.40052 | 41.9558
5 | 0.056466 | 0.014209 | -0.056377 | -0.014153 | 8.8516e-05 | 5.6256e-05 | 0.086296 | 0.086296 | 0.086296 | 0.97388 | -0.50157 | 0.97222 | -0.53443 | 23.7077
6 | -0.10753 | -0.02717 | 0.10772 | 0.027291 | 0.00018832 | 0.00012029 | 0.16352 | 0.16352 | 0.16352 | 0.97904 | -0.40052 | 0.98091 | -0.36406 | 44.9219
7 | 0.043931 | 0.011034 | -0.043869 | -0.010995 | 6.2143e-05 | 3.9318e-05 | 0.067246 | 0.067246 | 0.067246 | 0.97222 | -0.53443 | 0.97072 | -0.56412 | 18.4743
8 | -0.11071 | -0.028039 | 0.11081 | 0.028105 | 0.0001037 | 6.5871e-05 | 0.16804 | 0.16804 | 0.16804 | 0.98091 | -0.36406 | 0.98192 | -0.34458 | 23.0829
9 | 0.0029846 | 0.00074801 | -0.0029846 | -0.00074801 | 5.796e-09 | -5.8083e-09 | 0.0045276 | 0.0045276 | 0.0045276 | 0.98091 | -0.36406 | 0.98091 | -0.3641 | 1.2438
10 | -0.11081 | -0.028105 | 0.11082 | 0.028112 | 1.1212e-05 | 7.1222e-06 | 0.16804 | 0.16804 | 0.16804 | 0.98192 | -0.34458 | 0.98203 | -0.34247 | 23.0828
11 | -0.11675 | -0.029598 | 0.11678 | 0.029619 | 3.2586e-05 | 2.0715e-05 | 0.17703 | 0.17703 | 0.17703 | 0.98203 | -0.34247 | 0.98232 | -0.33667 | 24.3173
12 | -0.11678 | -0.029619 | 0.11756 | 0.030112 | 0.000776 | 0.00049327 | 0.17703 | 0.17703 | 0.17703 | 0.98232 | -0.33667 | 0.98946 | -0.19945 | 24.3173
13 | -0.11756 | -0.030112 | 0.11804 | 0.030417 | 0.00048033 | 0.0003053 | 0.17703 | 0.17703 | 0.17703 | 0.98946 | -0.19945 | 0.99387 | -0.11549 | 24.3171
14 | -0.13357 | -0.034309 | 0.13432 | 0.034789 | 0.00075367 | 0.00047973 | 0.20028 | 0.20028 | 0.20028 | 0.99387 | -0.11549 | 1 | 0 | 27.5105
15 | 0.19081 | 0.048585 | -0.1902 | -0.048197 | 0.0006075 | 0.00038775 | 0.2842 | 0.2842 | 0.2842 | 1 | 0 | 0.99652 | -0.066249 | 39.0379
16 | -0.095282 | -0.02388 | 0.095571 | 0.024064 | 0.00028816 | 0.00018395 | 0.14407 | 0.14407 | 0.14407 | 0.98413 | -0.30537 | 0.98738 | -0.2421 | 39.5791
17 | -0.095571 | -0.024064 | 0.095608 | 0.024088 | 3.7236e-05 | 2.377e-05 | 0.14407 | 0.14407 | 0.14407 | 0.98738 | -0.2421 | 0.9878 | -0.23395 | 39.5791
18 | -0.12417 | -0.031246 | 0.12452 | 0.031473 | 0.00035512 | 0.00022693 | 0.18709 | 0.18709 | 0.18709 | 0.9878 | -0.23395 | 0.99089 | -0.17429 | 51.3988
19 | -0.12452 | -0.031473 | 0.12477 | 0.031633 | 0.00025067 | 0.00016018 | 0.18709 | 0.18709 | 0.18709 | 0.99089 | -0.17429 | 0.99307 | -0.1324 | 51.3988
20 | -0.12477 | -0.031633 | 0.12504 | 0.031804 | 0.00026734 | 0.00017083 | 0.18709 | 0.18709 | 0.18709 | 0.99307 | -0.1324 | 0.99539 | -0.087925 | 51.3988
21 | -0.15595 | -0.039551 | 0.15612 | 0.039655 | 0.0001627 | 0.00010371 | 0.2333 | 0.2333 | 0.2333 | 0.99539 | -0.087925 | 0.99652 | -0.066249 | 32.0469

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36835 | 0.093791

## res_load
| p_mw | q_mvar
0 | 0.01211 | 0.0030351
1 | 0.0081399 | 0.0020401
2 | 0.011687 | 0.0029291
3 | 0.011607 | 0.0029091
4 | 0.0071037 | 0.0017804
5 | 0.012446 | 0.0031193
6 | 0.043869 | 0.010995
7 | 0.0029846 | 0.00074801
8 | 0.0059309 | 0.0014864
9 | 0.015528 | 0.0038918
10 | 0.041565 | 0.010417
11 | 0.095282 | 0.02388
12 | 0.028561 | 0.007158
13 | 0.030912 | 0.0077472
14 | 0.034084 | 0.0085423

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1