## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1509-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1509-3_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1509-3_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1509-3_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1509-3_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1509-3_0_5_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1509-3_0_5_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_1509-3_0_5_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_1509-3_0_5_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1509-3_0_5_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_1509-3_0_5_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1509-3_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1509-3_0_5_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1509-3_0_5_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1509-3_0_5_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1509-3_0_5_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1509-3_0_5_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_1509-3_0_5_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1509-3_0_5_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1509-3_0_5_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1509-3_0_5_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1509-3_0_5_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1509-3_0_5_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1509-3_0_5_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_1509-3_0_5_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1509-3_0_5_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_1509-3_0_5_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_1509-3_0_5_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_1509-3_0_5_node_35 | 0.4 | n |  | TRUE
29 | bus_LV_1509-3_0_5_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_1509-3_0_5_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1509-3_0_5_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1509-3_0_5_node_32 | 0.4 | n |  | TRUE
33 | bus_MV_136_1_node_204 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1509-3_0_5_load_0 | 0 | 0.053983 | 0.013529 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1509-3_0_5_load_1 | 1 | 0.0016268 | 0.00040771 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1509-3_0_5_load_19 | 6 | 0.042504 | 0.010653 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1509-3_0_5_load_24 | 7 | 0.025138 | 0.0063002 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1509-3_0_5_load_36 | 9 | 0.026888 | 0.0067388 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1509-3_0_5_load_9 | 12 | 0.0097054 | 0.0024324 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1509-3_0_5_load_6 | 13 | 0.0099463 | 0.0024928 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1509-3_0_5_load_21 | 16 | 0.023581 | 0.00591 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1509-3_0_5_load_29 | 18 | 0.013336 | 0.0033423 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1509-3_0_5_load_23 | 20 | 0.03452 | 0.0086514 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1509-3_0_5_load_22 | 21 | 0.044091 | 0.01105 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1509-3_0_5_load_27 | 24 | 0.0051347 | 0.0012869 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1509-3_0_5_load_34 | 25 | 0.021471 | 0.0053811 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1509-3_0_5_load_35 | 28 | 0.037366 | 0.0093649 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1509-3_0_5_load_25 | 30 | 0.054614 | 0.013688 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1509-3_0_5_load_26 | 31 | 0.0099499 | 0.0024937 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1509-3_0_5_load_32 | 32 | 0.03075 | 0.0077068 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1509-3_0_5_line_0 |  | 0 | 1 | 0.038972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1509-3_0_5_line_1 |  | 0 | 2 | 0.026345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1509-3_0_5_line_2 |  | 2 | 3 | 0.050582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1509-3_0_5_line_3 |  | 3 | 7 | 0.01121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1509-3_0_5_line_4 |  | 4 | 5 | 0.007662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1509-3_0_5_line_5 |  | 4 | 6 | 0.036916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1509-3_0_5_line_6 |  | 5 | 18 | 0.032563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1509-3_0_5_line_7 |  | 6 | 17 | 0.0045097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1509-3_0_5_line_8 |  | 7 | 24 | 0.025035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1509-3_0_5_line_9 |  | 8 | 9 | 0.021811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1509-3_0_5_line_10 |  | 8 | 10 | 0.045417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1509-3_0_5_line_11 |  | 10 | 21 | 0.014213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1509-3_0_5_line_12 |  | 11 | 12 | 0.021578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1509-3_0_5_line_13 |  | 11 | 13 | 0.0077001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1509-3_0_5_line_14 |  | 12 | 15 | 0.017826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1509-3_0_5_line_15 |  | 14 | 15 | 0.027936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1509-3_0_5_line_16 |  | 14 | 16 | 0.012376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1509-3_0_5_line_17 |  | 15 | 17 | 0.024758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1509-3_0_5_line_18 |  | 18 | 22 | 0.0031736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1509-3_0_5_line_19 |  | 19 | 20 | 0.010436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1509-3_0_5_line_20 |  | 19 | 21 | 0.033897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1509-3_0_5_line_21 |  | 20 | 27 | 0.013542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1509-3_0_5_line_22 |  | 22 | 23 | 0.004631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1509-3_0_5_line_23 |  | 23 | 28 | 0.0098975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1509-3_0_5_line_24 |  | 23 | 29 | 0.007698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_1509-3_0_5_line_25 |  | 24 | 30 | 0.0040669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1509-3_0_5_line_26 |  | 25 | 26 | 0.0063901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1509-3_0_5_line_27 |  | 26 | 28 | 0.010427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1509-3_0_5_line_28 |  | 26 | 32 | 0.00081428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1509-3_0_5_line_29 |  | 27 | 29 | 0.016572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1509-3_0_5_line_30 |  | 29 | 31 | 0.023073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1509-3_0_5_line_31 |  | 30 | 31 | 0.026168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1509-3_0_5_trafo_26 | 0.63 MVA 20/0.4 kV | 33 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2670809.2551 | 1201177.6571 | 2670819.9402 | 1201195.0551 | 2670829.6494 | 1201210.8666
1 | 2670795.4675 | 1201155.2076 | 2670809.2551 | 1201177.6571
2 | 2670788.3491 | 1201118.6789 | 2670795.6487 | 1201125.147 | 2670802.7881 | 1201141.2747 | 2670804.8964 | 1201146.4362 | 2670806.2308 | 1201150.0987 | 2670806.9198 | 1201151.6967 | 2670795.4675 | 1201155.2076
3 | 2670788.3491 | 1201118.6789 | 2670779.6329 | 1201125.7577
4 | 2670725.0438 | 1201190.8511 | 2670720.3137 | 1201196.8877
5 | 2670725.0438 | 1201190.8511 | 2670754.7399 | 1201212.7815
6 | 2670720.3137 | 1201196.8877 | 2670713.851 | 1201191.0966 | 2670711.3382 | 1201184.096 | 2670711.0823 | 1201182.5587 | 2670709.3315 | 1201167.7734
7 | 2670758.3675 | 1201215.4605 | 2670754.7399 | 1201212.7815
8 | 2670779.6329 | 1201125.7577 | 2670765.8175 | 1201130.8306 | 2670756.2862 | 1201134.7811
9 | 2670764.6768 | 1201060.0518 | 2670765.8811 | 1201066.9925 | 2670767.519 | 1201081.6653
10 | 2670744.6122 | 1201089.4989 | 2670752.0925 | 1201078.792 | 2670749.939 | 1201061.3671 | 2670759.4325 | 1201060.6457 | 2670764.6768 | 1201060.0518
11 | 2670744.6122 | 1201089.4989 | 2670733.2 | 1201097.9709
12 | 2670796.5318 | 1201261.3069 | 2670779.7939 | 1201247.6882
13 | 2670796.5318 | 1201261.3069 | 2670793.511 | 1201266.3409 | 2670793.2384 | 1201268.1498
14 | 2670765.8047 | 1201236.6503 | 2670769.2015 | 1201239.0697 | 2670779.7939 | 1201247.6882
15 | 2670745.0308 | 1201234.7699 | 2670751.6516 | 1201226.5544 | 2670765.8047 | 1201236.6503
16 | 2670745.0308 | 1201234.7699 | 2670737.4205 | 1201244.53
17 | 2670765.8047 | 1201236.6503 | 2670765.4533 | 1201220.692 | 2670758.3675 | 1201215.4605
18 | 2670707.7349 | 1201165.0306 | 2670709.3315 | 1201167.7734
19 | 2670703.1057 | 1201112.3772 | 2670703.751 | 1201122.7929
20 | 2670703.1057 | 1201112.3772 | 2670708.8815 | 1201111.256 | 2670711.134 | 1201110.6712 | 2670721.5422 | 1201106.6252 | 2670733.2 | 1201097.9709
21 | 2670704.5885 | 1201136.3093 | 2670703.751 | 1201122.7929
22 | 2670707.7349 | 1201165.0306 | 2670707.5805 | 1201163.9281 | 2670707.0355 | 1201160.4529
23 | 2670707.0355 | 1201160.4529 | 2670697.1434 | 1201160.7806
24 | 2670706.3727 | 1201152.7849 | 2670707.0355 | 1201160.4529
25 | 2670756.2862 | 1201134.7811 | 2670752.5292 | 1201136.3382
26 | 2670688.9993 | 1201154.2692 | 2670685.411 | 1201159.5566
27 | 2670688.9993 | 1201154.2692 | 2670697.1434 | 1201160.7806
28 | 2670688.9993 | 1201154.2692 | 2670688.4475 | 1201153.6704
29 | 2670706.3727 | 1201152.7849 | 2670705.4839 | 1201144.2692 | 2670704.5885 | 1201136.3093
30 | 2670706.3727 | 1201152.7849 | 2670713.4765 | 1201152.0018 | 2670718.9016 | 1201150.276 | 2670728.3553 | 1201146.3577
31 | 2670728.3553 | 1201146.3577 | 2670752.5292 | 1201136.3382

## bus_geodata
| x | y | coords
0 | 2670809.2551 | 1201177.6571
1 | 2670829.6494 | 1201210.8666
2 | 2670795.4675 | 1201155.2076
3 | 2670788.3491 | 1201118.6789
4 | 2670725.0438 | 1201190.8511
5 | 2670720.3137 | 1201196.8877
6 | 2670754.7399 | 1201212.7815
7 | 2670779.6329 | 1201125.7577
8 | 2670764.6768 | 1201060.0518
9 | 2670767.519 | 1201081.6653
10 | 2670744.6122 | 1201089.4989
11 | 2670796.5318 | 1201261.3069
12 | 2670779.7939 | 1201247.6882
13 | 2670793.2384 | 1201268.1498
14 | 2670745.0308 | 1201234.7699
15 | 2670765.8047 | 1201236.6503
16 | 2670737.4205 | 1201244.53
17 | 2670758.3675 | 1201215.4605
18 | 2670709.3315 | 1201167.7734
19 | 2670703.1057 | 1201112.3772
20 | 2670703.751 | 1201122.7929
21 | 2670733.2 | 1201097.9709
22 | 2670707.7349 | 1201165.0306
23 | 2670707.0355 | 1201160.4529
24 | 2670756.2862 | 1201134.7811
25 | 2670685.411 | 1201159.5566
26 | 2670688.9993 | 1201154.2692
27 | 2670704.5885 | 1201136.3093
28 | 2670697.1434 | 1201160.7806
29 | 2670706.3727 | 1201152.7849
30 | 2670752.5292 | 1201136.3382
31 | 2670728.3553 | 1201146.3577
32 | 2670688.4475 | 1201153.6704
33 | 2670706.3727 | 1201152.7849

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99168 | -0.16013 | 0.053983 | 0.013529
1 | 0.99162 | -0.16125 | 0.0016268 | 0.00040771
2 | 0.99302 | -0.1342 | 0 | 0
3 | 0.99559 | -0.084604 | 0 | 0
4 | 0.9934 | -0.12652 | 0 | 0
5 | 0.994 | -0.11492 | 0 | 0
6 | 0.9905 | -0.18258 | 0.042504 | 0.010653
7 | 0.99616 | -0.073648 | 0.025138 | 0.0063002
8 | 0.99068 | -0.17927 | 0 | 0
9 | 0.99015 | -0.18969 | 0.026888 | 0.0067388
10 | 0.9918 | -0.15761 | 0 | 0
11 | 0.98882 | -0.21516 | 0 | 0
12 | 0.98902 | -0.21133 | 0.0097054 | 0.0024324
13 | 0.98875 | -0.21652 | 0.0099463 | 0.0024928
14 | 0.98874 | -0.21683 | 0 | 0
15 | 0.98934 | -0.20509 | 0 | 0
16 | 0.98847 | -0.22203 | 0.023581 | 0.00591
17 | 0.99032 | -0.18605 | 0 | 0
18 | 0.99656 | -0.065795 | 0.013336 | 0.0033423
19 | 0.99435 | -0.10833 | 0 | 0
20 | 0.99503 | -0.095284 | 0.03452 | 0.0086514
21 | 0.99215 | -0.15084 | 0.044091 | 0.01105
22 | 0.99685 | -0.060279 | 0 | 0
23 | 0.99727 | -0.052234 | 0 | 0
24 | 0.99801 | -0.038205 | 0.0051347 | 0.0012869
25 | 0.99584 | -0.07976 | 0.021471 | 0.0053811
26 | 0.99597 | -0.077349 | 0 | 0
27 | 0.99634 | -0.070165 | 0 | 0
28 | 0.99646 | -0.067786 | 0.037366 | 0.0093649
29 | 0.99793 | -0.039516 | 0 | 0
30 | 0.99832 | -0.032095 | 0.054614 | 0.013688
31 | 1 | 0 | -0.43882 | -0.11054
32 | 0.99594 | -0.077789 | 0.03075 | 0.0077068
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0016269 | 0.00040726 | -0.0016268 | -0.00040771 | 8.7082e-08 | -4.4705e-07 | 0.002441 | 0.0024411 | 0.0024411 | 0.99168 | -0.16013 | 0.99162 | -0.16125 | 0.67064
1 | -0.05561 | -0.013937 | 0.055679 | 0.01398 | 6.8788e-05 | 4.3684e-05 | 0.083442 | 0.083442 | 0.083442 | 0.99168 | -0.16013 | 0.99302 | -0.1342 | 22.9238
2 | -0.055679 | -0.01398 | 0.055811 | 0.014064 | 0.00013207 | 8.3868e-05 | 0.083442 | 0.083442 | 0.083442 | 0.99302 | -0.1342 | 0.99559 | -0.084604 | 22.9237
3 | -0.055811 | -0.014064 | 0.05584 | 0.014083 | 2.9269e-05 | 1.8586e-05 | 0.083442 | 0.083442 | 0.083442 | 0.99559 | -0.084604 | 0.99616 | -0.073648 | 22.9237
4 | -0.086041 | -0.02168 | 0.086089 | 0.021711 | 4.7756e-05 | 3.0465e-05 | 0.12892 | 0.12892 | 0.12892 | 0.9934 | -0.12652 | 0.994 | -0.11492 | 35.4181
5 | 0.086041 | 0.02168 | -0.085811 | -0.021533 | 0.00023009 | 0.00014678 | 0.12892 | 0.12892 | 0.12892 | 0.9934 | -0.12652 | 0.9905 | -0.18258 | 35.4182
6 | -0.086089 | -0.021711 | 0.086292 | 0.02184 | 0.00020296 | 0.00012947 | 0.12892 | 0.12892 | 0.12892 | 0.994 | -0.11492 | 0.99656 | -0.065795 | 35.4181
7 | 0.043307 | 0.010881 | -0.0433 | -0.010876 | 7.1601e-06 | 4.5244e-06 | 0.065069 | 0.065069 | 0.065069 | 0.9905 | -0.18258 | 0.99032 | -0.18605 | 17.876
8 | -0.080978 | -0.020383 | 0.081115 | 0.020471 | 0.00013743 | 8.7631e-05 | 0.12099 | 0.12099 | 0.12099 | 0.99616 | -0.073648 | 0.99801 | -0.038205 | 33.2396
9 | 0.026902 | 0.0067471 | -0.026888 | -0.0067388 | 1.3355e-05 | 8.2666e-06 | 0.040408 | 0.040408 | 0.040408 | 0.99068 | -0.17927 | 0.99015 | -0.18969 | 11.1012
10 | -0.026902 | -0.0067471 | 0.026929 | 0.0067643 | 2.7809e-05 | 1.7213e-05 | 0.040408 | 0.040408 | 0.040408 | 0.99068 | -0.17927 | 0.9918 | -0.15761 | 11.1012
11 | -0.026929 | -0.0067643 | 0.026938 | 0.0067697 | 8.7028e-06 | 5.3863e-06 | 0.040408 | 0.040408 | 0.040408 | 0.9918 | -0.15761 | 0.99215 | -0.15084 | 11.1011
12 | -0.0099469 | -0.0024931 | 0.0099487 | 0.002494 | 1.813e-06 | 8.8348e-07 | 0.014969 | 0.014968 | 0.014969 | 0.98882 | -0.21516 | 0.98902 | -0.21133 | 4.1122
13 | 0.0099469 | 0.0024931 | -0.0099463 | -0.0024928 | 6.4698e-07 | 3.153e-07 | 0.014969 | 0.014969 | 0.014969 | 0.98882 | -0.21516 | 0.98875 | -0.21652 | 4.1122
14 | -0.019654 | -0.0049264 | 0.01966 | 0.0049299 | 5.8453e-06 | 3.5121e-06 | 0.029571 | 0.02957 | 0.029571 | 0.98902 | -0.21133 | 0.98934 | -0.20509 | 8.1238
15 | -0.023587 | -0.0059136 | 0.0236 | 0.0059217 | 1.3201e-05 | 8.0904e-06 | 0.035499 | 0.035498 | 0.035499 | 0.98874 | -0.21683 | 0.98934 | -0.20509 | 9.7524
16 | 0.023587 | 0.0059136 | -0.023581 | -0.00591 | 5.8486e-06 | 3.5844e-06 | 0.035499 | 0.035499 | 0.035499 | 0.98874 | -0.21683 | 0.98847 | -0.22203 | 9.7524
17 | -0.04326 | -0.010852 | 0.0433 | 0.010876 | 3.9309e-05 | 2.484e-05 | 0.065069 | 0.065069 | 0.065069 | 0.98934 | -0.20509 | 0.99032 | -0.18605 | 17.8761
18 | -0.099627 | -0.025182 | 0.099654 | 0.025199 | 2.6363e-05 | 1.6831e-05 | 0.14883 | 0.14883 | 0.14883 | 0.99656 | -0.065795 | 0.99685 | -0.060279 | 40.8885
19 | -0.071173 | -0.017912 | 0.071217 | 0.01794 | 4.4415e-05 | 2.829e-05 | 0.10653 | 0.10653 | 0.10653 | 0.99435 | -0.10833 | 0.99503 | -0.095284 | 29.2676
20 | 0.071173 | 0.017912 | -0.071029 | -0.01782 | 0.00014427 | 9.1892e-05 | 0.10653 | 0.10653 | 0.10653 | 0.99435 | -0.10833 | 0.99215 | -0.15084 | 29.2677
21 | -0.10574 | -0.026591 | 0.10586 | 0.026673 | 0.00012703 | 8.1121e-05 | 0.15816 | 0.15816 | 0.15816 | 0.99503 | -0.095284 | 0.99634 | -0.070165 | 43.4495
22 | -0.099654 | -0.025199 | 0.099692 | 0.025224 | 3.8469e-05 | 2.456e-05 | 0.14883 | 0.14883 | 0.14883 | 0.99685 | -0.060279 | 0.99727 | -0.052234 | 40.8885
23 | 0.089681 | 0.022512 | -0.089615 | -0.02247 | 6.6471e-05 | 4.2412e-05 | 0.13382 | 0.13382 | 0.13382 | 0.99727 | -0.052234 | 0.99646 | -0.067786 | 36.7651
24 | -0.18937 | -0.047736 | 0.18949 | 0.04781 | 0.00011532 | 7.3604e-05 | 0.28266 | 0.28266 | 0.28266 | 0.99727 | -0.052234 | 0.99793 | -0.039516 | 38.8267
25 | -0.08625 | -0.021757 | 0.086275 | 0.021774 | 2.524e-05 | 1.6101e-05 | 0.12865 | 0.12865 | 0.12865 | 0.99801 | -0.038205 | 0.99832 | -0.032095 | 35.3428
26 | -0.021471 | -0.0053811 | 0.021473 | 0.0053826 | 2.4665e-06 | 1.4954e-06 | 0.032083 | 0.032083 | 0.032083 | 0.99584 | -0.07976 | 0.99597 | -0.077349 | 8.8139
27 | -0.052225 | -0.01309 | 0.052248 | 0.013105 | 2.3805e-05 | 1.51e-05 | 0.078026 | 0.078026 | 0.078026 | 0.99597 | -0.077349 | 0.99646 | -0.067786 | 21.4357
28 | 0.030751 | 0.0077072 | -0.03075 | -0.0077068 | 6.4454e-07 | 4.0191e-07 | 0.045943 | 0.045943 | 0.045943 | 0.99597 | -0.077349 | 0.99594 | -0.077789 | 12.6218
29 | -0.10586 | -0.026673 | 0.10602 | 0.026772 | 0.00015545 | 9.9269e-05 | 0.15816 | 0.15816 | 0.15816 | 0.99634 | -0.070165 | 0.99793 | -0.039516 | 43.4495
30 | -0.29551 | -0.074581 | 0.29607 | 0.074939 | 0.00056045 | 0.00035778 | 0.44081 | 0.44081 | 0.44081 | 0.99793 | -0.039516 | 1 | 0 | 40.3677
31 | -0.14089 | -0.035461 | 0.14111 | 0.035599 | 0.00021648 | 0.00013786 | 0.21005 | 0.21005 | 0.21005 | 0.99832 | -0.032095 | 1 | 0 | 28.8532

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44877 | 0.11303

## res_load
| p_mw | q_mvar
0 | 0.053983 | 0.013529
1 | 0.0016268 | 0.00040771
2 | 0.042504 | 0.010653
3 | 0.025138 | 0.0063002
4 | 0.026888 | 0.0067388
5 | 0.0097054 | 0.0024324
6 | 0.0099463 | 0.0024928
7 | 0.023581 | 0.00591
8 | 0.013336 | 0.0033423
9 | 0.03452 | 0.0086514
10 | 0.044091 | 0.01105
11 | 0.0051347 | 0.0012869
12 | 0.021471 | 0.0053811
13 | 0.037366 | 0.0093649
14 | 0.054614 | 0.013688
15 | 0.0099499 | 0.0024937
16 | 0.03075 | 0.0077068

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1