## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1510-10_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1510-10_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1510-10_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1510-10_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1510-10_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1510-10_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1510-10_0_5_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1510-10_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1510-10_0_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1510-10_0_5_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_1510-10_0_5_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_1510-10_0_5_node_22 | 0.4 | n |  | TRUE
12 | bus_LV_1510-10_0_5_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_1510-10_0_5_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1510-10_0_5_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_1510-10_0_5_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1510-10_0_5_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1510-10_0_5_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1510-10_0_5_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1510-10_0_5_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_1510-10_0_5_node_36 | 0.4 | n |  | TRUE
21 | bus_LV_1510-10_0_5_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_1510-10_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1510-10_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1510-10_0_5_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1510-10_0_5_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_1510-10_0_5_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1510-10_0_5_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1510-10_0_5_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_1510-10_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1510-10_0_5_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1510-10_0_5_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1510-10_0_5_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1510-10_0_5_node_28 | 0.4 | n |  | TRUE
34 | bus_MV_143_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1510-10_0_5_load_0 | 0 | 0.071314 | 0.017873 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1510-10_0_5_load_1 | 1 | 0.040129 | 0.010057 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1510-10_0_5_load_25 | 10 | 0.050984 | 0.012778 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1510-10_0_5_load_22 | 11 | 0.011658 | 0.0029218 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1510-10_0_5_load_29 | 12 | 0.010989 | 0.0027542 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1510-10_0_5_load_10 | 13 | 0.042178 | 0.010571 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1510-10_0_5_load_32 | 14 | 0.031333 | 0.0078528 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1510-10_0_5_load_16 | 18 | 0.0059671 | 0.0014955 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1510-10_0_5_load_20 | 19 | 0.068766 | 0.017234 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1510-10_0_5_load_36 | 20 | 0.020292 | 0.0050855 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1510-10_0_5_load_31 | 21 | 0.047349 | 0.011867 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1510-10_0_5_load_33 | 25 | 0.029114 | 0.0072968 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1510-10_0_5_load_21 | 26 | 0.010942 | 0.0027423 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1510-10_0_5_load_19 | 27 | 0.0064725 | 0.0016222 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1510-10_0_5_load_30 | 28 | 0.0066662 | 0.0016707 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1510-10_0_5_load_23 | 29 | 0.009998 | 0.0025057 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1510-10_0_5_load_26 | 31 | 0.015331 | 0.0038423 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1510-10_0_5_load_27 | 32 | 0.037804 | 0.0094745 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1510-10_0_5_load_28 | 33 | 0.014955 | 0.0037482 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 0 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1510-10_0_5_line_0 |  | 0 | 1 | 0.002756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1510-10_0_5_line_1 |  | 0 | 2 | 0.023217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1510-10_0_5_line_2 |  | 2 | 3 | 0.02948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1510-10_0_5_line_3 |  | 2 | 4 | 0.015436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1510-10_0_5_line_4 |  | 2 | 5 | 0.019232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1510-10_0_5_line_5 |  | 3 | 9 | 0.017973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1510-10_0_5_line_6 |  | 4 | 10 | 0.022419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1510-10_0_5_line_7 |  | 4 | 11 | 0.023645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1510-10_0_5_line_8 |  | 5 | 12 | 0.036706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1510-10_0_5_line_9 |  | 5 | 13 | 0.018457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1510-10_0_5_line_10 |  | 6 | 7 | 0.015519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1510-10_0_5_line_11 |  | 6 | 8 | 0.064992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1510-10_0_5_line_12 |  | 7 | 14 | 0.012644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1510-10_0_5_line_13 |  | 7 | 15 | 0.026369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1510-10_0_5_line_14 |  | 8 | 19 | 0.016767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1510-10_0_5_line_15 |  | 9 | 20 | 0.018841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1510-10_0_5_line_16 |  | 11 | 26 | 0.032543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1510-10_0_5_line_17 |  | 15 | 21 | 0.0096824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1510-10_0_5_line_18 |  | 16 | 17 | 0.018642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1510-10_0_5_line_19 |  | 16 | 18 | 0.0048616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1510-10_0_5_line_20 |  | 17 | 27 | 0.03611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1510-10_0_5_line_21 |  | 17 | 19 | 0.022713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1510-10_0_5_line_22 |  | 20 | 22 | 0.014511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1510-10_0_5_line_23 |  | 21 | 24 | 0.0064705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1510-10_0_5_line_24 |  | 22 | 23 | 0.011884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1510-10_0_5_line_25 |  | 23 | 24 | 0.037949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1510-10_0_5_line_26 |  | 23 | 25 | 0.036031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1510-10_0_5_line_27 |  | 26 | 29 | 0.013692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1510-10_0_5_line_28 |  | 27 | 28 | 0.010882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1510-10_0_5_line_29 |  | 29 | 30 | 0.011089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1510-10_0_5_line_30 |  | 30 | 31 | 0.0042429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1510-10_0_5_line_31 |  | 30 | 32 | 0.027997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1510-10_0_5_line_32 |  | 31 | 33 | 0.00056395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1510-10_0_5_trafo_0 | 0.63 MVA 20/0.4 kV | 34 | 0 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2668235.1674 | 1203446.4554 | 2668236.5726 | 1203444.0846
1 | 2668223.3293 | 1203466.4273 | 2668235.1674 | 1203446.4554
2 | 2668223.3293 | 1203466.4273 | 2668198.2606 | 1203450.7983
3 | 2668223.3293 | 1203466.4273 | 2668228.9332 | 1203470.1157 | 2668236.2522 | 1203474.8689
4 | 2668223.3293 | 1203466.4273 | 2668228.9332 | 1203470.1157 | 2668221.9132 | 1203480.4863
5 | 2668182.4182 | 1203449.4722 | 2668184.0398 | 1203446.7335 | 2668198.2606 | 1203450.7983
6 | 2668236.2522 | 1203474.8689 | 2668254.9295 | 1203487.2695
7 | 2668236.2522 | 1203474.8689 | 2668232.1936 | 1203481.1152 | 2668231.606 | 1203487.2566 | 2668239.9996 | 1203492.74
8 | 2668221.9132 | 1203480.4863 | 2668210.1275 | 1203499.063 | 2668197.5122 | 1203491.5049
9 | 2668221.9132 | 1203480.4863 | 2668206.1926 | 1203470.8162
10 | 2668210.02 | 1203409.8855 | 2668195.1084 | 1203414.3291
11 | 2668210.02 | 1203409.8855 | 2668220.7879 | 1203405.8171 | 2668233.0715 | 1203400.9544 | 2668251.2061 | 1203393.4792 | 2668259.2722 | 1203390.1248 | 2668263.956 | 1203401.085
12 | 2668195.1084 | 1203414.3291 | 2668190.2424 | 1203402.6554
13 | 2668168.8443 | 1203414.7296 | 2668173.4513 | 1203415.7717 | 2668176.2808 | 1203415.8707 | 2668195.1084 | 1203414.3291
14 | 2668263.956 | 1203401.085 | 2668279.3661 | 1203394.4777
15 | 2668182.4182 | 1203449.4722 | 2668179.906 | 1203448.9099 | 2668178.2264 | 1203448.7351 | 2668176.1175 | 1203448.8333 | 2668174.0517 | 1203449.1544 | 2668171.6 | 1203449.9602 | 2668169.1017 | 1203450.8433 | 2668166.6127 | 1203451.5821 | 2668164.0828 | 1203451.8978
16 | 2668267.2449 | 1203510.5375 | 2668249.2568 | 1203498.7874 | 2668239.9996 | 1203492.74
17 | 2668168.8443 | 1203414.7296 | 2668163.5523 | 1203413.7131 | 2668159.2934 | 1203414.2583
18 | 2668300.6471 | 1203392.4991 | 2668293.5852 | 1203375.2412
19 | 2668293.5852 | 1203375.2412 | 2668298.0338 | 1203373.2805
20 | 2668300.6471 | 1203392.4991 | 2668310.8402 | 1203421.3887 | 2668308.9779 | 1203426.5372
21 | 2668300.6471 | 1203392.4991 | 2668290.8037 | 1203389.5737 | 2668279.3661 | 1203394.4777
22 | 2668150.2995 | 1203454.8313 | 2668151.9485 | 1203453.6938 | 2668154.2131 | 1203452.619 | 2668156.7481 | 1203451.8475 | 2668159.193 | 1203451.6419 | 2668161.8313 | 1203451.8277 | 2668164.0828 | 1203451.8978
23 | 2668153.3597 | 1203416.7209 | 2668158.2104 | 1203414.397 | 2668159.2934 | 1203414.2583
24 | 2668140.8541 | 1203447.7081 | 2668143.1617 | 1203448.8685 | 2668147.7369 | 1203452.6896 | 2668150.2995 | 1203454.8313
25 | 2668140.8541 | 1203447.7081 | 2668143.1617 | 1203448.8685 | 2668145.8407 | 1203443.4847 | 2668146.6917 | 1203440.9261 | 2668147.0939 | 1203438.3514 | 2668146.9987 | 1203436.0267 | 2668146.0941 | 1203430.6131 | 2668146.9777 | 1203425.1977 | 2668149.4821 | 1203420.4456 | 2668153.3597 | 1203416.7209
26 | 2668140.8541 | 1203447.7081 | 2668137.6913 | 1203446.1489 | 2668133.3145 | 1203441.6073 | 2668129.1096 | 1203440.6811 | 2668114.8942 | 1203446.8116 | 2668108.4842 | 1203446.753
27 | 2668279.3536 | 1203516.5198 | 2668274.7397 | 1203515.4331 | 2668267.2449 | 1203510.5375
28 | 2668308.9779 | 1203426.5372 | 2668308.9779 | 1203426.5372 | 2668298.8757 | 1203430.5837
29 | 2668286.1924 | 1203508.0262 | 2668281.6917 | 1203515.0012 | 2668279.3536 | 1203516.5198 | 2668279.3536 | 1203516.5198
30 | 2668286.1924 | 1203508.0262 | 2668282.6576 | 1203505.6793
31 | 2668286.1924 | 1203508.0262 | 2668310.0759 | 1203522.6343
32 | 2668282.6576 | 1203505.6793 | 2668282.1878 | 1203505.3674

## bus_geodata
| x | y | coords
0 | 2668235.1674 | 1203446.4554
1 | 2668236.5726 | 1203444.0846
2 | 2668223.3293 | 1203466.4273
3 | 2668198.2606 | 1203450.7983
4 | 2668236.2522 | 1203474.8689
5 | 2668221.9132 | 1203480.4863
6 | 2668210.02 | 1203409.8855
7 | 2668195.1084 | 1203414.3291
8 | 2668263.956 | 1203401.085
9 | 2668182.4182 | 1203449.4722
10 | 2668254.9295 | 1203487.2695
11 | 2668239.9996 | 1203492.74
12 | 2668197.5122 | 1203491.5049
13 | 2668206.1926 | 1203470.8162
14 | 2668190.2424 | 1203402.6554
15 | 2668168.8443 | 1203414.7296
16 | 2668293.5852 | 1203375.2412
17 | 2668300.6471 | 1203392.4991
18 | 2668298.0338 | 1203373.2805
19 | 2668279.3661 | 1203394.4777
20 | 2668164.0828 | 1203451.8978
21 | 2668159.2934 | 1203414.2583
22 | 2668150.2995 | 1203454.8313
23 | 2668140.8541 | 1203447.7081
24 | 2668153.3597 | 1203416.7209
25 | 2668108.4842 | 1203446.753
26 | 2668267.2449 | 1203510.5375
27 | 2668308.9779 | 1203426.5372
28 | 2668298.8757 | 1203430.5837
29 | 2668279.3536 | 1203516.5198
30 | 2668286.1924 | 1203508.0262
31 | 2668282.6576 | 1203505.6793
32 | 2668310.0759 | 1203522.6343
33 | 2668282.1878 | 1203505.3674
34 | 2668223.3293 | 1203466.4273

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1 | 0 | -0.46662 | -0.11809
1 | 0.9999 | -0.0019278 | 0.040129 | 0.010057
2 | 0.99776 | -0.042669 | 0 | 0
3 | 0.9963 | -0.070579 | 0 | 0
4 | 0.99669 | -0.063186 | 0 | 0
5 | 0.99683 | -0.060588 | 0 | 0
6 | 0.98609 | -0.26679 | 0 | 0
7 | 0.98735 | -0.24237 | 0 | 0
8 | 0.9808 | -0.36971 | 0 | 0
9 | 0.9954 | -0.087634 | 0 | 0
10 | 0.99565 | -0.083262 | 0.050984 | 0.012778
11 | 0.99451 | -0.10505 | 0.011658 | 0.0029218
12 | 0.99646 | -0.067667 | 0.010989 | 0.0027542
13 | 0.99612 | -0.074253 | 0.042178 | 0.010571
14 | 0.98699 | -0.24946 | 0.031333 | 0.0078528
15 | 0.99026 | -0.18634 | 0 | 0
16 | 0.97893 | -0.40636 | 0 | 0
17 | 0.97903 | -0.40433 | 0 | 0
18 | 0.9789 | -0.40688 | 0.0059671 | 0.0014955
19 | 0.97943 | -0.39644 | 0.068766 | 0.017234
20 | 0.99447 | -0.10555 | 0.020292 | 0.0050855
21 | 0.99132 | -0.16584 | 0.047349 | 0.011867
22 | 0.99381 | -0.11807 | 0 | 0
23 | 0.99328 | -0.12833 | 0 | 0
24 | 0.99182 | -0.15629 | 0 | 0
25 | 0.99232 | -0.14688 | 0.029114 | 0.0072968
26 | 0.99186 | -0.15625 | 0.010942 | 0.0027423
27 | 0.97859 | -0.41296 | 0.0064725 | 0.0016222
28 | 0.97852 | -0.41428 | 0.0066662 | 0.0016707
29 | 0.99088 | -0.17521 | 0.009998 | 0.0025057
30 | 0.99018 | -0.18862 | 0 | 0
31 | 0.99007 | -0.1909 | 0.015331 | 0.0038423
32 | 0.98921 | -0.20745 | 0.037804 | 0.0094745
33 | 0.99006 | -0.19105 | 0.014955 | 0.0037482
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.040133 | 0.01006 | -0.040129 | -0.010057 | 3.6858e-06 | 2.3228e-06 | 0.059719 | 0.059719 | 0.059719 | 1 | 0 | 0.9999 | -0.0019278 | 16.4063
1 | 0.42484 | 0.10803 | -0.42397 | -0.10748 | 0.00087135 | 0.00055645 | 0.63272 | 0.63272 | 0.63272 | 1 | 0 | 0.99776 | -0.042669 | 43.4561
2 | 0.21828 | 0.055599 | -0.21799 | -0.055413 | 0.00029345 | 0.00018627 | 0.32585 | 0.32585 | 0.32585 | 0.99776 | -0.042669 | 0.9963 | -0.070579 | 22.3799
3 | 0.15244 | 0.038504 | -0.15229 | -0.038409 | 0.00014973 | 9.5426e-05 | 0.22745 | 0.22745 | 0.22745 | 0.99776 | -0.042669 | 0.99669 | -0.063186 | 31.2437
4 | 0.053244 | 0.013373 | -0.053199 | -0.013344 | 4.5486e-05 | 2.886e-05 | 0.079417 | 0.079417 | 0.079417 | 0.99776 | -0.042669 | 0.99683 | -0.060588 | 21.8177
5 | 0.21799 | 0.055413 | -0.21781 | -0.0553 | 0.00017891 | 0.00011357 | 0.32585 | 0.32585 | 0.32585 | 0.9963 | -0.070579 | 0.9954 | -0.087634 | 22.3799
6 | 0.051033 | 0.012809 | -0.050984 | -0.012778 | 4.8812e-05 | 3.0948e-05 | 0.076197 | 0.076197 | 0.076197 | 0.99669 | -0.063186 | 0.99565 | -0.083262 | 20.9332
7 | 0.10126 | 0.0256 | -0.10106 | -0.025471 | 0.00020286 | 0.00012952 | 0.15126 | 0.15126 | 0.15126 | 0.99669 | -0.063186 | 0.99451 | -0.10505 | 41.5543
8 | 0.010993 | 0.0027561 | -0.010989 | -0.0027542 | 3.7068e-06 | 1.894e-06 | 0.01641 | 0.01641 | 0.01641 | 0.99683 | -0.060588 | 0.99646 | -0.067667 | 4.5083
9 | 0.042206 | 0.010588 | -0.042178 | -0.010571 | 2.7476e-05 | 1.7344e-05 | 0.063006 | 0.063006 | 0.063006 | 0.99683 | -0.060588 | 0.99612 | -0.074253 | 17.3095
10 | -0.088432 | -0.022379 | 0.088536 | 0.022445 | 0.00010375 | 6.6204e-05 | 0.13352 | 0.13352 | 0.13352 | 0.98609 | -0.26679 | 0.98735 | -0.24237 | 36.6819
11 | 0.088432 | 0.022379 | -0.087998 | -0.022102 | 0.00043451 | 0.00027726 | 0.13352 | 0.13352 | 0.13352 | 0.98609 | -0.26679 | 0.9808 | -0.36971 | 36.682
12 | 0.031344 | 0.0078594 | -0.031333 | -0.0078528 | 1.0581e-05 | 6.61e-06 | 0.047239 | 0.047239 | 0.047239 | 0.98735 | -0.24237 | 0.98699 | -0.24946 | 12.9778
13 | -0.11988 | -0.030305 | 0.1202 | 0.030511 | 0.0003231 | 0.00020644 | 0.18076 | 0.18076 | 0.18076 | 0.98735 | -0.24237 | 0.99026 | -0.18634 | 49.6596
14 | 0.087998 | 0.022102 | -0.087885 | -0.02203 | 0.0001121 | 7.1531e-05 | 0.13352 | 0.13352 | 0.13352 | 0.9808 | -0.36971 | 0.97943 | -0.39644 | 36.682
15 | 0.21781 | 0.0553 | -0.21762 | -0.05518 | 0.00018755 | 0.00011905 | 0.32585 | 0.32585 | 0.32585 | 0.9954 | -0.087634 | 0.99447 | -0.10555 | 22.3799
16 | 0.0894 | 0.022549 | -0.089182 | -0.022409 | 0.00021852 | 0.00013943 | 0.13381 | 0.13381 | 0.13381 | 0.99451 | -0.10505 | 0.99186 | -0.15625 | 36.7622
17 | -0.1202 | -0.030511 | 0.12032 | 0.030587 | 0.00011864 | 7.5804e-05 | 0.18076 | 0.18076 | 0.18076 | 0.99026 | -0.18634 | 0.99132 | -0.16584 | 49.6596
18 | -0.0059672 | -0.0014955 | 0.0059678 | 0.0014957 | 5.7515e-07 | 1.337e-07 | 0.0090705 | 0.0090704 | 0.0090705 | 0.97893 | -0.40636 | 0.97903 | -0.40433 | 2.4919
19 | 0.0059672 | 0.0014955 | -0.0059671 | -0.0014955 | 1.4999e-07 | 3.4876e-08 | 0.0090705 | 0.0090705 | 0.0090705 | 0.97893 | -0.40636 | 0.9789 | -0.40688 | 2.4919
20 | 0.013145 | 0.003296 | -0.013139 | -0.003293 | 5.4051e-06 | 3.0054e-06 | 0.019979 | 0.019979 | 0.019979 | 0.97903 | -0.40433 | 0.97859 | -0.41296 | 5.4887
21 | -0.019112 | -0.0047917 | 0.01912 | 0.004796 | 7.1876e-06 | 4.3143e-06 | 0.029049 | 0.029049 | 0.029049 | 0.97903 | -0.40433 | 0.97943 | -0.39644 | 7.9805
22 | 0.19733 | 0.050095 | -0.19721 | -0.05002 | 0.00011878 | 7.5267e-05 | 0.29549 | 0.29549 | 0.29549 | 0.99447 | -0.10555 | 0.99381 | -0.11807 | 20.2946
23 | -0.16767 | -0.042454 | 0.16775 | 0.042503 | 7.6942e-05 | 4.9076e-05 | 0.25183 | 0.25183 | 0.25183 | 0.99132 | -0.16584 | 0.99182 | -0.15629 | 34.5924
24 | 0.19721 | 0.05002 | -0.19711 | -0.049958 | 9.7276e-05 | 6.1641e-05 | 0.29549 | 0.29549 | 0.29549 | 0.99381 | -0.11807 | 0.99328 | -0.12833 | 20.2946
25 | 0.16797 | 0.042645 | -0.16775 | -0.042503 | 0.00022563 | 0.00014244 | 0.25183 | 0.25183 | 0.25183 | 0.99328 | -0.12833 | 0.99182 | -0.15629 | 17.2962
26 | 0.02914 | 0.0073128 | -0.029114 | -0.0072968 | 2.5753e-05 | 1.6016e-05 | 0.043658 | 0.043658 | 0.043658 | 0.99328 | -0.12833 | 0.99232 | -0.14688 | 11.994
27 | 0.07824 | 0.019667 | -0.078169 | -0.019622 | 7.0767e-05 | 4.5114e-05 | 0.1174 | 0.1174 | 0.1174 | 0.99186 | -0.15625 | 0.99088 | -0.17521 | 32.2524
28 | 0.0066666 | 0.0016708 | -0.0066662 | -0.0016707 | 4.1936e-07 | 1.3167e-07 | 0.010137 | 0.010137 | 0.010137 | 0.97859 | -0.41296 | 0.97852 | -0.41428 | 2.7849
29 | 0.068171 | 0.017116 | -0.068128 | -0.017088 | 4.3591e-05 | 2.7755e-05 | 0.10238 | 0.10238 | 0.10238 | 0.99088 | -0.17521 | 0.99018 | -0.18862 | 28.1277
30 | 0.03029 | 0.0075927 | -0.030287 | -0.0075906 | 3.2967e-06 | 2.0553e-06 | 0.045519 | 0.045519 | 0.045519 | 0.99018 | -0.18862 | 0.99007 | -0.1909 | 12.5053
31 | 0.037838 | 0.0094958 | -0.037804 | -0.0094745 | 3.395e-05 | 2.1368e-05 | 0.056866 | 0.056866 | 0.056866 | 0.99018 | -0.18862 | 0.98921 | -0.20745 | 15.6224
32 | 0.014956 | 0.0037482 | -0.014955 | -0.0037482 | 1.0685e-07 | 6.113e-08 | 0.022477 | 0.022477 | 0.022477 | 0.99007 | -0.1909 | 0.99006 | -0.19105 | 6.1751

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53794 | 0.13597

## res_load
| p_mw | q_mvar
0 | 0.071314 | 0.017873
1 | 0.040129 | 0.010057
2 | 0.050984 | 0.012778
3 | 0.011658 | 0.0029218
4 | 0.010989 | 0.0027542
5 | 0.042178 | 0.010571
6 | 0.031333 | 0.0078528
7 | 0.0059671 | 0.0014955
8 | 0.068766 | 0.017234
9 | 0.020292 | 0.0050855
10 | 0.047349 | 0.011867
11 | 0.029114 | 0.0072968
12 | 0.010942 | 0.0027423
13 | 0.0064725 | 0.0016222
14 | 0.0066662 | 0.0016707
15 | 0.009998 | 0.0025057
16 | 0.015331 | 0.0038423
17 | 0.037804 | 0.0094745
18 | 0.014955 | 0.0037482

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1