## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1510-12_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1510-12_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1510-12_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1510-12_0_3_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_1510-12_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1510-12_0_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1510-12_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1510-12_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1510-12_0_3_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_1510-12_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1510-12_0_3_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_1510-12_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1510-12_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1510-12_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1510-12_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1510-12_0_3_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_1510-12_0_3_node_47 | 0.4 | n |  | TRUE
17 | bus_LV_1510-12_0_3_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_1510-12_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1510-12_0_3_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1510-12_0_3_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1510-12_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1510-12_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1510-12_0_3_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_1510-12_0_3_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_1510-12_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_1510-12_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1510-12_0_3_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_1510-12_0_3_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1510-12_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1510-12_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_1510-12_0_3_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1510-12_0_3_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1510-12_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1510-12_0_3_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_1510-12_0_3_node_38 | 0.4 | n |  | TRUE
36 | bus_LV_1510-12_0_3_node_42 | 0.4 | n |  | TRUE
37 | bus_LV_1510-12_0_3_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_1510-12_0_3_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_1510-12_0_3_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_1510-12_0_3_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_1510-12_0_3_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_1510-12_0_3_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_1510-12_0_3_node_49 | 0.4 | n |  | TRUE
44 | bus_MV_143_0_node_79 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1510-12_0_3_load_0 | 0 | 0.011806 | 0.0029588 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1510-12_0_3_load_1 | 1 | 0.004602 | 0.0011534 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1510-12_0_3_load_6 | 3 | 0.0036903 | 0.00092488 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1510-12_0_3_load_3 | 4 | 0.013941 | 0.0034939 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1510-12_0_3_load_7 | 5 | 0.0059325 | 0.0014868 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1510-12_0_3_load_4 | 6 | 0.012873 | 0.0032264 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1510-12_0_3_load_5 | 7 | 0.020535 | 0.0051465 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1510-12_0_3_load_12 | 9 | 0.020477 | 0.0051321 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1510-12_0_3_load_8 | 11 | 0.015434 | 0.0038681 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1510-12_0_3_load_9 | 12 | 0.0083117 | 0.0020831 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1510-12_0_3_load_10 | 13 | 0.011412 | 0.00286 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1510-12_0_3_load_11 | 14 | 0.002109 | 0.00052857 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1510-12_0_3_load_13 | 18 | 0.02438 | 0.0061102 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1510-12_0_3_load_14 | 19 | 0.028419 | 0.0071226 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1510-12_0_3_load_18 | 22 | 0.017102 | 0.0042863 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1510-12_0_3_load_31 | 23 | 0.010043 | 0.0025171 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1510-12_0_3_load_32 | 24 | 0.0067557 | 0.0016931 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1510-12_0_3_load_28 | 25 | 0.013577 | 0.0034027 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1510-12_0_3_load_27 | 26 | 0.014661 | 0.0036745 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1510-12_0_3_load_33 | 27 | 0.0059689 | 0.001496 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1510-12_0_3_load_19 | 28 | 0.034425 | 0.0086278 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1510-12_0_3_load_26 | 32 | 0.0027326 | 0.00068486 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1510-12_0_3_load_25 | 33 | 0.0063512 | 0.0015918 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1510-12_0_3_load_41 | 34 | 0.016124 | 0.004041 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1510-12_0_3_load_38 | 35 | 0.015782 | 0.0039553 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1510-12_0_3_load_42 | 36 | 0.0025342 | 0.00063513 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1510-12_0_3_load_39 | 37 | 0.0043018 | 0.0010781 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1510-12_0_3_load_43 | 38 | 0.0019291 | 0.00048347 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1510-12_0_3_load_44 | 39 | 0.0043506 | 0.0010904 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1510-12_0_3_load_34 | 41 | 0.0078807 | 0.0019751 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1510-12_0_3_load_49 | 43 | 0.015181 | 0.0038048 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1510-12_0_3_line_0 |  | 0 | 1 | 0.021922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1510-12_0_3_line_1 |  | 1 | 2 | 0.0085667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1510-12_0_3_line_2 |  | 2 | 3 | 0.013001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1510-12_0_3_line_3 |  | 2 | 4 | 0.020288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1510-12_0_3_line_4 |  | 3 | 5 | 0.015097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1510-12_0_3_line_5 |  | 4 | 6 | 0.028857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1510-12_0_3_line_6 |  | 6 | 7 | 0.0010164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1510-12_0_3_line_7 |  | 7 | 8 | 0.016225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1510-12_0_3_line_8 |  | 8 | 9 | 0.012283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_1510-12_0_3_line_9 |  | 8 | 10 | 0.028151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1510-12_0_3_line_10 |  | 9 | 13 | 0.016738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1510-12_0_3_line_11 |  | 10 | 23 | 0.020868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1510-12_0_3_line_12 |  | 10 | 26 | 0.043272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1510-12_0_3_line_13 |  | 11 | 12 | 0.0030182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1510-12_0_3_line_14 |  | 11 | 13 | 0.031243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1510-12_0_3_line_15 |  | 12 | 14 | 0.014178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1510-12_0_3_line_16 |  | 14 | 15 | 0.061401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1510-12_0_3_line_17 |  | 15 | 16 | 0.047878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1510-12_0_3_line_18 |  | 15 | 17 | 0.20093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1510-12_0_3_line_19 |  | 16 | 43 | 0.06229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1510-12_0_3_line_20 |  | 17 | 42 | 0.014606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1510-12_0_3_line_21 |  | 17 | 41 | 0.019878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1510-12_0_3_line_22 |  | 18 | 19 | 0.062216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1510-12_0_3_line_23 |  | 18 | 20 | 0.012221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1510-12_0_3_line_24 |  | 20 | 21 | 0.014837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1510-12_0_3_line_25 |  | 20 | 22 | 0.015349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1510-12_0_3_line_26 |  | 21 | 23 | 0.0072674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1510-12_0_3_line_27 |  | 22 | 24 | 0.016805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_1510-12_0_3_line_28 |  | 24 | 27 | 0.038136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1510-12_0_3_line_29 |  | 25 | 26 | 0.0052122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1510-12_0_3_line_30 |  | 28 | 29 | 0.0048899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1510-12_0_3_line_31 |  | 29 | 30 | 0.051151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_1510-12_0_3_line_32 |  | 29 | 31 | 0.028511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1510-12_0_3_line_33 |  | 30 | 32 | 0.02825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1510-12_0_3_line_34 |  | 30 | 33 | 0.02122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1510-12_0_3_line_35 |  | 31 | 34 | 0.01281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1510-12_0_3_line_36 |  | 31 | 35 | 0.02017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1510-12_0_3_line_37 |  | 32 | 36 | 0.0028509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1510-12_0_3_line_38 |  | 35 | 37 | 0.008335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1510-12_0_3_line_39 |  | 36 | 38 | 0.012258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1510-12_0_3_line_40 |  | 38 | 42 | 0.022122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_1510-12_0_3_line_41 |  | 39 | 40 | 0.085902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1510-12_0_3_line_42 |  | 40 | 43 | 0.20912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1510-12_0_3_trafo_33 | 0.63 MVA 20/0.4 kV | 44 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2668689.5891 | 1203240.2036 | 2668701.6234 | 1203221.8803
1 | 2668706.3263 | 1203214.7199 | 2668701.6234 | 1203221.8803
2 | 2668706.3263 | 1203214.7199 | 2668713.0597 | 1203203.598
3 | 2668706.3263 | 1203214.7199 | 2668714.8844 | 1203215.6077 | 2668725.7046 | 1203220.0163
4 | 2668720.8783 | 1203190.6838 | 2668713.0597 | 1203203.598
5 | 2668725.7046 | 1203220.0163 | 2668730.9185 | 1203222.1406 | 2668749.9516 | 1203235.4538
6 | 2668750.7844 | 1203236.0363 | 2668749.9516 | 1203235.4538
7 | 2668764.0799 | 1203245.3362 | 2668750.7844 | 1203236.0363
8 | 2668764.0799 | 1203245.3362 | 2668756.3266 | 1203254.863
9 | 2668783.589 | 1203224.9928 | 2668764.0799 | 1203245.3362
10 | 2668756.3266 | 1203254.863 | 2668745.7611 | 1203267.8454
11 | 2668783.589 | 1203224.9928 | 2668798.0305 | 1203209.9285
12 | 2668783.589 | 1203224.9928 | 2668793.5751 | 1203235.3474 | 2668801.626 | 1203244.5901 | 2668807.9679 | 1203243.6515 | 2668816.1033 | 1203237.469
13 | 2668724.1351 | 1203294.4182 | 2668726.0402 | 1203292.0773
14 | 2668745.7611 | 1203267.8454 | 2668726.0402 | 1203292.0773
15 | 2668724.1351 | 1203294.4182 | 2668715.1857 | 1203305.4147
16 | 2668676.4282 | 1203353.0379 | 2668715.1857 | 1203305.4147
17 | 2668711.7357 | 1203385.4191 | 2668693.1589 | 1203369.7626 | 2668676.4282 | 1203353.0379
18 | 2668643.0585 | 1203204.998 | 2668632.8673 | 1203216.4323 | 2668625.1091 | 1203222.747 | 2668604.0273 | 1203234.3119 | 2668607.5469 | 1203243.2356 | 2668608.9283 | 1203246.8536 | 2668604.6386 | 1203251.9741 | 2668598.5619 | 1203258.3193 | 2668607.0692 | 1203268.9234 | 2668617.664 | 1203282.609 | 2668622.1977 | 1203288.0421 | 2668624.517 | 1203290.826 | 2668651.7562 | 1203323.4698 | 2668657.0179 | 1203329.7785 | 2668670.1574 | 1203345.817 | 2668676.4282 | 1203353.0379
19 | 2668750.9304 | 1203337.2407 | 2668748.1123 | 1203343.412 | 2668711.7357 | 1203385.4191
20 | 2668653.2841 | 1203194.5424 | 2668643.0585 | 1203204.998
21 | 2668643.0585 | 1203204.998 | 2668657.9087 | 1203218.2125
22 | 2668848.104 | 1203136.6384 | 2668837.6424 | 1203146.8234 | 2668835.8387 | 1203156.086 | 2668837.9274 | 1203160.3904 | 2668841.0654 | 1203164.0955 | 2668840.4791 | 1203164.7892 | 2668835.8293 | 1203170.1055 | 2668831.5575 | 1203174.9704 | 2668821.8014 | 1203185.1416
23 | 2668813.3421 | 1203193.961 | 2668821.8014 | 1203185.1416
24 | 2668813.3421 | 1203193.961 | 2668803.0598 | 1203204.6824
25 | 2668813.3421 | 1203193.961 | 2668801.3651 | 1203184.3619
26 | 2668803.0598 | 1203204.6824 | 2668798.0305 | 1203209.9285
27 | 2668788.2519 | 1203173.8522 | 2668801.3651 | 1203184.3619
28 | 2668762.2568 | 1203189.0704 | 2668766.8365 | 1203181.7293 | 2668769.3824 | 1203173.4202 | 2668774.9262 | 1203170.4266 | 2668784.1098 | 1203170.5324 | 2668788.2519 | 1203173.8522
29 | 2668820.2531 | 1203234.3154 | 2668816.1033 | 1203237.469
30 | 2668739.1031 | 1203115.9814 | 2668742.8128 | 1203112.7955
31 | 2668699.338 | 1203148.1547 | 2668712.5875 | 1203137.4672 | 2668728.4946 | 1203124.6424 | 2668739.1031 | 1203115.9814
32 | 2668718.6388 | 1203103.594 | 2668725.6037 | 1203112.6685 | 2668734.1837 | 1203109.6876 | 2668735.8869 | 1203111.7863 | 2668739.1031 | 1203115.9814
33 | 2668699.338 | 1203148.1547 | 2668692.6957 | 1203153.3704 | 2668678.4046 | 1203167.0809
34 | 2668699.338 | 1203148.1547 | 2668690.9879 | 1203139.7536 | 2668683.8998 | 1203145.8901
35 | 2668718.6388 | 1203103.594 | 2668714.4614 | 1203099.5991 | 2668712.9601 | 1203099.126 | 2668707.5838 | 1203098.2009
36 | 2668718.6388 | 1203103.594 | 2668713.5865 | 1203108.8391 | 2668701.0278 | 1203111.7298 | 2668701.0278 | 1203111.7298
37 | 2668678.4046 | 1203167.0809 | 2668676.3474 | 1203169.0545
38 | 2668701.0278 | 1203111.7298 | 2668692.6946 | 1203111.5587
39 | 2668668.0427 | 1203178.0625 | 2668674.6598 | 1203170.6736 | 2668676.3474 | 1203169.0545
40 | 2668653.2841 | 1203194.5424 | 2668668.0427 | 1203178.0625
41 | 2668951.2297 | 1203397.3519 | 2668961.1426 | 1203392.2521 | 2669007.971 | 1203370.4461 | 2669030.7183 | 1203366.4412
42 | 2668750.9304 | 1203337.2407 | 2668951.2297 | 1203397.3519

## bus_geodata
| x | y | coords
0 | 2668689.5891 | 1203240.2036
1 | 2668701.6234 | 1203221.8803
2 | 2668706.3263 | 1203214.7199
3 | 2668713.0597 | 1203203.598
4 | 2668725.7046 | 1203220.0163
5 | 2668720.8783 | 1203190.6838
6 | 2668749.9516 | 1203235.4538
7 | 2668750.7844 | 1203236.0363
8 | 2668764.0799 | 1203245.3362
9 | 2668756.3266 | 1203254.863
10 | 2668783.589 | 1203224.9928
11 | 2668726.0402 | 1203292.0773
12 | 2668724.1351 | 1203294.4182
13 | 2668745.7611 | 1203267.8454
14 | 2668715.1857 | 1203305.4147
15 | 2668676.4282 | 1203353.0379
16 | 2668711.7357 | 1203385.4191
17 | 2668643.0585 | 1203204.998
18 | 2668821.8014 | 1203185.1416
19 | 2668848.104 | 1203136.6384
20 | 2668813.3421 | 1203193.961
21 | 2668803.0598 | 1203204.6824
22 | 2668801.3651 | 1203184.3619
23 | 2668798.0305 | 1203209.9285
24 | 2668788.2519 | 1203173.8522
25 | 2668820.2531 | 1203234.3154
26 | 2668816.1033 | 1203237.469
27 | 2668762.2568 | 1203189.0704
28 | 2668742.8128 | 1203112.7955
29 | 2668739.1031 | 1203115.9814
30 | 2668699.338 | 1203148.1547
31 | 2668718.6388 | 1203103.594
32 | 2668678.4046 | 1203167.0809
33 | 2668683.8998 | 1203145.8901
34 | 2668707.5838 | 1203098.2009
35 | 2668701.0278 | 1203111.7298
36 | 2668676.3474 | 1203169.0545
37 | 2668692.6946 | 1203111.5587
38 | 2668668.0427 | 1203178.0625
39 | 2669030.7183 | 1203366.4412
40 | 2668951.2297 | 1203397.3519
41 | 2668657.9087 | 1203218.2125
42 | 2668653.2841 | 1203194.5424
43 | 2668750.9304 | 1203337.2407
44 | 2668758.5179 | 1203195.0639

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98357 | -0.3151 | 0.011806 | 0.0029588
1 | 0.98381 | -0.31044 | 0.004602 | 0.0011534
2 | 0.98394 | -0.30791 | 0 | 0
3 | 0.98383 | -0.31016 | 0.0036903 | 0.00092488
4 | 0.98443 | -0.29841 | 0.013941 | 0.0034939
5 | 0.98374 | -0.31178 | 0.0059325 | 0.0014868
6 | 0.98549 | -0.27768 | 0.012873 | 0.0032264
7 | 0.98554 | -0.27672 | 0.020535 | 0.0051465
8 | 0.98664 | -0.25538 | 0 | 0
9 | 0.98599 | -0.2678 | 0.020477 | 0.0051321
10 | 0.98875 | -0.21467 | 0 | 0
11 | 0.98389 | -0.30846 | 0.015434 | 0.0038681
12 | 0.98378 | -0.31067 | 0.0083117 | 0.0020831
13 | 0.98522 | -0.28271 | 0.011412 | 0.00286
14 | 0.98328 | -0.32036 | 0.002109 | 0.00052857
15 | 0.98115 | -0.36164 | 0 | 0
16 | 0.98028 | -0.3786 | 0 | 0
17 | 0.9754 | -0.47397 | 0 | 0
18 | 0.99182 | -0.15582 | 0.02438 | 0.0061102
19 | 0.9902 | -0.18721 | 0.028419 | 0.0071226
20 | 0.99241 | -0.1444 | 0 | 0
21 | 0.99112 | -0.16903 | 0 | 0
22 | 0.99399 | -0.11422 | 0.017102 | 0.0042863
23 | 0.99049 | -0.18112 | 0.010043 | 0.0025171
24 | 0.9958 | -0.079595 | 0.0067557 | 0.0016931
25 | 0.98756 | -0.23775 | 0.013577 | 0.0034027
26 | 0.98763 | -0.23648 | 0.014661 | 0.0036745
27 | 1 | 0 | -0.36491 | -0.093189
28 | 0.97209 | -0.53905 | 0.034425 | 0.0086278
29 | 0.97225 | -0.53595 | 0 | 0
30 | 0.97337 | -0.51377 | 0 | 0
31 | 0.97193 | -0.54229 | 0 | 0
32 | 0.97405 | -0.50044 | 0.0027326 | 0.00068486
33 | 0.97325 | -0.51624 | 0.0063512 | 0.0015918
34 | 0.97174 | -0.54611 | 0.016124 | 0.004041
35 | 0.97174 | -0.54603 | 0.015782 | 0.0039553
36 | 0.97412 | -0.49904 | 0.0025342 | 0.00063513
37 | 0.97171 | -0.54669 | 0.0043018 | 0.0010781
38 | 0.97443 | -0.49287 | 0.0019291 | 0.00048347
39 | 0.97796 | -0.42409 | 0.0043506 | 0.0010904
40 | 0.97831 | -0.41728 | 0 | 0
41 | 0.97525 | -0.47684 | 0.0078807 | 0.0019751
42 | 0.97501 | -0.48148 | 0 | 0
43 | 0.97915 | -0.4007 | 0.015181 | 0.0038048
44 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.011806 | -0.0029588 | 0.011809 | 0.0029602 | 2.6224e-06 | 1.4001e-06 | 0.017861 | 0.017861 | 0.017861 | 0.98357 | -0.3151 | 0.98381 | -0.31044 | 4.9068
1 | -0.016411 | -0.0041136 | 0.016413 | 0.0041148 | 1.9792e-06 | 1.1579e-06 | 0.024821 | 0.024821 | 0.024821 | 0.98381 | -0.31044 | 0.98394 | -0.30791 | 6.819
2 | 0.0096243 | 0.0024123 | -0.0096233 | -0.0024118 | 1.0329e-06 | 4.9592e-07 | 0.014555 | 0.014555 | 0.014555 | 0.98394 | -0.30791 | 0.98383 | -0.31016 | 3.9986
3 | -0.026037 | -0.0065271 | 0.026049 | 0.0065344 | 1.1796e-05 | 7.2916e-06 | 0.039376 | 0.039376 | 0.039376 | 0.98394 | -0.30791 | 0.98443 | -0.29841 | 10.8176
4 | 0.005933 | 0.0014869 | -0.0059325 | -0.0014868 | 4.5586e-07 | 1.0007e-07 | 0.0089735 | 0.0089735 | 0.0089735 | 0.98383 | -0.31016 | 0.98374 | -0.31178 | 2.4653
5 | -0.039989 | -0.010028 | 0.040029 | 0.010053 | 3.9541e-05 | 2.4939e-05 | 0.060448 | 0.060448 | 0.060448 | 0.98443 | -0.29841 | 0.98549 | -0.27768 | 16.6067
6 | -0.052902 | -0.01328 | 0.052905 | 0.013281 | 2.4324e-06 | 1.5438e-06 | 0.079886 | 0.079886 | 0.079886 | 0.98549 | -0.27768 | 0.98554 | -0.27672 | 21.9467
7 | -0.07344 | -0.018428 | 0.073514 | 0.018475 | 7.4818e-05 | 4.7677e-05 | 0.11089 | 0.11089 | 0.11089 | 0.98554 | -0.27672 | 0.98664 | -0.25538 | 30.4644
8 | 0.1708 | 0.043352 | -0.1707 | -0.043287 | 0.00010204 | 6.4833e-05 | 0.25779 | 0.25779 | 0.25779 | 0.98664 | -0.25538 | 0.98599 | -0.2678 | 23.6073
9 | -0.24432 | -0.061827 | 0.24479 | 0.062132 | 0.00047831 | 0.00030504 | 0.36868 | 0.36868 | 0.36868 | 0.98664 | -0.25538 | 0.98875 | -0.21467 | 33.7621
10 | 0.15022 | 0.038155 | -0.15011 | -0.038087 | 0.00010771 | 6.8293e-05 | 0.22689 | 0.22689 | 0.22689 | 0.98599 | -0.2678 | 0.98522 | -0.28271 | 20.7774
11 | -0.27306 | -0.069228 | 0.2735 | 0.06951 | 0.00044113 | 0.00028152 | 0.41123 | 0.41123 | 0.41123 | 0.98875 | -0.21467 | 0.99049 | -0.18112 | 37.6582
12 | 0.028269 | 0.0070959 | -0.028239 | -0.0070776 | 2.9374e-05 | 1.8245e-05 | 0.042547 | 0.042547 | 0.042547 | 0.98875 | -0.21467 | 0.98763 | -0.23648 | 11.6887
13 | 0.1231 | 0.03125 | -0.12308 | -0.031242 | 1.3096e-05 | 8.2664e-06 | 0.18631 | 0.18631 | 0.18631 | 0.98389 | -0.30846 | 0.98378 | -0.31067 | 17.0616
14 | -0.13853 | -0.035118 | 0.1387 | 0.035227 | 0.00017166 | 0.00010867 | 0.20965 | 0.20965 | 0.20965 | 0.98389 | -0.30846 | 0.98522 | -0.28271 | 19.1991
15 | 0.11477 | 0.029159 | -0.11472 | -0.029125 | 5.3497e-05 | 3.3698e-05 | 0.17374 | 0.17374 | 0.17374 | 0.98378 | -0.31067 | 0.98328 | -0.32036 | 15.9103
16 | 0.11261 | 0.028596 | -0.11239 | -0.028456 | 0.00022325 | 0.00014055 | 0.17055 | 0.17055 | 0.17055 | 0.98328 | -0.32036 | 0.98115 | -0.36164 | 15.6181
17 | 0.019573 | 0.0049165 | -0.019557 | -0.004907 | 1.5826e-05 | 9.5243e-06 | 0.029689 | 0.029689 | 0.029689 | 0.98115 | -0.36164 | 0.98028 | -0.3786 | 8.1564
18 | 0.092813 | 0.023539 | -0.092315 | -0.023228 | 0.00049835 | 0.00031138 | 0.14086 | 0.14086 | 0.14086 | 0.98115 | -0.36164 | 0.9754 | -0.47397 | 12.8996
19 | 0.019557 | 0.004907 | -0.019537 | -0.0048946 | 2.059e-05 | 1.2393e-05 | 0.029689 | 0.029689 | 0.029689 | 0.98028 | -0.3786 | 0.97915 | -0.4007 | 8.1565
20 | 0.084433 | 0.021252 | -0.084403 | -0.021234 | 3.0307e-05 | 1.885e-05 | 0.12884 | 0.12884 | 0.12884 | 0.9754 | -0.47397 | 0.97501 | -0.48148 | 11.7985
21 | 0.0078818 | 0.0019755 | -0.0078807 | -0.0019751 | 1.0778e-06 | 4.4169e-07 | 0.012024 | 0.012024 | 0.012024 | 0.9754 | -0.47397 | 0.97525 | -0.47684 | 3.3033
22 | 0.028462 | 0.007149 | -0.028419 | -0.0071226 | 4.2553e-05 | 2.6432e-05 | 0.042707 | 0.042707 | 0.042707 | 0.99182 | -0.15582 | 0.9902 | -0.18721 | 11.7327
23 | -0.052842 | -0.013259 | 0.052871 | 0.013277 | 2.8807e-05 | 1.8278e-05 | 0.079284 | 0.079284 | 0.079284 | 0.99182 | -0.15582 | 0.99241 | -0.1444 | 21.7813
24 | 0.28405 | 0.072347 | -0.28371 | -0.072132 | 0.00033707 | 0.00021515 | 0.42632 | 0.42632 | 0.42632 | 0.99241 | -0.1444 | 0.99112 | -0.16903 | 39.0399
25 | -0.33692 | -0.085625 | 0.33741 | 0.085938 | 0.00049046 | 0.0003133 | 0.5056 | 0.5056 | 0.5056 | 0.99241 | -0.1444 | 0.99399 | -0.11422 | 46.3003
26 | 0.28371 | 0.072132 | -0.28355 | -0.072027 | 0.0001651 | 0.00010538 | 0.42632 | 0.42632 | 0.42632 | 0.99112 | -0.16903 | 0.99049 | -0.18112 | 39.0399
27 | -0.35451 | -0.090224 | 0.35511 | 0.090603 | 0.00059274 | 0.0003787 | 0.5312 | 0.5312 | 0.5312 | 0.99399 | -0.11422 | 0.9958 | -0.079595 | 48.6448
28 | -0.36186 | -0.092296 | 0.36326 | 0.093189 | 0.0013967 | 0.00089241 | 0.5413 | 0.5413 | 0.5413 | 0.9958 | -0.079595 | 1 | 0 | 49.5692
29 | -0.013577 | -0.0034027 | 0.013578 | 0.0034032 | 8.1799e-07 | 4.5682e-07 | 0.020457 | 0.020457 | 0.020457 | 0.98756 | -0.23775 | 0.98763 | -0.23648 | 5.6201
30 | -0.034425 | -0.0086278 | 0.03443 | 0.008631 | 5.0919e-06 | 3.1982e-06 | 0.052696 | 0.052696 | 0.052696 | 0.97209 | -0.53905 | 0.97225 | -0.53595 | 14.4769
31 | -0.070655 | -0.017715 | 0.07073 | 0.017761 | 7.477e-05 | 4.5948e-05 | 0.10814 | 0.10814 | 0.10814 | 0.97225 | -0.53595 | 0.97337 | -0.51377 | 9.9029
32 | 0.036225 | 0.0090839 | -0.036214 | -0.009078 | 1.0956e-05 | 5.9512e-06 | 0.055444 | 0.055444 | 0.055444 | 0.97225 | -0.53595 | 0.97193 | -0.54229 | 5.0773
33 | -0.077082 | -0.019353 | 0.077131 | 0.019383 | 4.9043e-05 | 3.0333e-05 | 0.11785 | 0.11785 | 0.11785 | 0.97337 | -0.51377 | 0.97405 | -0.50044 | 10.7921
34 | 0.006352 | 0.001592 | -0.0063512 | -0.0015918 | 7.5034e-07 | 2.1649e-07 | 0.0097104 | 0.0097105 | 0.0097105 | 0.97337 | -0.51377 | 0.97325 | -0.51624 | 2.6677
35 | 0.016127 | 0.0040427 | -0.016124 | -0.004041 | 2.9283e-06 | 1.7154e-06 | 0.02469 | 0.02469 | 0.02469 | 0.97193 | -0.54229 | 0.97174 | -0.54611 | 6.783
36 | 0.020088 | 0.0050353 | -0.020084 | -0.0050335 | 3.5769e-06 | 1.7894e-06 | 0.030754 | 0.030754 | 0.030754 | 0.97193 | -0.54229 | 0.97174 | -0.54603 | 4.2245
37 | -0.079864 | -0.020068 | 0.079869 | 0.020071 | 5.3061e-06 | 3.2894e-06 | 0.12202 | 0.12202 | 0.12202 | 0.97405 | -0.50044 | 0.97412 | -0.49904 | 11.1743
38 | 0.004302 | 0.0010781 | -0.0043018 | -0.0010781 | 1.3564e-07 | -1.6443e-08 | 0.0065876 | 0.0065876 | 0.0065876 | 0.97174 | -0.54603 | 0.97171 | -0.54669 | 1.8098
39 | -0.082403 | -0.020706 | 0.082428 | 0.020721 | 2.4284e-05 | 1.5084e-05 | 0.12589 | 0.12589 | 0.12589 | 0.97412 | -0.49904 | 0.97443 | -0.49287 | 11.5288
40 | -0.084357 | -0.021205 | 0.084403 | 0.021234 | 4.5903e-05 | 2.8551e-05 | 0.12884 | 0.12884 | 0.12884 | 0.97443 | -0.49287 | 0.97501 | -0.48148 | 11.7985
41 | -0.0043506 | -0.0010904 | 0.004352 | 0.0010902 | 1.4115e-06 | -1.7487e-07 | 0.0066197 | 0.0066193 | 0.0066197 | 0.97796 | -0.42409 | 0.97831 | -0.41728 | 1.8186
42 | -0.004352 | -0.0010902 | 0.0043555 | 0.0010898 | 3.4356e-06 | -4.2936e-07 | 0.0066193 | 0.0066183 | 0.0066193 | 0.97831 | -0.41728 | 0.97915 | -0.4007 | 1.8185

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37088 | 0.094685

## res_load
| p_mw | q_mvar
0 | 0.011806 | 0.0029588
1 | 0.004602 | 0.0011534
2 | 0.0036903 | 0.00092488
3 | 0.013941 | 0.0034939
4 | 0.0059325 | 0.0014868
5 | 0.012873 | 0.0032264
6 | 0.020535 | 0.0051465
7 | 0.020477 | 0.0051321
8 | 0.015434 | 0.0038681
9 | 0.0083117 | 0.0020831
10 | 0.011412 | 0.00286
11 | 0.002109 | 0.00052857
12 | 0.02438 | 0.0061102
13 | 0.028419 | 0.0071226
14 | 0.017102 | 0.0042863
15 | 0.010043 | 0.0025171
16 | 0.0067557 | 0.0016931
17 | 0.013577 | 0.0034027
18 | 0.014661 | 0.0036745
19 | 0.0059689 | 0.001496
20 | 0.034425 | 0.0086278
21 | 0.0027326 | 0.00068486
22 | 0.0063512 | 0.0015918
23 | 0.016124 | 0.004041
24 | 0.015782 | 0.0039553
25 | 0.0025342 | 0.00063513
26 | 0.0043018 | 0.0010781
27 | 0.0019291 | 0.00048347
28 | 0.0043506 | 0.0010904
29 | 0.0078807 | 0.0019751
30 | 0.015181 | 0.0038048

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1