## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1510-15_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1510-15_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1510-15_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1510-15_0_4_node_30 | 0.4 | n |  | TRUE
4 | bus_LV_1510-15_0_4_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_1510-15_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1510-15_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1510-15_0_4_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_1510-15_0_4_node_33 | 0.4 | n |  | TRUE
9 | bus_LV_1510-15_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1510-15_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1510-15_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1510-15_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1510-15_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1510-15_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1510-15_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1510-15_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1510-15_0_4_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1510-15_0_4_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_1510-15_0_4_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_1510-15_0_4_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_1510-15_0_4_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_1510-15_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_1510-15_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1510-15_0_4_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_1510-15_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1510-15_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1510-15_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1510-15_0_4_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1510-15_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1510-15_0_4_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_1510-15_0_4_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_1510-15_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_1510-15_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1510-15_0_4_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_1510-15_0_4_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_1510-15_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1510-15_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_1510-15_0_4_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_1510-15_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1510-15_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_MV_143_0_node_137 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1510-15_0_4_load_0 | 0 | 0.0073265 | 0.0018362 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1510-15_0_4_load_1 | 1 | 0.0085846 | 0.0021515 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1510-15_0_4_load_30 | 3 | 0.017974 | 0.0045047 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1510-15_0_4_load_28 | 4 | 0.00018492 | 4.6345e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1510-15_0_4_load_3 | 5 | 0.0032388 | 0.00081172 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1510-15_0_4_load_4 | 6 | 0.001971 | 0.00049398 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1510-15_0_4_load_32 | 7 | 0.0029622 | 0.00074239 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1510-15_0_4_load_33 | 8 | 0.0026788 | 0.00067137 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1510-15_0_4_load_5 | 9 | 0.0045892 | 0.0011502 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1510-15_0_4_load_6 | 10 | 0.022992 | 0.0057624 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1510-15_0_4_load_7 | 11 | 0.00029032 | 7.276e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1510-15_0_4_load_9 | 13 | 0.0001411 | 3.5363e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1510-15_0_4_load_12 | 16 | 0.00018395 | 4.6103e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1510-15_0_4_load_25 | 17 | 0.025425 | 0.0063721 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1510-15_0_4_load_35 | 19 | 0.029649 | 0.0074308 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1510-15_0_4_load_29 | 20 | 0.00026917 | 6.7461e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1510-15_0_4_load_36 | 21 | 0.12482 | 0.031282 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1510-15_0_4_load_23 | 22 | 0.0087769 | 0.0021997 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1510-15_0_4_load_19 | 23 | 0.005874 | 0.0014722 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1510-15_0_4_load_40 | 24 | 0.0022936 | 0.00057484 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1510-15_0_4_load_13 | 25 | 0.0096067 | 0.0024077 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1510-15_0_4_load_14 | 26 | 0.0069077 | 0.0017312 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1510-15_0_4_load_15 | 27 | 0.0067849 | 0.0017004 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1510-15_0_4_load_16 | 28 | 0.0048513 | 0.0012159 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1510-15_0_4_load_17 | 29 | 0.0041267 | 0.0010342 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1510-15_0_4_load_31 | 30 | 0.0021894 | 0.00054872 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1510-15_0_4_load_38 | 31 | 0.001944 | 0.00048721 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1510-15_0_4_load_18 | 32 | 0.0079991 | 0.0020048 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1510-15_0_4_load_24 | 35 | 0.0064296 | 0.0016114 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1510-15_0_4_load_26 | 36 | 0.0064296 | 0.0016114 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1510-15_0_4_load_27 | 37 | 0.0038939 | 0.0009759 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1510-15_0_4_load_37 | 38 | 0.062263 | 0.015604 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1510-15_0_4_load_34 | 39 | 0.0026072 | 0.00065342 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1510-15_0_4_load_39 | 40 | 9.6503e-05 | 2.4186e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1510-15_0_4_line_0 |  | 0 | 1 | 0.004651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1510-15_0_4_line_1 |  | 1 | 2 | 0.013402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1510-15_0_4_line_2 |  | 2 | 5 | 0.022325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1510-15_0_4_line_3 |  | 2 | 3 | 0.058704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1510-15_0_4_line_4 |  | 3 | 4 | 0.019379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1510-15_0_4_line_5 |  | 4 | 20 | 0.01165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1510-15_0_4_line_6 |  | 5 | 6 | 0.015887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1510-15_0_4_line_7 |  | 6 | 7 | 0.012722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1510-15_0_4_line_8 |  | 7 | 8 | 0.0062716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1510-15_0_4_line_9 |  | 8 | 39 | 0.014165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1510-15_0_4_line_10 |  | 9 | 10 | 0.010619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1510-15_0_4_line_11 |  | 9 | 11 | 0.011602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1510-15_0_4_line_12 |  | 10 | 12 | 0.023338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1510-15_0_4_line_13 |  | 11 | 13 | 0.018563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1510-15_0_4_line_14 |  | 12 | 14 | 0.020727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1510-15_0_4_line_15 |  | 12 | 15 | 0.032631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1510-15_0_4_line_16 |  | 13 | 16 | 0.020105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1510-15_0_4_line_17 |  | 14 | 17 | 0.015331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1510-15_0_4_line_18 |  | 14 | 18 | 0.03963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1510-15_0_4_line_19 |  | 15 | 19 | 0.016585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1510-15_0_4_line_20 |  | 16 | 20 | 0.0074407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1510-15_0_4_line_21 |  | 17 | 21 | 0.025473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_1510-15_0_4_line_22 |  | 18 | 22 | 0.026966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1510-15_0_4_line_23 |  | 18 | 23 | 0.021287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1510-15_0_4_line_24 |  | 19 | 24 | 0.025997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1510-15_0_4_line_25 |  | 21 | 38 | 0.0067153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1510-15_0_4_line_26 |  | 23 | 32 | 0.019303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1510-15_0_4_line_27 |  | 24 | 40 | 0.010388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1510-15_0_4_line_28 |  | 25 | 26 | 0.0035299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1510-15_0_4_line_29 |  | 25 | 27 | 0.025759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1510-15_0_4_line_30 |  | 26 | 28 | 0.030898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1510-15_0_4_line_31 |  | 28 | 29 | 0.032695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1510-15_0_4_line_32 |  | 29 | 30 | 0.016794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1510-15_0_4_line_33 |  | 30 | 31 | 0.0072178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1510-15_0_4_line_34 |  | 31 | 40 | 0.010887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1510-15_0_4_line_35 |  | 32 | 33 | 0.042578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1510-15_0_4_line_36 |  | 33 | 34 | 0.03052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1510-15_0_4_line_37 |  | 34 | 35 | 0.016735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1510-15_0_4_line_38 |  | 35 | 36 | 0.022518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1510-15_0_4_line_39 |  | 36 | 37 | 0.00017382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1510-15_0_4_trafo_11 | 0.63 MVA 20/0.4 kV | 41 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2668504.8079 | 1203017.7382 | 2668501.2216 | 1203014.7765
1 | 2668490.8877 | 1203006.2424 | 2668501.2216 | 1203014.7765
2 | 2668490.8877 | 1203006.2424 | 2668480.4772 | 1203025.9918
3 | 2668435.9698 | 1202985.5006 | 2668490.8877 | 1203006.2424
4 | 2668435.9698 | 1202985.5006 | 2668438.9633 | 1202966.3544
5 | 2668440.7628 | 1202954.8445 | 2668438.9633 | 1202966.3544
6 | 2668480.4772 | 1203025.9918 | 2668473.0689 | 1203040.046
7 | 2668473.0689 | 1203040.046 | 2668469.27 | 1203047.2528 | 2668467.7794 | 1203049.1591 | 2668465.9402 | 1203050.2832 | 2668465.9402 | 1203050.2832
8 | 2668459.7235 | 1203050.1342 | 2668463.5317 | 1203050.6225 | 2668465.9402 | 1203050.2832
9 | 2668459.7235 | 1203050.1342 | 2668445.674 | 1203048.3329
10 | 2668451.3177 | 1202887.3355 | 2668449.6773 | 1202897.8274
11 | 2668447.8851 | 1202909.2902 | 2668449.6773 | 1202897.8274
12 | 2668454.9227 | 1202864.2775 | 2668451.3177 | 1202887.3355
13 | 2668447.8851 | 1202909.2902 | 2668445.0178 | 1202927.6299
14 | 2668454.9227 | 1202864.2775 | 2668457.5175 | 1202843.717
15 | 2668422.5204 | 1202868.8537 | 2668454.9227 | 1202864.2775
16 | 2668445.0178 | 1202927.6299 | 2668441.9122 | 1202947.4931
17 | 2668457.5175 | 1202843.717 | 2668442.2732 | 1202842.0844
18 | 2668462.4809 | 1202804.4056 | 2668457.5175 | 1202843.717
19 | 2668422.5204 | 1202868.8537 | 2668418.1515 | 1202884.8534
20 | 2668441.9122 | 1202947.4931 | 2668440.7628 | 1202954.8445
21 | 2668442.2732 | 1202842.0844 | 2668416.9453 | 1202839.372
22 | 2668462.4809 | 1202804.4056 | 2668467.137 | 1202809.8178 | 2668472.8572 | 1202811.3732 | 2668486.482 | 1202814.1202
23 | 2668462.4809 | 1202804.4056 | 2668465.3184 | 1202783.309
24 | 2668411.9802 | 1202910.0994 | 2668415.1571 | 1202895.819 | 2668418.1515 | 1202884.8534
25 | 2668416.0927 | 1202846.0329 | 2668416.9453 | 1202839.372
26 | 2668465.3184 | 1202783.309 | 2668467.8915 | 1202764.178
27 | 2668409.7546 | 1202920.2464 | 2668410.1588 | 1202918.2865 | 2668411.9802 | 1202910.0994
28 | 2668379.269 | 1203016.4977 | 2668381.5072 | 1203013.7681
29 | 2668362.9352 | 1203036.4156 | 2668363.1966 | 1203036.0983 | 2668379.269 | 1203016.4977
30 | 2668395.4243 | 1202986.2142 | 2668382.2356 | 1203012.8798 | 2668381.5072 | 1203013.7681
31 | 2668395.4243 | 1202986.2142 | 2668396.6707 | 1202983.694 | 2668402.7062 | 1202954.4264
32 | 2668402.7062 | 1202954.4264 | 2668406.098 | 1202937.9783
33 | 2668406.098 | 1202937.9783 | 2668407.5558 | 1202930.9093
34 | 2668409.7546 | 1202920.2464 | 2668407.5558 | 1202930.9093
35 | 2668473.0989 | 1202721.9218 | 2668470.642 | 1202743.729 | 2668467.8915 | 1202764.178
36 | 2668473.0989 | 1202721.9218 | 2668503.3244 | 1202726.7378
37 | 2668503.3244 | 1202726.7378 | 2668500.9094 | 1202743.298
38 | 2668497.6599 | 1202765.5806 | 2668500.9094 | 1202743.298
39 | 2668497.6348 | 1202765.7526 | 2668497.6599 | 1202765.5806

## bus_geodata
| x | y | coords
0 | 2668504.8079 | 1203017.7382
1 | 2668501.2216 | 1203014.7765
2 | 2668490.8877 | 1203006.2424
3 | 2668435.9698 | 1202985.5006
4 | 2668438.9633 | 1202966.3544
5 | 2668480.4772 | 1203025.9918
6 | 2668473.0689 | 1203040.046
7 | 2668465.9402 | 1203050.2832
8 | 2668459.7235 | 1203050.1342
9 | 2668449.6773 | 1202897.8274
10 | 2668451.3177 | 1202887.3355
11 | 2668447.8851 | 1202909.2902
12 | 2668454.9227 | 1202864.2775
13 | 2668445.0178 | 1202927.6299
14 | 2668457.5175 | 1202843.717
15 | 2668422.5204 | 1202868.8537
16 | 2668441.9122 | 1202947.4931
17 | 2668442.2732 | 1202842.0845
18 | 2668462.4809 | 1202804.4056
19 | 2668418.1515 | 1202884.8534
20 | 2668440.7628 | 1202954.8445
21 | 2668416.9453 | 1202839.372
22 | 2668486.482 | 1202814.1202
23 | 2668465.3184 | 1202783.309
24 | 2668411.9802 | 1202910.0994
25 | 2668379.269 | 1203016.4977
26 | 2668381.5072 | 1203013.7681
27 | 2668362.9352 | 1203036.4156
28 | 2668395.4243 | 1202986.2142
29 | 2668402.7062 | 1202954.4264
30 | 2668406.098 | 1202937.9783
31 | 2668407.5558 | 1202930.9093
32 | 2668467.8915 | 1202764.178
33 | 2668473.0989 | 1202721.9218
34 | 2668503.3244 | 1202726.7378
35 | 2668500.9094 | 1202743.298
36 | 2668497.6599 | 1202765.5806
37 | 2668497.6348 | 1202765.7526
38 | 2668416.0927 | 1202846.0329
39 | 2668445.674 | 1203048.3329
40 | 2668409.7546 | 1202920.2464
41 | 2668454.9227 | 1202864.2775

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9889 | -0.21365 | 0.0073265 | 0.0018362
1 | 0.98893 | -0.21304 | 0.0085846 | 0.0021515
2 | 0.98913 | -0.20924 | 0 | 0
3 | 0.99071 | -0.17858 | 0.017974 | 0.0045047
4 | 0.99155 | -0.1623 | 0.00018492 | 4.6345e-05
5 | 0.98885 | -0.2146 | 0.0032388 | 0.00081172
6 | 0.9887 | -0.21749 | 0.001971 | 0.00049398
7 | 0.98861 | -0.21937 | 0.0029622 | 0.00074239
8 | 0.98858 | -0.21996 | 0.0026788 | 0.00067137
9 | 0.9946 | -0.10345 | 0.0045892 | 0.0011502
10 | 0.99512 | -0.09354 | 0.022992 | 0.0057624
11 | 0.99409 | -0.11336 | 0.00029032 | 7.276e-05
12 | 0.99674 | -0.062372 | 0 | 0
13 | 0.99327 | -0.12913 | 0.0001411 | 3.5363e-05
14 | 0.99515 | -0.092955 | 0 | 0
15 | 1 | 0 | -0.4006 | -0.10099
16 | 0.99238 | -0.14619 | 0.00018395 | 4.6103e-05
17 | 0.99415 | -0.11209 | 0.025425 | 0.0063721
18 | 0.99372 | -0.12048 | 0 | 0
19 | 0.99897 | -0.019809 | 0.029649 | 0.0074308
20 | 0.99206 | -0.15248 | 0.00026917 | 6.7461e-05
21 | 0.99198 | -0.1542 | 0.12482 | 0.031282
22 | 0.9935 | -0.12466 | 0.0087769 | 0.0021997
23 | 0.99312 | -0.132 | 0.005874 | 0.0014722
24 | 0.99805 | -0.037445 | 0.0022936 | 0.00057484
25 | 0.99507 | -0.094744 | 0.0096067 | 0.0024077
26 | 0.99513 | -0.093726 | 0.0069077 | 0.0017312
27 | 0.99492 | -0.097821 | 0.0067849 | 0.0017004
28 | 0.99578 | -0.081063 | 0.0048513 | 0.0012159
29 | 0.99662 | -0.064897 | 0.0041267 | 0.0010342
30 | 0.99712 | -0.055389 | 0.0021894 | 0.00054872
31 | 0.99734 | -0.051028 | 0.001944 | 0.00048721
32 | 0.99269 | -0.14045 | 0.0079991 | 0.0020048
33 | 0.99204 | -0.15307 | 0 | 0
34 | 0.99157 | -0.16213 | 0 | 0
35 | 0.99131 | -0.16711 | 0.0064296 | 0.0016114
36 | 0.9911 | -0.17123 | 0.0064296 | 0.0016114
37 | 0.9911 | -0.17124 | 0.0038939 | 0.0009759
38 | 0.99159 | -0.16161 | 0.062263 | 0.015604
39 | 0.98854 | -0.22062 | 0.0026072 | 0.00065342
40 | 0.9977 | -0.044084 | 9.6503e-05 | 2.4186e-05
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0073265 | -0.0018362 | 0.0073268 | 0.0018363 | 2.1198e-07 | 7.5992e-08 | 0.011024 | 0.011024 | 0.011024 | 0.9889 | -0.21365 | 0.98893 | -0.21304 | 3.0287
1 | -0.015911 | -0.0039878 | 0.015914 | 0.0039895 | 2.8808e-06 | 1.6717e-06 | 0.023941 | 0.023941 | 0.023941 | 0.98893 | -0.21304 | 0.98913 | -0.20924 | 6.5773
2 | 0.013464 | 0.0033757 | -0.01346 | -0.0033738 | 3.4348e-06 | 1.9118e-06 | 0.020255 | 0.020255 | 0.020255 | 0.98913 | -0.20924 | 0.98885 | -0.2146 | 5.5646
3 | -0.029378 | -0.0073652 | 0.029421 | 0.0073919 | 4.3e-05 | 2.6765e-05 | 0.044196 | 0.044196 | 0.044196 | 0.98913 | -0.20924 | 0.99071 | -0.17858 | 12.1419
4 | -0.047395 | -0.011897 | 0.047432 | 0.01192 | 3.6832e-05 | 2.3323e-05 | 0.071193 | 0.071193 | 0.071193 | 0.99071 | -0.17858 | 0.99155 | -0.1623 | 19.5584
5 | -0.047617 | -0.011966 | 0.047639 | 0.01198 | 2.2315e-05 | 1.4131e-05 | 0.07147 | 0.07147 | 0.07147 | 0.99155 | -0.1623 | 0.99206 | -0.15248 | 19.6346
6 | 0.010222 | 0.0025621 | -0.01022 | -0.0025614 | 1.4095e-06 | 6.9833e-07 | 0.015381 | 0.015382 | 0.015382 | 0.98885 | -0.2146 | 0.9887 | -0.21749 | 4.2257
7 | 0.0082492 | 0.0020674 | -0.0082484 | -0.0020671 | 7.3535e-07 | 3.0748e-07 | 0.012415 | 0.012415 | 0.012415 | 0.9887 | -0.21749 | 0.98861 | -0.21937 | 3.4108
8 | 0.0052862 | 0.0013247 | -0.0052861 | -0.0013247 | 1.4889e-07 | 1.4877e-08 | 0.0079566 | 0.0079566 | 0.0079566 | 0.98861 | -0.21937 | 0.98858 | -0.21996 | 2.1859
9 | 0.0026073 | 0.00065329 | -0.0026072 | -0.00065342 | 8.1808e-08 | -1.2924e-07 | 0.0039244 | 0.0039245 | 0.0039245 | 0.98858 | -0.21996 | 0.98854 | -0.22062 | 1.0782
10 | -0.053226 | -0.013424 | 0.053251 | 0.01344 | 2.5271e-05 | 1.6036e-05 | 0.079661 | 0.079661 | 0.079661 | 0.9946 | -0.10345 | 0.99512 | -0.09354 | 21.8849
11 | 0.048637 | 0.012274 | -0.048614 | -0.012259 | 2.3055e-05 | 1.4605e-05 | 0.072795 | 0.072795 | 0.072795 | 0.9946 | -0.10345 | 0.99409 | -0.11336 | 19.9987
12 | -0.076244 | -0.019202 | 0.076358 | 0.019275 | 0.00011382 | 7.2542e-05 | 0.11404 | 0.11404 | 0.11404 | 0.99512 | -0.09354 | 0.99674 | -0.062372 | 31.3302
13 | 0.048324 | 0.012186 | -0.048287 | -0.012163 | 3.6448e-05 | 2.3086e-05 | 0.072361 | 0.072361 | 0.072361 | 0.99409 | -0.11336 | 0.99327 | -0.12913 | 19.8793
14 | 0.25298 | 0.063812 | -0.25261 | -0.063576 | 0.00036982 | 0.00023587 | 0.37781 | 0.37781 | 0.37781 | 0.99674 | -0.062372 | 0.99515 | -0.092955 | 34.5978
15 | -0.32933 | -0.083087 | 0.33032 | 0.083717 | 0.00098674 | 0.00063024 | 0.49185 | 0.49185 | 0.49185 | 0.99674 | -0.062372 | 1 | 0 | 45.0412
16 | 0.048146 | 0.012128 | -0.048107 | -0.012103 | 3.9246e-05 | 2.4857e-05 | 0.072149 | 0.072149 | 0.072149 | 0.99327 | -0.12913 | 0.99238 | -0.14619 | 19.8213
17 | 0.2131 | 0.053637 | -0.2129 | -0.053513 | 0.00019468 | 0.000124 | 0.31872 | 0.31872 | 0.31872 | 0.99515 | -0.092955 | 0.99415 | -0.11209 | 29.1869
18 | 0.039507 | 0.0099389 | -0.039455 | -0.0099063 | 5.1885e-05 | 3.2692e-05 | 0.059087 | 0.059087 | 0.059087 | 0.99515 | -0.092955 | 0.99372 | -0.12048 | 16.2327
19 | 0.068631 | 0.017269 | -0.068566 | -0.017227 | 6.4896e-05 | 4.1316e-05 | 0.10215 | 0.10215 | 0.10215 | 1 | 0 | 0.99897 | -0.019809 | 28.0625
20 | 0.047923 | 0.012057 | -0.047908 | -0.012048 | 1.4414e-05 | 9.1289e-06 | 0.071874 | 0.071874 | 0.071874 | 0.99238 | -0.14619 | 0.99206 | -0.15248 | 19.7455
21 | 0.18748 | 0.047141 | -0.1871 | -0.046901 | 0.00037623 | 0.00024013 | 0.28067 | 0.28067 | 0.28067 | 0.99415 | -0.11209 | 0.99198 | -0.1542 | 38.5531
22 | 0.0087787 | 0.0022005 | -0.0087769 | -0.0021997 | 1.7475e-06 | 7.6911e-07 | 0.013145 | 0.013146 | 0.013146 | 0.99372 | -0.12048 | 0.9935 | -0.12466 | 3.6114
23 | 0.030676 | 0.0077058 | -0.03066 | -0.0076953 | 1.6848e-05 | 1.0507e-05 | 0.045942 | 0.045942 | 0.045942 | 0.99372 | -0.12048 | 0.99312 | -0.132 | 12.6213
24 | 0.038917 | 0.0097964 | -0.038884 | -0.0097758 | 3.2776e-05 | 2.0637e-05 | 0.057984 | 0.057984 | 0.057984 | 0.99897 | -0.019809 | 0.99805 | -0.037445 | 15.9296
25 | 0.062285 | 0.015618 | -0.062263 | -0.015604 | 2.1984e-05 | 1.3983e-05 | 0.093433 | 0.093433 | 0.093433 | 0.99198 | -0.1542 | 0.99159 | -0.16161 | 25.6684
26 | 0.024786 | 0.0062231 | -0.024776 | -0.006217 | 9.9853e-06 | 6.1409e-06 | 0.037141 | 0.037141 | 0.037141 | 0.99312 | -0.132 | 0.99269 | -0.14045 | 10.2035
27 | 0.03659 | 0.0092009 | -0.036579 | -0.0091937 | 1.1598e-05 | 7.2872e-06 | 0.054564 | 0.054564 | 0.054564 | 0.99805 | -0.037445 | 0.9977 | -0.044084 | 14.9901
28 | -0.016393 | -0.0041084 | 0.016393 | 0.0041089 | 7.9541e-07 | 4.6321e-07 | 0.024513 | 0.024513 | 0.024513 | 0.99507 | -0.094744 | 0.99513 | -0.093726 | 6.7344
29 | 0.0067859 | 0.0017007 | -0.0067849 | -0.0017004 | 9.9466e-07 | 3.0202e-07 | 0.010147 | 0.010148 | 0.010148 | 0.99507 | -0.094744 | 0.99492 | -0.097821 | 2.7878
30 | -0.023301 | -0.0058401 | 0.023315 | 0.0058487 | 1.4066e-05 | 8.6004e-06 | 0.034842 | 0.034842 | 0.034842 | 0.99513 | -0.093726 | 0.99578 | -0.081063 | 9.572
31 | -0.028166 | -0.0070646 | 0.028188 | 0.007078 | 2.1722e-05 | 1.3476e-05 | 0.042091 | 0.042091 | 0.042091 | 0.99578 | -0.081063 | 0.99662 | -0.064897 | 11.5636
32 | -0.032315 | -0.0081123 | 0.032329 | 0.0081214 | 1.4663e-05 | 9.1656e-06 | 0.048253 | 0.048253 | 0.048253 | 0.99662 | -0.064897 | 0.99712 | -0.055389 | 13.2562
33 | -0.034519 | -0.0086702 | 0.034526 | 0.0086747 | 7.1843e-06 | 4.5038e-06 | 0.05152 | 0.05152 | 0.05152 | 0.99712 | -0.055389 | 0.99734 | -0.051028 | 14.1538
34 | -0.03647 | -0.0091619 | 0.036482 | 0.0091695 | 1.2091e-05 | 7.5962e-06 | 0.05442 | 0.05442 | 0.05442 | 0.99734 | -0.051028 | 0.9977 | -0.044084 | 14.9506
35 | 0.016776 | 0.0042122 | -0.016766 | -0.0042063 | 1.01e-05 | 5.9137e-06 | 0.02515 | 0.02515 | 0.02515 | 0.99269 | -0.14045 | 0.99204 | -0.15307 | 6.9095
36 | 0.016766 | 0.0042063 | -0.016759 | -0.0042021 | 7.2395e-06 | 4.2394e-06 | 0.02515 | 0.025151 | 0.025151 | 0.99204 | -0.15307 | 0.99157 | -0.16213 | 6.9095
37 | 0.016759 | 0.0042021 | -0.016755 | -0.0041997 | 3.9698e-06 | 2.3248e-06 | 0.025151 | 0.025151 | 0.025151 | 0.99157 | -0.16213 | 0.99131 | -0.16711 | 6.9095
38 | 0.010326 | 0.0025883 | -0.010323 | -0.0025873 | 2.0286e-06 | 1.0081e-06 | 0.015499 | 0.015499 | 0.015499 | 0.99131 | -0.16711 | 0.9911 | -0.17123 | 4.2581
39 | 0.0038939 | 0.0009759 | -0.0038939 | -0.0009759 | 2.2283e-09 | -8.142e-10 | 0.0058462 | 0.0058462 | 0.0058462 | 0.9911 | -0.17123 | 0.9911 | -0.17124 | 1.6061

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4006 | 0.10099

## res_load
| p_mw | q_mvar
0 | 0.0073265 | 0.0018362
1 | 0.0085846 | 0.0021515
2 | 0.017974 | 0.0045047
3 | 0.00018492 | 4.6345e-05
4 | 0.0032388 | 0.00081172
5 | 0.001971 | 0.00049398
6 | 0.0029622 | 0.00074239
7 | 0.0026788 | 0.00067137
8 | 0.0045892 | 0.0011502
9 | 0.022992 | 0.0057624
10 | 0.00029032 | 7.276e-05
11 | 0.0001411 | 3.5363e-05
12 | 0.00018395 | 4.6103e-05
13 | 0.025425 | 0.0063721
14 | 0.029649 | 0.0074308
15 | 0.00026917 | 6.7461e-05
16 | 0.12482 | 0.031282
17 | 0.0087769 | 0.0021997
18 | 0.005874 | 0.0014722
19 | 0.0022936 | 0.00057484
20 | 0.0096067 | 0.0024077
21 | 0.0069077 | 0.0017312
22 | 0.0067849 | 0.0017004
23 | 0.0048513 | 0.0012159
24 | 0.0041267 | 0.0010342
25 | 0.0021894 | 0.00054872
26 | 0.001944 | 0.00048721
27 | 0.0079991 | 0.0020048
28 | 0.0064296 | 0.0016114
29 | 0.0064296 | 0.0016114
30 | 0.0038939 | 0.0009759
31 | 0.062263 | 0.015604
32 | 0.0026072 | 0.00065342
33 | 9.6503e-05 | 2.4186e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1