## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1510-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1510-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1510-1_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1510-1_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1510-1_0_3_node_25 | 0.4 | n |  | TRUE
5 | bus_LV_1510-1_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1510-1_0_3_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_1510-1_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1510-1_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1510-1_0_3_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_1510-1_0_3_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_1510-1_0_3_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_1510-1_0_3_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_1510-1_0_3_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_1510-1_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1510-1_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1510-1_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1510-1_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1510-1_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1510-1_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1510-1_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1510-1_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1510-1_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1510-1_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1510-1_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1510-1_0_3_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_1510-1_0_3_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_1510-1_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1510-1_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_1510-1_0_3_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_1510-1_0_3_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1510-1_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1510-1_0_3_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1510-1_0_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1510-1_0_3_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1510-1_0_3_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1510-1_0_3_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1510-1_0_3_node_37 | 0.4 | n |  | TRUE
38 | bus_MV_143_0_node_142 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1510-1_0_3_load_0 | 0 | 0.012688 | 0.0031799 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1510-1_0_3_load_25 | 4 | 0.00072371 | 0.00018138 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1510-1_0_3_load_5 | 5 | 0.0064233 | 0.0016098 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1510-1_0_3_load_24 | 6 | 0.00061657 | 0.00015453 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1510-1_0_3_load_6 | 7 | 0.0061574 | 0.0015432 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1510-1_0_3_load_7 | 8 | 0.0016791 | 0.00042082 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1510-1_0_3_load_34 | 9 | 0.018628 | 0.0046687 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1510-1_0_3_load_39 | 12 | 0.011569 | 0.0028995 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1510-1_0_3_load_40 | 13 | 0.013163 | 0.0032989 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1510-1_0_3_load_8 | 14 | 0.0021568 | 0.00054054 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1510-1_0_3_load_9 | 15 | 0.0006434 | 0.00016125 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1510-1_0_3_load_12 | 18 | 0.00067068 | 0.00016809 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1510-1_0_3_load_13 | 19 | 0.0012973 | 0.00032513 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1510-1_0_3_load_14 | 20 | 0.0013069 | 0.00032753 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1510-1_0_3_load_18 | 24 | 0.00051698 | 0.00012957 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1510-1_0_3_load_33 | 25 | 0.00068283 | 0.00017113 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1510-1_0_3_load_32 | 26 | 0.0012468 | 0.00031247 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1510-1_0_3_load_19 | 27 | 0.0013445 | 0.00033695 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1510-1_0_3_load_20 | 28 | 0.00014207 | 3.5606e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1510-1_0_3_load_23 | 29 | 0.00024683 | 6.1861e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1510-1_0_3_load_21 | 30 | 0.0004159 | 0.00010423 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1510-1_0_3_load_26 | 31 | 0.00027559 | 6.907e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1510-1_0_3_load_27 | 32 | 0.0011139 | 0.00027916 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1510-1_0_3_load_28 | 33 | 0.00047764 | 0.00011971 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1510-1_0_3_load_29 | 34 | 0.0013465 | 0.00033747 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1510-1_0_3_load_30 | 35 | 0.0041323 | 0.0010357 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1510-1_0_3_load_31 | 36 | 0.0011245 | 0.00028183 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1510-1_0_3_load_37 | 37 | 0.0014878 | 0.00037287 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1510-1_0_3_line_0 |  | 0 | 1 | 0.055062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1510-1_0_3_line_1 |  | 1 | 2 | 0.040971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1510-1_0_3_line_2 |  | 1 | 3 | 0.011128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1510-1_0_3_line_3 |  | 2 | 4 | 0.19974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1510-1_0_3_line_4 |  | 3 | 5 | 0.040231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1510-1_0_3_line_5 |  | 4 | 6 | 0.27802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1510-1_0_3_line_6 |  | 5 | 7 | 0.097976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1510-1_0_3_line_7 |  | 6 | 27 | 0.28848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1510-1_0_3_line_8 |  | 7 | 8 | 0.036422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1510-1_0_3_line_9 |  | 8 | 9 | 0.22316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1510-1_0_3_line_10 |  | 9 | 10 | 0.048847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1510-1_0_3_line_11 |  | 10 | 11 | 0.013454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1510-1_0_3_line_12 |  | 11 | 12 | 0.029701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1510-1_0_3_line_13 |  | 12 | 13 | 0.071397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1510-1_0_3_line_14 |  | 14 | 15 | 0.017483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1510-1_0_3_line_15 |  | 14 | 16 | 0.0077272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1510-1_0_3_line_16 |  | 15 | 17 | 0.018455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1510-1_0_3_line_17 |  | 16 | 18 | 0.024272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1510-1_0_3_line_18 |  | 17 | 19 | 0.018308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1510-1_0_3_line_19 |  | 17 | 20 | 0.020131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1510-1_0_3_line_20 |  | 19 | 21 | 0.039684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1510-1_0_3_line_21 |  | 20 | 22 | 0.031291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1510-1_0_3_line_22 |  | 21 | 23 | 0.12805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1510-1_0_3_line_23 |  | 22 | 24 | 0.036417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1510-1_0_3_line_24 |  | 23 | 25 | 0.027055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1510-1_0_3_line_25 |  | 25 | 26 | 0.082546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1510-1_0_3_line_26 |  | 26 | 37 | 0.24664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1510-1_0_3_line_27 |  | 27 | 28 | 0.0061353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1510-1_0_3_line_28 |  | 27 | 29 | 0.19091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1510-1_0_3_line_29 |  | 28 | 30 | 0.0095222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1510-1_0_3_line_30 |  | 30 | 31 | 6.281e-08 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1510-1_0_3_line_31 |  | 31 | 32 | 0.069495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1510-1_0_3_line_32 |  | 32 | 33 | 0.011658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1510-1_0_3_line_33 |  | 33 | 34 | 0.060734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1510-1_0_3_line_34 |  | 34 | 35 | 0.016915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1510-1_0_3_line_35 |  | 35 | 36 | 0.00018949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1510-1_0_3_line_36 |  | 36 | 37 | 0.20935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1510-1_0_3_trafo_7 | 0.63 MVA 20/0.4 kV | 38 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2671126.5681 | 1205272.0348 | 2671135.7453 | 1205272.3999 | 2671141.8185 | 1205274.7181 | 2671153.0223 | 1205281.2 | 2671162.3565 | 1205291.373 | 2671169.8807 | 1205295.7542 | 2671173.5134 | 1205297.2274
1 | 2671126.5681 | 1205272.0348 | 2671098.1972 | 1205242.401
2 | 2671126.5681 | 1205272.0348 | 2671130.4233 | 1205275.3494 | 2671135.1708 | 1205279.1194
3 | 2671098.1972 | 1205242.401 | 2670969.0044 | 1205090.0651
4 | 2671135.1708 | 1205279.1194 | 2671137.8687 | 1205286.9897 | 2671158.7128 | 1205311.1528
5 | 2670969.0044 | 1205090.0651 | 2670803.8692 | 1204866.4042
6 | 2671158.7128 | 1205311.1528 | 2671158.7128 | 1205311.1528 | 2671177.3312 | 1205320.3581 | 2671247.3988 | 1205352.783
7 | 2670803.8692 | 1204866.4042 | 2671029.4742 | 1204686.6163
8 | 2671280.1232 | 1205368.7693 | 2671251.56 | 1205354.7087 | 2671247.3988 | 1205352.783
9 | 2671280.1232 | 1205368.7693 | 2671450.5238 | 1205512.8673
10 | 2671492.8644 | 1205490.0088 | 2671480.4722 | 1205492.6288 | 2671466.1721 | 1205501.4853 | 2671450.8035 | 1205512.5527 | 2671450.5238 | 1205512.8673
11 | 2671492.8644 | 1205490.0088 | 2671498.5986 | 1205502.185
12 | 2671498.5986 | 1205502.185 | 2671507.8497 | 1205496.3477 | 2671520.1775 | 1205491.4923 | 2671525.1178 | 1205493.939
13 | 2671585.8936 | 1205507.8229 | 2671573.8762 | 1205519.1414 | 2671536.3896 | 1205499.5581 | 2671535.3843 | 1205499.0235 | 2671525.1178 | 1205493.939
14 | 2671734.4078 | 1204987.6622 | 2671734.2165 | 1204988.071 | 2671724.4585 | 1205002.0302
15 | 2671737.6832 | 1204980.6636 | 2671734.4078 | 1204987.6622
16 | 2671720.3068 | 1205018.1224 | 2671718.0701 | 1205011.1691 | 2671724.4585 | 1205002.0302
17 | 2671737.6832 | 1204980.6636 | 2671724.187 | 1204960.4669
18 | 2671720.3068 | 1205018.1224 | 2671707.4413 | 1205031.1474
19 | 2671720.3068 | 1205018.1224 | 2671729.8962 | 1205026.6317 | 2671734.7612 | 1205032.089
20 | 2671679.5536 | 1205059.3809 | 2671707.4413 | 1205031.1474
21 | 2671739.5316 | 1205061.0686 | 2671741.1707 | 1205051.916 | 2671741.7622 | 1205045.1078 | 2671739.5641 | 1205037.4767 | 2671734.7612 | 1205032.089
22 | 2671552.8137 | 1205038.7153 | 2671679.5536 | 1205059.3809
23 | 2671739.5316 | 1205061.0686 | 2671742.572 | 1205060.0156 | 2671748.6067 | 1205057.9313 | 2671773.2572 | 1205047.376
24 | 2671552.8137 | 1205038.7153 | 2671525.9234 | 1205035.734
25 | 2671444.3562 | 1205046.0057 | 2671502.9566 | 1205035.4607 | 2671520.3206 | 1205035.1128 | 2671525.9234 | 1205035.734
26 | 2671444.3562 | 1205046.0057 | 2671333.4315 | 1204825.7123
27 | 2671029.4742 | 1204686.6163 | 2671033.442 | 1204691.2959
28 | 2671029.4742 | 1204686.6163 | 2670873.7122 | 1204576.2241
29 | 2671039.6001 | 1204698.5589 | 2671033.442 | 1204691.2959
30 | 2671039.6001 | 1204698.5589 | 2671039.6001 | 1204698.5589
31 | 2671039.6001 | 1204698.5589 | 2671076.4049 | 1204741.9674 | 2671082.4011 | 1204753.0302
32 | 2671082.4011 | 1204753.0302 | 2671087.9566 | 1204763.2799
33 | 2671087.9566 | 1204763.2799 | 2671088.3898 | 1204764.0791 | 2671116.2225 | 1204817.0359
34 | 2671124.0918 | 1204832.0087 | 2671116.2225 | 1204817.0359
35 | 2671124.0918 | 1204832.0087 | 2671124.1799 | 1204832.1764
36 | 2671124.1799 | 1204832.1764 | 2671333.4315 | 1204825.7123

## bus_geodata
| x | y | coords
0 | 2671173.5134 | 1205297.2274
1 | 2671126.5681 | 1205272.0348
2 | 2671098.1972 | 1205242.401
3 | 2671135.1708 | 1205279.1194
4 | 2670969.0044 | 1205090.0651
5 | 2671158.7128 | 1205311.1528
6 | 2670803.8692 | 1204866.4042
7 | 2671247.3988 | 1205352.783
8 | 2671280.1232 | 1205368.7693
9 | 2671450.5238 | 1205512.8673
10 | 2671492.8644 | 1205490.0088
11 | 2671498.5986 | 1205502.185
12 | 2671525.1178 | 1205493.939
13 | 2671585.8936 | 1205507.8229
14 | 2671734.4078 | 1204987.6622
15 | 2671724.4585 | 1205002.0302
16 | 2671737.6832 | 1204980.6636
17 | 2671720.3068 | 1205018.1224
18 | 2671724.187 | 1204960.4669
19 | 2671707.4413 | 1205031.1474
20 | 2671734.7612 | 1205032.089
21 | 2671679.5536 | 1205059.3809
22 | 2671739.5316 | 1205061.0686
23 | 2671552.8137 | 1205038.7153
24 | 2671773.2572 | 1205047.376
25 | 2671525.9234 | 1205035.734
26 | 2671444.3562 | 1205046.0057
27 | 2671029.4742 | 1204686.6163
28 | 2671033.442 | 1204691.2959
29 | 2670873.7122 | 1204576.2241
30 | 2671039.6001 | 1204698.5589
31 | 2671039.6001 | 1204698.5589
32 | 2671082.4011 | 1204753.0302
33 | 2671087.9566 | 1204763.2799
34 | 2671116.2225 | 1204817.0359
35 | 2671124.0918 | 1204832.0087
36 | 2671124.1799 | 1204832.1764
37 | 2671333.4315 | 1204825.7123
38 | 2671292.7067 | 1205351.4199

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99507 | -0.093884 | 0.012688 | 0.0031799
1 | 0.99571 | -0.081594 | 0 | 0
2 | 0.99487 | -0.097479 | 0 | 0
3 | 0.99607 | -0.074803 | 0 | 0
4 | 0.99079 | -0.17529 | 0.00072371 | 0.00018138
5 | 0.99735 | -0.050291 | 0.0064233 | 0.0016098
6 | 0.9853 | -0.28102 | 0.00061657 | 0.00015453
7 | 0.99921 | -0.01503 | 0.0061574 | 0.0015432
8 | 1 | 0 | -0.093238 | -0.023304
9 | 0.99113 | -0.1702 | 0.018628 | 0.0046687
10 | 0.99002 | -0.19166 | 0 | 0
11 | 0.98972 | -0.19758 | 0 | 0
12 | 0.98904 | -0.21066 | 0.011569 | 0.0028995
13 | 0.98818 | -0.22742 | 0.013163 | 0.0032989
14 | 0.97107 | -0.55982 | 0.0021568 | 0.00054054
15 | 0.97112 | -0.55891 | 0.0006434 | 0.00016125
16 | 0.97106 | -0.55992 | 0 | 0
17 | 0.97118 | -0.55773 | 0 | 0
18 | 0.97105 | -0.56022 | 0.00067068 | 0.00016809
19 | 0.97127 | -0.55593 | 0.0012973 | 0.00032513
20 | 0.97114 | -0.5584 | 0.0013069 | 0.00032753
21 | 0.97151 | -0.5511 | 0 | 0
22 | 0.97113 | -0.5587 | 0 | 0
23 | 0.9723 | -0.5355 | 0 | 0
24 | 0.97111 | -0.55905 | 0.00051698 | 0.00012957
25 | 0.97246 | -0.53221 | 0.00068283 | 0.00017113
26 | 0.97302 | -0.52113 | 0.0012468 | 0.00031247
27 | 0.97976 | -0.3887 | 0.0013445 | 0.00033695
28 | 0.97965 | -0.39083 | 0.00014207 | 3.5606e-05
29 | 0.97972 | -0.38957 | 0.00024683 | 6.1861e-05
30 | 0.97948 | -0.3941 | 0.0004159 | 0.00010423
31 | 0.97948 | -0.3941 | 0.00027559 | 6.907e-05
32 | 0.97831 | -0.41716 | 0.0011139 | 0.00027916
33 | 0.97812 | -0.42079 | 0.00047764 | 0.00011971
34 | 0.97718 | -0.43922 | 0.0013465 | 0.00033747
35 | 0.97694 | -0.44395 | 0.0041323 | 0.0010357
36 | 0.97694 | -0.44399 | 0.0011245 | 0.00028183
37 | 0.97499 | -0.48243 | 0.0014878 | 0.00037287
38 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012688 | -0.0031799 | 0.012695 | 0.0031839 | 7.433e-06 | 4.0414e-06 | 0.018973 | 0.018973 | 0.018973 | 0.99507 | -0.093884 | 0.99571 | -0.081594 | 5.2125
1 | 0.02238 | 0.0057425 | -0.022363 | -0.005732 | 1.7235e-05 | 1.0498e-05 | 0.033492 | 0.033493 | 0.033493 | 0.99571 | -0.081594 | 0.99487 | -0.097479 | 9.2013
2 | -0.035075 | -0.0089264 | 0.035087 | 0.0089337 | 1.1487e-05 | 7.2067e-06 | 0.052465 | 0.052465 | 0.052465 | 0.99571 | -0.081594 | 0.99607 | -0.074803 | 14.4136
3 | 0.022363 | 0.005732 | -0.022278 | -0.0056808 | 8.4026e-05 | 5.1194e-05 | 0.033493 | 0.033494 | 0.033494 | 0.99487 | -0.097479 | 0.99079 | -0.17529 | 9.2015
4 | -0.035087 | -0.0089337 | 0.035128 | 0.0089597 | 4.1528e-05 | 2.6053e-05 | 0.052465 | 0.052465 | 0.052465 | 0.99607 | -0.074803 | 0.99735 | -0.050291 | 14.4136
5 | 0.021555 | 0.0054994 | -0.021445 | -0.0054329 | 0.00010949 | 6.6516e-05 | 0.032407 | 0.032408 | 0.032408 | 0.99079 | -0.17529 | 0.9853 | -0.28102 | 8.9033
6 | -0.041551 | -0.01057 | 0.041622 | 0.010612 | 7.0726e-05 | 4.2703e-05 | 0.062048 | 0.062048 | 0.062048 | 0.99735 | -0.050291 | 0.99921 | -0.01503 | 8.5231
7 | 0.020829 | 0.0052784 | -0.020722 | -0.0052134 | 0.00010719 | 6.4947e-05 | 0.031477 | 0.031478 | 0.031478 | 0.9853 | -0.28102 | 0.97976 | -0.3887 | 8.6478
8 | -0.04778 | -0.012155 | 0.047814 | 0.012177 | 3.4636e-05 | 2.1212e-05 | 0.071217 | 0.071217 | 0.071217 | 0.99921 | -0.01503 | 1 | 0 | 9.7826
9 | 0.043774 | 0.011127 | -0.043419 | -0.010902 | 0.00035567 | 0.00022472 | 0.065192 | 0.065193 | 0.065193 | 1 | 0 | 0.99113 | -0.1702 | 17.9101
10 | 0.02479 | 0.0062336 | -0.024765 | -0.006218 | 2.5383e-05 | 1.5616e-05 | 0.037225 | 0.037226 | 0.037226 | 0.99113 | -0.1702 | 0.99002 | -0.19166 | 10.2268
11 | 0.024765 | 0.006218 | -0.024758 | -0.0062137 | 6.9915e-06 | 4.3016e-06 | 0.037226 | 0.037226 | 0.037226 | 0.99002 | -0.19166 | 0.98972 | -0.19758 | 10.2268
12 | 0.024758 | 0.0062137 | -0.024742 | -0.0062042 | 1.5435e-05 | 9.4967e-06 | 0.037226 | 0.037226 | 0.037226 | 0.98972 | -0.19758 | 0.98904 | -0.21066 | 10.2269
13 | 0.013173 | 0.0033047 | -0.013163 | -0.0032989 | 1.0518e-05 | 5.8161e-06 | 0.01982 | 0.019821 | 0.019821 | 0.98904 | -0.21066 | 0.98818 | -0.22742 | 5.4452
14 | -0.0028275 | -0.00070824 | 0.0028276 | 0.0007081 | 1.2306e-07 | -1.3754e-07 | 0.0043325 | 0.0043325 | 0.0043325 | 0.97107 | -0.55982 | 0.97112 | -0.55891 | 1.1903
15 | 0.00067069 | 0.0001677 | -0.00067069 | -0.00016779 | 3.0599e-09 | -9.3635e-08 | 0.0010276 | 0.0010276 | 0.0010276 | 0.97107 | -0.55982 | 0.97106 | -0.55992 | 0.28231
16 | -0.003471 | -0.00086936 | 0.0034712 | 0.00086925 | 1.9574e-07 | -1.0307e-07 | 0.0053183 | 0.0053182 | 0.0053183 | 0.97112 | -0.55891 | 0.97118 | -0.55773 | 1.4611
17 | 0.00067069 | 0.00016779 | -0.00067068 | -0.00016809 | 9.6128e-09 | -2.9411e-07 | 0.0010276 | 0.0010277 | 0.0010277 | 0.97106 | -0.55992 | 0.97105 | -0.56022 | 0.28234
18 | -0.0052951 | -0.0013253 | 0.0052956 | 0.0013254 | 4.5182e-07 | 6.2605e-08 | 0.0081124 | 0.0081124 | 0.0081124 | 0.97118 | -0.55773 | 0.97127 | -0.55593 | 2.2287
19 | 0.0018239 | 0.00045606 | -0.0018239 | -0.00045627 | 5.8943e-08 | -2.1137e-07 | 0.0027942 | 0.0027943 | 0.0027943 | 0.97118 | -0.55773 | 0.97114 | -0.5584 | 0.76766
20 | -0.0065928 | -0.0016505 | 0.0065944 | 0.001651 | 1.518e-06 | 4.8025e-07 | 0.0101 | 0.0101 | 0.0101 | 0.97127 | -0.55593 | 0.97151 | -0.5511 | 2.7747
21 | 0.00051699 | 0.00012874 | -0.00051698 | -0.00012912 | 7.359e-09 | -3.8245e-07 | 0.00079185 | 0.00079199 | 0.00079199 | 0.97114 | -0.5584 | 0.97113 | -0.5587 | 0.21758
22 | -0.0065944 | -0.001651 | 0.0065993 | 0.0016525 | 4.8977e-06 | 1.5477e-06 | 0.0101 | 0.010099 | 0.0101 | 0.97151 | -0.5511 | 0.9723 | -0.5355 | 2.7746
23 | 0.00051698 | 0.00012912 | -0.00051698 | -0.00012957 | 8.5679e-09 | -4.4509e-07 | 0.00079199 | 0.00079216 | 0.00079216 | 0.97113 | -0.5587 | 0.97111 | -0.55905 | 0.21763
24 | -0.0065993 | -0.0016525 | 0.0066003 | 0.0016529 | 1.0348e-06 | 3.2664e-07 | 0.010099 | 0.010099 | 0.010099 | 0.9723 | -0.5355 | 0.97246 | -0.53221 | 2.7745
25 | -0.0072831 | -0.001824 | 0.007287 | 0.0018254 | 3.844e-06 | 1.4354e-06 | 0.011144 | 0.011143 | 0.011144 | 0.97246 | -0.53221 | 0.97302 | -0.52113 | 3.0615
26 | -0.0085337 | -0.0021379 | 0.0085495 | 0.0021449 | 1.575e-05 | 7.0105e-06 | 0.01305 | 0.013049 | 0.01305 | 0.97302 | -0.52113 | 0.97499 | -0.48243 | 3.5852
27 | 0.01913 | 0.004817 | -0.019128 | -0.0048159 | 1.9432e-06 | 1.1664e-06 | 0.029062 | 0.029062 | 0.029062 | 0.97976 | -0.3887 | 0.97965 | -0.39083 | 7.9841
28 | 0.00024684 | 5.9464e-05 | -0.00024683 | -6.1861e-05 | 1.0039e-08 | -2.3978e-06 | 0.00037404 | 0.00037489 | 0.00037489 | 0.97976 | -0.3887 | 0.97972 | -0.38957 | 0.10299
29 | 0.018986 | 0.0047803 | -0.018983 | -0.0047785 | 2.9714e-06 | 1.7818e-06 | 0.028846 | 0.028847 | 0.028847 | 0.97965 | -0.39083 | 0.97948 | -0.3941 | 7.9249
30 | 0.018567 | 0.0046742 | -0.018567 | -0.0046742 | 1.875e-11 | 1.2e-11 | 0.028215 | 0.028215 | 0.028215 | 0.97948 | -0.3941 | 0.97948 | -0.3941 | 7.7513
31 | 0.018292 | 0.0046052 | -0.018272 | -0.0045932 | 2.0135e-05 | 1.2013e-05 | 0.027796 | 0.027796 | 0.027796 | 0.97948 | -0.3941 | 0.97831 | -0.41716 | 7.6364
32 | 0.017158 | 0.004314 | -0.017155 | -0.0043122 | 2.9787e-06 | 1.76e-06 | 0.026102 | 0.026102 | 0.026102 | 0.97831 | -0.41716 | 0.97812 | -0.42079 | 7.1709
33 | 0.016677 | 0.0041925 | -0.016662 | -0.0041839 | 1.4666e-05 | 8.6245e-06 | 0.025376 | 0.025376 | 0.025376 | 0.97812 | -0.42079 | 0.97718 | -0.43922 | 6.9714
34 | 0.015316 | 0.0038464 | -0.015313 | -0.0038444 | 3.4511e-06 | 1.9969e-06 | 0.023325 | 0.023325 | 0.023325 | 0.97718 | -0.43922 | 0.97694 | -0.44395 | 6.4081
35 | 0.01118 | 0.0028088 | -0.01118 | -0.0028088 | 2.0611e-08 | 1.0819e-08 | 0.017031 | 0.017031 | 0.017031 | 0.97694 | -0.44395 | 0.97694 | -0.44399 | 4.6789
36 | 0.010056 | 0.0025269 | -0.010037 | -0.0025178 | 1.8424e-05 | 9.175e-06 | 0.015319 | 0.01532 | 0.01532 | 0.97694 | -0.44399 | 0.97499 | -0.48243 | 4.2087

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.094917 | 0.023725

## res_load
| p_mw | q_mvar
0 | 0.012688 | 0.0031799
1 | 0.00072371 | 0.00018138
2 | 0.0064233 | 0.0016098
3 | 0.00061657 | 0.00015453
4 | 0.0061574 | 0.0015432
5 | 0.0016791 | 0.00042082
6 | 0.018628 | 0.0046687
7 | 0.011569 | 0.0028995
8 | 0.013163 | 0.0032989
9 | 0.0021568 | 0.00054054
10 | 0.0006434 | 0.00016125
11 | 0.00067068 | 0.00016809
12 | 0.0012973 | 0.00032513
13 | 0.0013069 | 0.00032753
14 | 0.00051698 | 0.00012957
15 | 0.00068283 | 0.00017113
16 | 0.0012468 | 0.00031247
17 | 0.0013445 | 0.00033695
18 | 0.00014207 | 3.5606e-05
19 | 0.00024683 | 6.1861e-05
20 | 0.0004159 | 0.00010423
21 | 0.00027559 | 6.907e-05
22 | 0.0011139 | 0.00027916
23 | 0.00047764 | 0.00011971
24 | 0.0013465 | 0.00033747
25 | 0.0041323 | 0.0010357
26 | 0.0011245 | 0.00028183
27 | 0.0014878 | 0.00037287

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1