## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-100_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-100_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-100_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-100_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-100_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-100_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_1630-100_0_4_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1630-100_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1630-100_0_4_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_1630-100_0_4_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_1630-100_0_4_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_1630-100_0_4_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1630-100_0_4_node_37 | 0.4 | n |  | TRUE
13 | bus_LV_1630-100_0_4_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_1630-100_0_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_1630-100_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_1630-100_0_4_node_41 | 0.4 | n |  | TRUE
17 | bus_LV_1630-100_0_4_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1630-100_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1630-100_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1630-100_0_4_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1630-100_0_4_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_1630-100_0_4_node_7 | 0.4 | n |  | TRUE
23 | bus_LV_1630-100_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1630-100_0_4_node_6 | 0.4 | n |  | TRUE
25 | bus_LV_1630-100_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1630-100_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1630-100_0_4_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_1630-100_0_4_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1630-100_0_4_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_1630-100_0_4_node_8 | 0.4 | n |  | TRUE
31 | bus_LV_1630-100_0_4_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1630-100_0_4_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_1630-100_0_4_node_43 | 0.4 | n |  | TRUE
34 | bus_LV_1630-100_0_4_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_1630-100_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_1630-100_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1630-100_0_4_node_44 | 0.4 | n |  | TRUE
38 | bus_LV_1630-100_0_4_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_1630-100_0_4_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_1630-100_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_1630-100_0_4_node_39 | 0.4 | n |  | TRUE
42 | bus_LV_1630-100_0_4_node_32 | 0.4 | n |  | TRUE
43 | bus_MV_54_0_node_30 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-100_0_4_load_0 | 0 | 0.078924 | 0.01978 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-100_0_4_load_17 | 6 | 0.0062811 | 0.0015742 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-100_0_4_load_30 | 9 | 0.011156 | 0.002796 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-100_0_4_load_35 | 10 | 0.0056179 | 0.001408 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-100_0_4_load_37 | 12 | 0.0055801 | 0.0013985 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-100_0_4_load_27 | 13 | 0.011221 | 0.0028122 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-100_0_4_load_26 | 15 | 0.0091069 | 0.0022824 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-100_0_4_load_41 | 16 | 0.0066653 | 0.0016705 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-100_0_4_load_20 | 20 | 0.0036612 | 0.00091758 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-100_0_4_load_40 | 21 | 0.015583 | 0.0039054 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-100_0_4_load_6 | 24 | 0.0051168 | 0.0012824 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-100_0_4_load_18 | 25 | 0.034806 | 0.0087232 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-100_0_4_load_22 | 26 | 0.012444 | 0.0031188 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-100_0_4_load_34 | 27 | 0.013093 | 0.0032814 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-100_0_4_load_31 | 28 | 0.037951 | 0.0095114 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-100_0_4_load_36 | 29 | 0.0053815 | 0.0013487 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-100_0_4_load_16 | 31 | 0.007737 | 0.0019391 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-100_0_4_load_42 | 32 | 0.029038 | 0.0072777 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-100_0_4_load_38 | 34 | 0.0057779 | 0.0014481 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-100_0_4_load_28 | 35 | 0.0078327 | 0.0019631 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-100_0_4_load_44 | 37 | 0.03098 | 0.0077643 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-100_0_4_load_19 | 38 | 0.0054418 | 0.0013639 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-100_0_4_load_23 | 39 | 0.032448 | 0.0081321 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-100_0_4_load_29 | 40 | 0.0095228 | 0.0023866 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-100_0_4_load_39 | 41 | 0.0081012 | 0.0020304 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-100_0_4_load_32 | 42 | 0.0074966 | 0.0018788 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-100_0_4_line_0 |  | 0 | 1 | 0.027155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-100_0_4_line_1 |  | 1 | 2 | 0.026517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_1630-100_0_4_line_2 |  | 1 | 3 | 0.046194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_1630-100_0_4_line_3 |  | 1 | 4 | 0.058398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-100_0_4_line_4 |  | 2 | 5 | 0.10635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1630-100_0_4_line_5 |  | 2 | 6 | 0.011441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-100_0_4_line_6 |  | 3 | 7 | 0.068159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1630-100_0_4_line_7 |  | 3 | 8 | 0.001736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1630-100_0_4_line_8 |  | 3 | 9 | 0.013772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-100_0_4_line_9 |  | 4 | 10 | 0.010194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-100_0_4_line_10 |  | 5 | 13 | 0.014342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-100_0_4_line_11 |  | 5 | 14 | 0.12683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-100_0_4_line_12 |  | 5 | 15 | 0.013161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-100_0_4_line_13 |  | 6 | 25 | 0.0059879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-100_0_4_line_14 |  | 7 | 11 | 0.012918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1630-100_0_4_line_15 |  | 7 | 12 | 0.0098151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-100_0_4_line_16 |  | 8 | 26 | 0.017899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-100_0_4_line_17 |  | 8 | 18 | 0.026287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1630-100_0_4_line_18 |  | 11 | 27 | 0.01586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-100_0_4_line_19 |  | 11 | 28 | 0.0099257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1630-100_0_4_line_20 |  | 12 | 29 | 0.017259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-100_0_4_line_21 |  | 13 | 34 | 0.026251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-100_0_4_line_22 |  | 14 | 16 | 0.013242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-100_0_4_line_23 |  | 14 | 17 | 0.027755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-100_0_4_line_24 |  | 17 | 35 | 0.0087421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-100_0_4_line_25 |  | 17 | 36 | 0.021965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-100_0_4_line_26 |  | 18 | 19 | 0.077526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-100_0_4_line_27 |  | 18 | 20 | 0.016713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-100_0_4_line_28 |  | 19 | 21 | 0.004202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-100_0_4_line_29 |  | 19 | 22 | 0.066062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-100_0_4_line_30 |  | 22 | 23 | 0.0664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-100_0_4_line_31 |  | 22 | 24 | 0.026616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-100_0_4_line_32 |  | 23 | 32 | 0.016388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-100_0_4_line_33 |  | 23 | 33 | 0.1291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-100_0_4_line_34 |  | 24 | 30 | 0.0079761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1630-100_0_4_line_35 |  | 25 | 38 | 0.015586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-100_0_4_line_36 |  | 28 | 42 | 0.0073663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-100_0_4_line_37 |  | 30 | 31 | 0.009363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-100_0_4_line_38 |  | 33 | 37 | 0.035136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-100_0_4_line_39 |  | 34 | 41 | 0.0079128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-100_0_4_line_40 |  | 35 | 40 | 0.0070001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-100_0_4_line_41 |  | 36 | 39 | 0.010156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-100_0_4_trafo_31 | 0.63 MVA 20/0.4 kV | 43 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2722960.9725 | 1219372.7877 | 2722959.4921 | 1219346.7034 | 2722959.3994 | 1219345.6785
1 | 2722960.9725 | 1219372.7877 | 2722953.5004 | 1219374.3792 | 2722934.5997 | 1219375.7903
2 | 2722960.9725 | 1219372.7877 | 2722964.0606 | 1219372.1287 | 2722994.4516 | 1219370.8439 | 2723007.0572 | 1219370.2704
3 | 2722960.9725 | 1219372.7877 | 2722964.0606 | 1219372.1287 | 2722969.0492 | 1219408.082 | 2722972.2111 | 1219419.2783 | 2722974.4969 | 1219426.2198
4 | 2722902.5041 | 1219347.1279 | 2722881.1929 | 1219349.8348 | 2722880.8627 | 1219373.9246 | 2722881.5692 | 1219376.4745 | 2722882.7484 | 1219378.923 | 2722884.3799 | 1219381.1584 | 2722887.3034 | 1219383.6873 | 2722891.2289 | 1219380.6993 | 2722895.1569 | 1219379.068 | 2722899.5353 | 1219378.4133 | 2722934.5997 | 1219375.7903
5 | 2722934.5997 | 1219375.7903 | 2722933.8369 | 1219364.3747
6 | 2723007.0572 | 1219370.2704 | 2722994.4516 | 1219370.8439 | 2722993.5222 | 1219360.7168 | 2722993.7389 | 1219355.7396 | 2722994.5458 | 1219351.2194 | 2722996.0143 | 1219346.6462 | 2722998.2195 | 1219342.0548 | 2723008.4483 | 1219324.252 | 2723010.9228 | 1219319.4883
7 | 2723007.0572 | 1219370.2704 | 2723008.7971 | 1219370.1952
8 | 2723007.0572 | 1219370.2704 | 2723007.9381 | 1219384.0142
9 | 2722974.4969 | 1219426.2198 | 2722976.1969 | 1219431.3812 | 2722976.8407 | 1219436.0972
10 | 2722902.5041 | 1219347.1279 | 2722900.8604 | 1219335.1846 | 2722903.126 | 1219334.879
11 | 2722902.5041 | 1219347.1279 | 2722881.1929 | 1219349.8348 | 2722880.8636 | 1219343.3563 | 2722879.8512 | 1219323.6311 | 2722878.7514 | 1219302.2584 | 2722878.2312 | 1219292.1509 | 2722892.6231 | 1219287.0548 | 2722915.3353 | 1219279.006 | 2722923.2815 | 1219276.8905
12 | 2722902.5041 | 1219347.1279 | 2722915.5604 | 1219345.4717
13 | 2722933.4377 | 1219358.4001 | 2722933.8369 | 1219364.3747
14 | 2722998.9471 | 1219314.5594 | 2723010.9228 | 1219319.4883
15 | 2723010.9228 | 1219319.4883 | 2723012.3971 | 1219315.371 | 2723013.6072 | 1219312.2825 | 2723014.6775 | 1219310.447
16 | 2723008.7971 | 1219370.1952 | 2723006.9859 | 1219359.7607 | 2723009.3059 | 1219352.8299
17 | 2723008.7971 | 1219370.1952 | 2723030.3078 | 1219369.2164 | 2723035.0567 | 1219369.0032
18 | 2722998.9471 | 1219314.5594 | 2722997.9609 | 1219318.1974 | 2722991.935 | 1219328.6793
19 | 2722998.9471 | 1219314.5594 | 2722989.7708 | 1219310.7758
20 | 2723023.3716 | 1219295.5373 | 2723014.6775 | 1219310.447
21 | 2722903.126 | 1219334.879 | 2722919.3737 | 1219332.6868 | 2722917.9709 | 1219322.9309
22 | 2722923.2815 | 1219276.8905 | 2722924.7599 | 1219281.0242 | 2722925.4887 | 1219289.8461
23 | 2722923.2815 | 1219276.8905 | 2722925.9073 | 1219276.1885 | 2722929.4293 | 1219275.4718 | 2722948.3933 | 1219274.3177 | 2722950.816 | 1219274.6347
24 | 2722950.816 | 1219274.6347 | 2722959.4658 | 1219273.3677
25 | 2722951.9825 | 1219296.0755 | 2722951.9679 | 1219293.4732 | 2722952.3118 | 1219278.2906 | 2722952.1372 | 1219276.0853 | 2722950.816 | 1219274.6347
26 | 2723052.442 | 1219328.5305 | 2723071.3724 | 1219336.7057 | 2723058.6393 | 1219365.4763 | 2723057.3812 | 1219368.3193 | 2723035.0567 | 1219369.0032
27 | 2723035.0567 | 1219369.0032 | 2723040.9624 | 1219353.3686
28 | 2723052.442 | 1219328.5305 | 2723048.5746 | 1219326.8605
29 | 2723052.442 | 1219328.5305 | 2723071.3724 | 1219336.7057 | 2723078.9852 | 1219319.5051 | 2723087.3543 | 1219300.6076 | 2723089.7672 | 1219295.1532
30 | 2723089.7672 | 1219295.1532 | 2723090.2289 | 1219294.1175 | 2723095.3971 | 1219282.4374 | 2723100.183 | 1219271.6278 | 2723108.0268 | 1219253.9093 | 2723112.9638 | 1219242.7693 | 2723116.6508 | 1219234.439
31 | 2723089.7672 | 1219295.1532 | 2723073.0476 | 1219290.1928 | 2723072.1301 | 1219288.3057 | 2723072.139 | 1219285.6705 | 2723072.6561 | 1219283.0569 | 2723073.4554 | 1219281.4833 | 2723073.4645 | 1219281.4734
32 | 2723116.6508 | 1219234.439 | 2723101.4211 | 1219228.275
33 | 2723091.2508 | 1219147.7685 | 2723085.5351 | 1219151.7758 | 2723080.1267 | 1219161.8497 | 2723079.2323 | 1219164.7224 | 2723079.4174 | 1219167.5173 | 2723080.6113 | 1219169.2544 | 2723092.8747 | 1219174.6009 | 2723089.2674 | 1219182.7438 | 2723116.932 | 1219196.2482 | 2723130.6035 | 1219202.8804 | 2723124.463 | 1219216.7866 | 2723123.125 | 1219219.8169 | 2723116.6508 | 1219234.439
34 | 2723079.5931 | 1219276.5173 | 2723076.313 | 1219278.3844 | 2723073.4645 | 1219281.4734
35 | 2722933.4377 | 1219358.4001 | 2722932.8832 | 1219350.1014 | 2722931.8214 | 1219342.9109
36 | 2722989.7708 | 1219310.7758 | 2722982.9606 | 1219307.9679
37 | 2723081.8684 | 1219267.435 | 2723079.5931 | 1219276.5173
38 | 2723111.5594 | 1219168.6156 | 2723114.4399 | 1219162.2145 | 2723094.6894 | 1219153.2883 | 2723091.2508 | 1219147.7685
39 | 2722916.8447 | 1219315.0987 | 2722917.9709 | 1219322.9309
40 | 2722959.9289 | 1219266.3829 | 2722959.4658 | 1219273.3677
41 | 2722951.9825 | 1219296.0755 | 2722941.9164 | 1219297.423

## bus_geodata
| x | y | coords
0 | 2722959.3994 | 1219345.6785
1 | 2722960.9725 | 1219372.7877
2 | 2722934.5997 | 1219375.7903
3 | 2723007.0572 | 1219370.2704
4 | 2722974.4969 | 1219426.2198
5 | 2722902.5041 | 1219347.1279
6 | 2722933.8369 | 1219364.3747
7 | 2723010.9228 | 1219319.4883
8 | 2723008.7971 | 1219370.1952
9 | 2723007.9381 | 1219384.0142
10 | 2722976.8407 | 1219436.0972
11 | 2722998.9471 | 1219314.5594
12 | 2723014.6775 | 1219310.447
13 | 2722903.126 | 1219334.879
14 | 2722923.2815 | 1219276.8905
15 | 2722915.5604 | 1219345.4717
16 | 2722925.4887 | 1219289.8461
17 | 2722950.816 | 1219274.6347
18 | 2723035.0567 | 1219369.0032
19 | 2723052.442 | 1219328.5305
20 | 2723040.9624 | 1219353.3686
21 | 2723048.5746 | 1219326.8605
22 | 2723089.7672 | 1219295.1532
23 | 2723116.6508 | 1219234.439
24 | 2723073.4645 | 1219281.4734
25 | 2722933.4377 | 1219358.4001
26 | 2723009.306 | 1219352.8299
27 | 2722991.935 | 1219328.6793
28 | 2722989.7708 | 1219310.7758
29 | 2723023.3716 | 1219295.5373
30 | 2723079.5931 | 1219276.5173
31 | 2723081.8684 | 1219267.435
32 | 2723101.4211 | 1219228.275
33 | 2723091.2508 | 1219147.7685
34 | 2722917.9709 | 1219322.9309
35 | 2722959.4658 | 1219273.3677
36 | 2722951.9825 | 1219296.0755
37 | 2723111.5594 | 1219168.6156
38 | 2722931.8214 | 1219342.9109
39 | 2722941.9164 | 1219297.423
40 | 2722959.9289 | 1219266.3829
41 | 2722916.8447 | 1219315.0987
42 | 2722982.9606 | 1219307.9679
43 | 2722989.7708 | 1219310.7758

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98528 | -0.28168 | 0.078924 | 0.01978
1 | 0.98725 | -0.24328 | 0 | 0
2 | 0.98613 | -0.26499 | 0 | 0
3 | 0.99041 | -0.1824 | 0 | 0
4 | 0.98695 | -0.24915 | 0 | 0
5 | 0.98165 | -0.35181 | 0 | 0
6 | 0.98564 | -0.27454 | 0.0062811 | 0.0015742
7 | 0.9975 | -0.047122 | 0 | 0
8 | 0.99035 | -0.18348 | 0 | 0
9 | 0.99027 | -0.18514 | 0.011156 | 0.002796
10 | 0.9869 | -0.25017 | 0.0056179 | 0.001408
11 | 0.99889 | -0.020874 | 0 | 0
12 | 0.99741 | -0.049007 | 0.0055801 | 0.0013985
13 | 0.98131 | -0.35833 | 0.011221 | 0.0028122
14 | 0.97497 | -0.48225 | 0 | 0
15 | 0.98153 | -0.35398 | 0.0091069 | 0.0022824
16 | 0.97489 | -0.48387 | 0.0066653 | 0.0016705
17 | 0.97368 | -0.50763 | 0 | 0
18 | 0.9896 | -0.19784 | 0 | 0
19 | 0.98321 | -0.3207 | 0 | 0
20 | 0.98954 | -0.19893 | 0.0036612 | 0.00091758
21 | 0.98315 | -0.32188 | 0.015583 | 0.0039054
22 | 0.97873 | -0.4079 | 0 | 0
23 | 0.97501 | -0.4807 | 0 | 0
24 | 0.97841 | -0.41413 | 0.0051168 | 0.0012824
25 | 0.98541 | -0.27886 | 0.034806 | 0.0087232
26 | 0.99015 | -0.18744 | 0.012444 | 0.0031188
27 | 0.9987 | -0.024502 | 0.013093 | 0.0032814
28 | 1 | 0 | -0.37682 | -0.096401
29 | 0.99732 | -0.050634 | 0.0053815 | 0.0013487
30 | 0.97835 | -0.41525 | 0 | 0
31 | 0.97829 | -0.41657 | 0.007737 | 0.0019391
32 | 0.97457 | -0.48943 | 0.029038 | 0.0072777
33 | 0.97127 | -0.55432 | 0 | 0
34 | 0.98098 | -0.36493 | 0.0057779 | 0.0014481
35 | 0.97354 | -0.51042 | 0.0078327 | 0.0019631
36 | 0.97302 | -0.52074 | 0 | 0
37 | 0.97025 | -0.57445 | 0.03098 | 0.0077643
38 | 0.98534 | -0.28038 | 0.0054418 | 0.0013639
39 | 0.97271 | -0.52681 | 0.032448 | 0.0081321
40 | 0.97348 | -0.51165 | 0.0095228 | 0.0023866
41 | 0.98092 | -0.36609 | 0.0081012 | 0.0020304
42 | 0.99995 | -0.00096256 | 0.0074966 | 0.0018788
43 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.078924 | -0.01978 | 0.079069 | 0.019872 | 0.00014468 | 9.2248e-05 | 0.1192 | 0.11919 | 0.1192 | 0.98528 | -0.28168 | 0.98725 | -0.24328 | 32.7459
1 | 0.13822 | 0.035029 | -0.13808 | -0.034938 | 0.00014405 | 9.1177e-05 | 0.20847 | 0.20847 | 0.20847 | 0.98725 | -0.24328 | 0.98613 | -0.26499 | 19.0906
2 | -0.22291 | -0.05631 | 0.22356 | 0.056726 | 0.00065241 | 0.00041577 | 0.33613 | 0.33613 | 0.33613 | 0.98725 | -0.24328 | 0.99041 | -0.1824 | 30.7815
3 | 0.0056197 | 0.0014083 | -0.0056182 | -0.001408 | 1.5712e-06 | 2.5906e-07 | 0.0084702 | 0.0084705 | 0.0084705 | 0.98725 | -0.24328 | 0.98695 | -0.24915 | 2.327
4 | 0.091517 | 0.023258 | -0.091137 | -0.023017 | 0.0003809 | 0.00024108 | 0.13821 | 0.13821 | 0.13821 | 0.98613 | -0.26499 | 0.98165 | -0.35181 | 18.9851
5 | 0.046559 | 0.01168 | -0.046538 | -0.011667 | 2.1179e-05 | 1.3409e-05 | 0.070259 | 0.070259 | 0.070259 | 0.98613 | -0.26499 | 0.98564 | -0.27454 | 19.3019
6 | -0.34056 | -0.086538 | 0.34279 | 0.087965 | 0.0022342 | 0.0014272 | 0.51208 | 0.51208 | 0.51208 | 0.99041 | -0.1824 | 0.9975 | -0.047122 | 46.8942
7 | 0.10584 | 0.027015 | -0.10583 | -0.027012 | 5.4989e-06 | 3.4523e-06 | 0.15919 | 0.15919 | 0.15919 | 0.99041 | -0.1824 | 0.99035 | -0.18348 | 14.5776
8 | 0.011158 | 0.0027968 | -0.011156 | -0.002796 | 1.4514e-06 | 7.5168e-07 | 0.016764 | 0.016764 | 0.016764 | 0.99041 | -0.1824 | 0.99027 | -0.18514 | 4.6055
9 | 0.0056182 | 0.001408 | -0.0056179 | -0.001408 | 2.7428e-07 | 4.5275e-08 | 0.0084705 | 0.0084705 | 0.0084705 | 0.98695 | -0.24915 | 0.9869 | -0.25017 | 2.3271
10 | 0.025112 | 0.0062981 | -0.025105 | -0.0062933 | 7.794e-06 | 4.8069e-06 | 0.038068 | 0.038068 | 0.038068 | 0.98165 | -0.35181 | 0.98131 | -0.35833 | 10.4583
11 | 0.056916 | 0.014436 | -0.056562 | -0.014211 | 0.00035453 | 0.00022531 | 0.086338 | 0.086338 | 0.086338 | 0.98165 | -0.35181 | 0.97497 | -0.48225 | 23.7193
12 | 0.0091078 | 0.0022828 | -0.0091069 | -0.0022824 | 9.4073e-07 | 4.357e-07 | 0.013806 | 0.013806 | 0.013806 | 0.98165 | -0.35181 | 0.98153 | -0.35398 | 3.7929
13 | 0.040256 | 0.010092 | -0.040248 | -0.010087 | 8.2942e-06 | 5.232e-06 | 0.060776 | 0.060776 | 0.060776 | 0.98564 | -0.27454 | 0.98541 | -0.27886 | 16.6968
14 | -0.35375 | -0.090713 | 0.3542 | 0.091001 | 0.00045091 | 0.00028808 | 0.52844 | 0.52844 | 0.52844 | 0.9975 | -0.047122 | 0.99889 | -0.020874 | 48.3917
15 | 0.010963 | 0.0027478 | -0.010962 | -0.0027473 | 9.8441e-07 | 5.0191e-07 | 0.016354 | 0.016354 | 0.016354 | 0.9975 | -0.047122 | 0.99741 | -0.049007 | 4.4929
16 | 0.012446 | 0.0031201 | -0.012444 | -0.0031188 | 2.3475e-06 | 1.2721e-06 | 0.018701 | 0.018701 | 0.018701 | 0.99035 | -0.18348 | 0.99015 | -0.18744 | 5.1377
17 | 0.093385 | 0.023892 | -0.09332 | -0.023851 | 6.4851e-05 | 4.0491e-05 | 0.14049 | 0.14049 | 0.14049 | 0.99035 | -0.18348 | 0.9896 | -0.19784 | 12.8651
18 | 0.013095 | 0.0032826 | -0.013093 | -0.0032814 | 2.2633e-06 | 1.241e-06 | 0.019508 | 0.019508 | 0.019508 | 0.99889 | -0.020874 | 0.9987 | -0.024502 | 5.3593
19 | -0.3673 | -0.094284 | 0.36767 | 0.094522 | 0.00037252 | 0.00023802 | 0.54794 | 0.54794 | 0.54794 | 0.99889 | -0.020874 | 1 | 0 | 50.1781
20 | 0.0053819 | 0.0013488 | -0.0053815 | -0.0013487 | 4.1726e-07 | 4.1808e-08 | 0.0080292 | 0.0080293 | 0.0080293 | 0.99741 | -0.049007 | 0.99732 | -0.050634 | 2.2059
21 | 0.013884 | 0.0034811 | -0.01388 | -0.0034786 | 4.3634e-06 | 2.4611e-06 | 0.021053 | 0.021054 | 0.021054 | 0.98131 | -0.35833 | 0.98098 | -0.36493 | 5.7839
22 | 0.0066658 | 0.0016706 | -0.0066653 | -0.0016705 | 5.1396e-07 | 1.6381e-07 | 0.010174 | 0.010174 | 0.010174 | 0.97497 | -0.48225 | 0.97489 | -0.48387 | 2.7949
23 | 0.049896 | 0.01254 | -0.049836 | -0.012502 | 6.0378e-05 | 3.8296e-05 | 0.076165 | 0.076165 | 0.076165 | 0.97497 | -0.48225 | 0.97368 | -0.50763 | 20.9244
24 | 0.017358 | 0.0043513 | -0.017356 | -0.00435 | 2.307e-06 | 1.3678e-06 | 0.026528 | 0.026528 | 0.026528 | 0.97368 | -0.50763 | 0.97354 | -0.51042 | 7.2879
25 | 0.032477 | 0.0081507 | -0.032457 | -0.008138 | 2.0294e-05 | 1.2715e-05 | 0.049637 | 0.049637 | 0.049637 | 0.97368 | -0.50763 | 0.97302 | -0.52074 | 13.6365
26 | 0.089659 | 0.022934 | -0.089129 | -0.022596 | 0.0005297 | 0.00033802 | 0.13498 | 0.13498 | 0.13498 | 0.9896 | -0.19784 | 0.98321 | -0.3207 | 37.083
27 | 0.0036614 | 0.00091749 | -0.0036612 | -0.00091758 | 1.8996e-07 | -9.3134e-08 | 0.0055054 | 0.0055055 | 0.0055055 | 0.9896 | -0.19784 | 0.98954 | -0.19893 | 1.5125
28 | 0.015583 | 0.0039059 | -0.015583 | -0.0039054 | 8.7648e-07 | 5.0766e-07 | 0.023584 | 0.023584 | 0.023584 | 0.98321 | -0.3207 | 0.98315 | -0.32188 | 6.4793
29 | 0.073545 | 0.01869 | -0.073238 | -0.018494 | 0.00030742 | 0.00019592 | 0.1114 | 0.1114 | 0.1114 | 0.98321 | -0.3207 | 0.97873 | -0.4079 | 30.6038
30 | 0.060379 | 0.01527 | -0.060169 | -0.015136 | 0.00021006 | 0.00013361 | 0.091848 | 0.091848 | 0.091848 | 0.97873 | -0.4079 | 0.97501 | -0.4807 | 25.233
31 | 0.012859 | 0.0032239 | -0.012855 | -0.0032218 | 3.8148e-06 | 2.1071e-06 | 0.01955 | 0.01955 | 0.01955 | 0.97873 | -0.4079 | 0.97841 | -0.41413 | 5.3709
32 | 0.02905 | 0.0072852 | -0.029038 | -0.0072777 | 1.2081e-05 | 7.5273e-06 | 0.044337 | 0.044337 | 0.044337 | 0.97501 | -0.4807 | 0.97457 | -0.48943 | 12.1805
33 | 0.031119 | 0.0078513 | -0.03101 | -0.0077829 | 0.00010929 | 6.8339e-05 | 0.047511 | 0.047512 | 0.047512 | 0.97501 | -0.4807 | 0.97127 | -0.55432 | 13.0528
34 | 0.0077379 | 0.0019394 | -0.0077375 | -0.0019393 | 4.1423e-07 | 1.6494e-07 | 0.011768 | 0.011768 | 0.011768 | 0.97841 | -0.41413 | 0.97835 | -0.41525 | 3.233
35 | 0.0054422 | 0.0013639 | -0.0054418 | -0.0013639 | 3.9472e-07 | 5.4085e-08 | 0.008218 | 0.008218 | 0.008218 | 0.98541 | -0.27886 | 0.98534 | -0.28038 | 2.2577
36 | 0.0074969 | 0.0018789 | -0.0074966 | -0.0018788 | 3.4377e-07 | 1.2338e-07 | 0.011156 | 0.011156 | 0.011156 | 1 | 0 | 0.99995 | -0.00096256 | 3.0647
37 | 0.0077375 | 0.0019393 | -0.007737 | -0.0019391 | 4.8626e-07 | 1.9364e-07 | 0.011768 | 0.011768 | 0.011768 | 0.97835 | -0.41525 | 0.97829 | -0.41657 | 3.233
38 | 0.03101 | 0.0077829 | -0.03098 | -0.0077643 | 2.9743e-05 | 1.8601e-05 | 0.047512 | 0.047512 | 0.047512 | 0.97127 | -0.55432 | 0.97025 | -0.57445 | 13.0528
39 | 0.0081017 | 0.0020305 | -0.0081012 | -0.0020304 | 4.4814e-07 | 1.8692e-07 | 0.012289 | 0.012289 | 0.012289 | 0.98098 | -0.36493 | 0.98092 | -0.36609 | 3.3762
40 | 0.0095234 | 0.0023869 | -0.0095228 | -0.0023866 | 5.562e-07 | 2.6893e-07 | 0.014556 | 0.014556 | 0.014556 | 0.97354 | -0.51042 | 0.97348 | -0.51165 | 3.9989
41 | 0.032457 | 0.008138 | -0.032448 | -0.0081321 | 9.3834e-06 | 5.8793e-06 | 0.049637 | 0.049637 | 0.049637 | 0.97302 | -0.52074 | 0.97271 | -0.52681 | 13.6366

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41477 | 0.10591

## res_load
| p_mw | q_mvar
0 | 0.078924 | 0.01978
1 | 0.0062811 | 0.0015742
2 | 0.011156 | 0.002796
3 | 0.0056179 | 0.001408
4 | 0.0055801 | 0.0013985
5 | 0.011221 | 0.0028122
6 | 0.0091069 | 0.0022824
7 | 0.0066653 | 0.0016705
8 | 0.0036612 | 0.00091758
9 | 0.015583 | 0.0039054
10 | 0.0051168 | 0.0012824
11 | 0.034806 | 0.0087232
12 | 0.012444 | 0.0031188
13 | 0.013093 | 0.0032814
14 | 0.037951 | 0.0095114
15 | 0.0053815 | 0.0013487
16 | 0.007737 | 0.0019391
17 | 0.029038 | 0.0072777
18 | 0.0057779 | 0.0014481
19 | 0.0078327 | 0.0019631
20 | 0.03098 | 0.0077643
21 | 0.0054418 | 0.0013639
22 | 0.032448 | 0.0081321
23 | 0.0095228 | 0.0023866
24 | 0.0081012 | 0.0020304
25 | 0.0074966 | 0.0018788

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1