## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-110_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-110_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-110_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-110_0_3_node_29 | 0.4 | n |  | TRUE
4 | bus_LV_1630-110_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1630-110_0_3_node_23 | 0.4 | n |  | TRUE
6 | bus_LV_1630-110_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1630-110_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1630-110_0_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1630-110_0_3_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_1630-110_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1630-110_0_3_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1630-110_0_3_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1630-110_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1630-110_0_3_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1630-110_0_3_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1630-110_0_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1630-110_0_3_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1630-110_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1630-110_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1630-110_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1630-110_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1630-110_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1630-110_0_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1630-110_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1630-110_0_3_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_1630-110_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_MV_54_0_node_170 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-110_0_3_load_0 | 0 | 0.046481 | 0.011649 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-110_0_3_load_2 | 2 | 0.003952 | 0.00099046 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-110_0_3_load_29 | 3 | 0.028927 | 0.0072497 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-110_0_3_load_4 | 6 | 0.0056797 | 0.0014235 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-110_0_3_load_5 | 7 | 0.0062706 | 0.0015716 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-110_0_3_load_22 | 9 | 0.0093333 | 0.0023391 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-110_0_3_load_8 | 10 | 0.0093788 | 0.0023506 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-110_0_3_load_16 | 11 | 0.0070867 | 0.0017761 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-110_0_3_load_6 | 13 | 0.01352 | 0.0033883 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-110_0_3_load_7 | 14 | 0.0052009 | 0.0013035 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-110_0_3_load_24 | 15 | 0.0055996 | 0.0014034 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-110_0_3_load_15 | 16 | 0.01789 | 0.0044836 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-110_0_3_load_10 | 17 | 0.0052977 | 0.0013277 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-110_0_3_load_11 | 18 | 0.0039703 | 0.00099504 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-110_0_3_load_14 | 21 | 0.018508 | 0.0046385 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-110_0_3_load_18 | 22 | 0.012073 | 0.0030258 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-110_0_3_load_19 | 23 | 0.055375 | 0.013878 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-110_0_3_load_26 | 25 | 0.0050773 | 0.0012725 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-110_0_3_load_27 | 26 | 0.0048159 | 0.001207 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-110_0_3_line_0 |  | 0 | 1 | 0.014902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-110_0_3_line_1 |  | 0 | 2 | 0.010688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-110_0_3_line_2 |  | 0 | 3 | 0.051482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-110_0_3_line_3 |  | 1 | 4 | 0.012246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-110_0_3_line_4 |  | 3 | 5 | 0.020268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-110_0_3_line_5 |  | 4 | 6 | 0.012683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-110_0_3_line_6 |  | 4 | 7 | 0.028675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-110_0_3_line_7 |  | 5 | 16 | 0.027688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-110_0_3_line_8 |  | 7 | 11 | 0.032268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-110_0_3_line_9 |  | 8 | 9 | 0.015242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1630-110_0_3_line_10 |  | 8 | 10 | 0.013306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-110_0_3_line_11 |  | 9 | 15 | 0.016648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1630-110_0_3_line_12 |  | 10 | 13 | 0.017463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-110_0_3_line_13 |  | 11 | 12 | 0.0045036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1630-110_0_3_line_14 |  | 12 | 22 | 0.009837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-110_0_3_line_15 |  | 12 | 23 | 0.00947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1630-110_0_3_line_16 |  | 13 | 14 | 0.011275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-110_0_3_line_17 |  | 15 | 24 | 0.013851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-110_0_3_line_18 |  | 15 | 23 | 0.041475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1630-110_0_3_line_19 |  | 16 | 20 | 0.020279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-110_0_3_line_20 |  | 17 | 18 | 0.023157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-110_0_3_line_21 |  | 17 | 19 | 0.030834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-110_0_3_line_22 |  | 18 | 20 | 0.038213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-110_0_3_line_23 |  | 19 | 21 | 0.020304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-110_0_3_line_24 |  | 24 | 25 | 0.016442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-110_0_3_line_25 |  | 24 | 26 | 0.011466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-110_0_3_trafo_9 | 0.63 MVA 20/0.4 kV | 27 | 8 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2722803.75 | 1220479.9786 | 2722808.1378 | 1220466.325 | 2722807.6009 | 1220466.1649
1 | 2722797.3584 | 1220463.1114 | 2722807.6009 | 1220466.1649
2 | 2722819.3381 | 1220416.0387 | 2722807.6009 | 1220466.1649
3 | 2722792.0313 | 1220476.3119 | 2722803.75 | 1220479.9786
4 | 2722819.3381 | 1220416.0387 | 2722820.1825 | 1220411.1634 | 2722820.1343 | 1220409.083 | 2722820.1337 | 1220406.1696 | 2722819.7235 | 1220403.2477 | 2722818.2026 | 1220396.0329
5 | 2722792.0313 | 1220476.3119 | 2722788.5389 | 1220488.505
6 | 2722792.0313 | 1220476.3119 | 2722768.2321 | 1220468.8488 | 2722764.5988 | 1220467.9918
7 | 2722818.2026 | 1220396.0329 | 2722819.0796 | 1220389.5793 | 2722823.4967 | 1220378.9176 | 2722825.4977 | 1220369.4933
8 | 2722764.5988 | 1220467.9918 | 2722755.3693 | 1220465.8147 | 2722732.8852 | 1220462.1199
9 | 2722774.1889 | 1220424.3812 | 2722759.9299 | 1220418.996
10 | 2722774.1889 | 1220424.3812 | 2722776.6479 | 1220411.3039
11 | 2722759.9299 | 1220418.996 | 2722744.3552 | 1220413.1139
12 | 2722776.6479 | 1220411.3039 | 2722779.8751 | 1220394.1413
13 | 2722728.4412 | 1220461.3896 | 2722732.8852 | 1220462.1199
14 | 2722728.4412 | 1220461.3896 | 2722718.7346 | 1220459.7926
15 | 2722730.1285 | 1220452.0727 | 2722728.4412 | 1220461.3896
16 | 2722790.9677 | 1220396.1604 | 2722779.8751 | 1220394.1413
17 | 2722731.397 | 1220408.22 | 2722744.3552 | 1220413.1139
18 | 2722744.3552 | 1220413.1139 | 2722730.1285 | 1220452.0727
19 | 2722829.7095 | 1220349.6561 | 2722825.4977 | 1220369.4933
20 | 2722792.2715 | 1220341.9986 | 2722769.5847 | 1220337.3583
21 | 2722739.3763 | 1220331.1796 | 2722769.5847 | 1220337.3583
22 | 2722829.7095 | 1220349.6561 | 2722792.2715 | 1220341.9986
23 | 2722734.9451 | 1220350.9927 | 2722739.3763 | 1220331.1796
24 | 2722731.397 | 1220408.22 | 2722716.0166 | 1220402.409
25 | 2722731.397 | 1220408.22 | 2722734.897 | 1220401.1755 | 2722735.6453 | 1220397.6536

## bus_geodata
| x | y | coords
0 | 2722807.6009 | 1220466.1649
1 | 2722803.75 | 1220479.9786
2 | 2722797.3584 | 1220463.1114
3 | 2722819.3381 | 1220416.0387
4 | 2722792.0313 | 1220476.3119
5 | 2722818.2026 | 1220396.0329
6 | 2722788.5389 | 1220488.505
7 | 2722764.5988 | 1220467.9918
8 | 2722774.1889 | 1220424.3812
9 | 2722759.9299 | 1220418.996
10 | 2722776.6479 | 1220411.3039
11 | 2722732.8852 | 1220462.1199
12 | 2722728.4412 | 1220461.3896
13 | 2722779.8751 | 1220394.1413
14 | 2722790.9677 | 1220396.1604
15 | 2722744.3552 | 1220413.1139
16 | 2722825.4977 | 1220369.4933
17 | 2722769.5847 | 1220337.3583
18 | 2722792.2715 | 1220341.9986
19 | 2722739.3763 | 1220331.1796
20 | 2722829.7095 | 1220349.6561
21 | 2722734.9451 | 1220350.9927
22 | 2722718.7346 | 1220459.7926
23 | 2722730.1285 | 1220452.0727
24 | 2722731.397 | 1220408.22
25 | 2722716.0166 | 1220402.409
26 | 2722735.6453 | 1220397.6536
27 | 2722796.6561 | 1220433.14

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98083 | -0.36791 | 0.046481 | 0.011649
1 | 0.98256 | -0.33421 | 0 | 0
2 | 0.98079 | -0.36867 | 0.003952 | 0.00099046
3 | 0.97726 | -0.43774 | 0.028927 | 0.0072497
4 | 0.98398 | -0.30661 | 0 | 0
5 | 0.97639 | -0.45465 | 0 | 0
6 | 0.98391 | -0.3079 | 0.0056797 | 0.0014235
7 | 0.98746 | -0.23937 | 0.0062706 | 0.0015716
8 | 1 | 0 | -0.2695 | -0.06845
9 | 0.99834 | -0.031447 | 0.0093333 | 0.0023391
10 | 0.99966 | -0.0065194 | 0.0093788 | 0.0023506
11 | 0.99156 | -0.16068 | 0.0070867 | 0.0017761
12 | 0.99186 | -0.15493 | 0 | 0
13 | 0.99936 | -0.012223 | 0.01352 | 0.0033883
14 | 0.99931 | -0.013247 | 0.0052009 | 0.0013035
15 | 0.9966 | -0.064552 | 0.0055996 | 0.0014034
16 | 0.97522 | -0.4778 | 0.01789 | 0.0044836
17 | 0.97319 | -0.51776 | 0.0052977 | 0.0013277
18 | 0.9737 | -0.50762 | 0.0039703 | 0.00099504
19 | 0.97266 | -0.52827 | 0 | 0
20 | 0.97469 | -0.48812 | 0 | 0
21 | 0.97231 | -0.53519 | 0.018508 | 0.0046385
22 | 0.99175 | -0.15704 | 0.012073 | 0.0030258
23 | 0.99255 | -0.14184 | 0.055375 | 0.013878
24 | 0.99647 | -0.066958 | 0 | 0
25 | 0.99639 | -0.068423 | 0.0050773 | 0.0012725
26 | 0.99642 | -0.067927 | 0.0048159 | 0.001207
27 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.12543 | -0.03159 | 0.12563 | 0.031719 | 0.00020246 | 0.00012939 | 0.19034 | 0.19034 | 0.19034 | 0.98083 | -0.36791 | 0.98256 | -0.33421 | 52.2926
1 | 0.0039521 | 0.00099042 | -0.003952 | -0.00099046 | 1.4408e-07 | -4.2675e-08 | 0.0059957 | 0.0059958 | 0.0059958 | 0.98083 | -0.36791 | 0.98079 | -0.36867 | 1.6472
2 | 0.074997 | 0.01895 | -0.074746 | -0.018791 | 0.00025016 | 0.00015946 | 0.11383 | 0.11383 | 0.11383 | 0.98083 | -0.36791 | 0.97726 | -0.43774 | 31.2728
3 | -0.12563 | -0.031719 | 0.1258 | 0.031826 | 0.00016638 | 0.00010633 | 0.19034 | 0.19034 | 0.19034 | 0.98256 | -0.33421 | 0.98398 | -0.30661 | 52.2926
4 | 0.04582 | 0.011541 | -0.045783 | -0.011518 | 3.7017e-05 | 2.3437e-05 | 0.069788 | 0.069788 | 0.069788 | 0.97726 | -0.43774 | 0.97639 | -0.45465 | 19.1726
5 | 0.00568 | 0.0014235 | -0.0056797 | -0.0014235 | 3.5091e-07 | 6.3493e-08 | 0.0085896 | 0.0085896 | 0.0085896 | 0.98398 | -0.30661 | 0.98391 | -0.3079 | 2.3598
6 | -0.13148 | -0.033249 | 0.1319 | 0.033521 | 0.00042555 | 0.00027199 | 0.19893 | 0.19893 | 0.19893 | 0.98398 | -0.30661 | 0.98746 | -0.23937 | 54.6523
7 | 0.045783 | 0.011518 | -0.045732 | -0.011486 | 5.0569e-05 | 3.2018e-05 | 0.069788 | 0.069788 | 0.069788 | 0.97639 | -0.45465 | 0.97522 | -0.4778 | 19.1726
8 | -0.13817 | -0.035093 | 0.1387 | 0.035429 | 0.00052546 | 0.00033588 | 0.20838 | 0.20838 | 0.20838 | 0.98746 | -0.23937 | 0.99156 | -0.16068 | 57.2482
9 | 0.23973 | 0.061399 | -0.23937 | -0.061166 | 0.00036463 | 0.00023297 | 0.3572 | 0.3572 | 0.3572 | 1 | 0 | 0.99834 | -0.031447 | 49.0653
10 | 0.028113 | 0.0070508 | -0.028105 | -0.0070454 | 8.7332e-06 | 5.4147e-06 | 0.041835 | 0.041835 | 0.041835 | 1 | 0 | 0.99966 | -0.0065194 | 11.4931
11 | 0.23004 | 0.058827 | -0.22967 | -0.058592 | 0.00036786 | 0.000235 | 0.34328 | 0.34328 | 0.34328 | 0.99834 | -0.031447 | 0.9966 | -0.064552 | 47.1545
12 | 0.018726 | 0.0046948 | -0.018721 | -0.0046918 | 5.0883e-06 | 3.0276e-06 | 0.027874 | 0.027875 | 0.027875 | 0.99966 | -0.0065194 | 0.99936 | -0.012223 | 7.6578
13 | -0.14579 | -0.037205 | 0.14583 | 0.037231 | 4.0506e-05 | 2.5808e-05 | 0.21902 | 0.21902 | 0.21902 | 0.99156 | -0.16068 | 0.99186 | -0.15493 | 30.0849
14 | 0.012074 | 0.0030264 | -0.012073 | -0.0030258 | 1.2104e-06 | 6.4771e-07 | 0.018114 | 0.018114 | 0.018114 | 0.99186 | -0.15493 | 0.99175 | -0.15704 | 4.9764
15 | -0.1579 | -0.040257 | 0.158 | 0.040321 | 9.9846e-05 | 6.3657e-05 | 0.23713 | 0.23713 | 0.23713 | 0.99186 | -0.15493 | 0.99255 | -0.14184 | 32.5731
16 | 0.0052011 | 0.0013035 | -0.0052009 | -0.0013035 | 2.5358e-07 | 1.4566e-08 | 0.0077443 | 0.0077443 | 0.0077443 | 0.99936 | -0.012223 | 0.99931 | -0.013247 | 2.1276
17 | 0.009895 | 0.00248 | -0.0098938 | -0.0024795 | 1.1338e-06 | 5.4517e-07 | 0.014774 | 0.014774 | 0.014774 | 0.9966 | -0.064552 | 0.99647 | -0.066958 | 4.0589
18 | 0.21417 | 0.054708 | -0.21338 | -0.054199 | 0.00079707 | 0.00050905 | 0.32015 | 0.32015 | 0.32015 | 0.9966 | -0.064552 | 0.99255 | -0.14184 | 43.9767
19 | 0.027842 | 0.0070022 | -0.027829 | -0.0069937 | 1.3731e-05 | 8.5347e-06 | 0.042491 | 0.042492 | 0.042492 | 0.97522 | -0.4778 | 0.97469 | -0.48812 | 11.6735
20 | -0.023821 | -0.0059755 | 0.023833 | 0.0059825 | 1.1521e-05 | 7.0856e-06 | 0.036424 | 0.036424 | 0.036424 | 0.97319 | -0.51776 | 0.9737 | -0.50762 | 10.0067
21 | 0.018523 | 0.0046477 | -0.018514 | -0.0046422 | 9.2763e-06 | 5.5539e-06 | 0.028324 | 0.028324 | 0.028324 | 0.97319 | -0.51776 | 0.97266 | -0.52827 | 7.7814
22 | -0.027803 | -0.0069776 | 0.027829 | 0.0069937 | 2.5873e-05 | 1.6083e-05 | 0.042492 | 0.042492 | 0.042492 | 0.9737 | -0.50762 | 0.97469 | -0.48812 | 11.6736
23 | 0.018514 | 0.0046422 | -0.018508 | -0.0046385 | 6.1085e-06 | 3.6575e-06 | 0.028324 | 0.028324 | 0.028324 | 0.97266 | -0.52827 | 0.97231 | -0.53519 | 7.7814
24 | 0.0050777 | 0.0012725 | -0.0050773 | -0.0012725 | 3.5448e-07 | 1.2703e-08 | 0.0075824 | 0.0075825 | 0.0075825 | 0.99647 | -0.066958 | 0.99639 | -0.068423 | 2.0831
25 | 0.0048162 | 0.001207 | -0.0048159 | -0.001207 | 2.2241e-07 | -7.0241e-09 | 0.0071919 | 0.0071919 | 0.0071919 | 0.99647 | -0.066958 | 0.99642 | -0.067927 | 1.9758

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.2695 | 0.06845

## res_load
| p_mw | q_mvar
0 | 0.046481 | 0.011649
1 | 0.003952 | 0.00099046
2 | 0.028927 | 0.0072497
3 | 0.0056797 | 0.0014235
4 | 0.0062706 | 0.0015716
5 | 0.0093333 | 0.0023391
6 | 0.0093788 | 0.0023506
7 | 0.0070867 | 0.0017761
8 | 0.01352 | 0.0033883
9 | 0.0052009 | 0.0013035
10 | 0.0055996 | 0.0014034
11 | 0.01789 | 0.0044836
12 | 0.0052977 | 0.0013277
13 | 0.0039703 | 0.00099504
14 | 0.018508 | 0.0046385
15 | 0.012073 | 0.0030258
16 | 0.055375 | 0.013878
17 | 0.0050773 | 0.0012725
18 | 0.0048159 | 0.001207

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1