## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-116_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-116_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-116_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-116_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-116_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-116_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1630-116_0_3_node_36 | 0.4 | n |  | TRUE
7 | bus_LV_1630-116_0_3_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_1630-116_0_3_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_1630-116_0_3_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_1630-116_0_3_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1630-116_0_3_node_41 | 0.4 | n |  | TRUE
12 | bus_LV_1630-116_0_3_node_40 | 0.4 | n |  | TRUE
13 | bus_LV_1630-116_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1630-116_0_3_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_1630-116_0_3_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_1630-116_0_3_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_1630-116_0_3_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_1630-116_0_3_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1630-116_0_3_node_6 | 0.4 | n |  | TRUE
20 | bus_LV_1630-116_0_3_node_7 | 0.4 | n |  | TRUE
21 | bus_LV_1630-116_0_3_node_8 | 0.4 | n |  | TRUE
22 | bus_LV_1630-116_0_3_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_1630-116_0_3_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_1630-116_0_3_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_1630-116_0_3_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_1630-116_0_3_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_1630-116_0_3_node_38 | 0.4 | n |  | TRUE
28 | bus_LV_1630-116_0_3_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1630-116_0_3_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_1630-116_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1630-116_0_3_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_1630-116_0_3_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1630-116_0_3_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_1630-116_0_3_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_1630-116_0_3_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_1630-116_0_3_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1630-116_0_3_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_1630-116_0_3_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_1630-116_0_3_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_1630-116_0_3_node_31 | 0.4 | n |  | TRUE
41 | bus_MV_54_0_node_83 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-116_0_3_load_0 | 0 | 0.0085569 | 0.0021446 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-116_0_3_load_1 | 1 | 0.0085781 | 0.0021499 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-116_0_3_load_5 | 5 | 0.0083682 | 0.0020973 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-116_0_3_load_32 | 8 | 0.0083767 | 0.0020994 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-116_0_3_load_29 | 9 | 0.0080968 | 0.0020293 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-116_0_3_load_17 | 10 | 0.0083415 | 0.0020906 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-116_0_3_load_41 | 11 | 0.044846 | 0.01124 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-116_0_3_load_40 | 12 | 0.038261 | 0.0095891 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-116_0_3_load_33 | 14 | 0.01288 | 0.0032281 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-116_0_3_load_35 | 16 | 0.0065307 | 0.0016368 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-116_0_3_load_30 | 17 | 0.006498 | 0.0016285 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-116_0_3_load_16 | 18 | 0.0084787 | 0.002125 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-116_0_3_load_6 | 19 | 0.0063707 | 0.0015966 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-116_0_3_load_9 | 22 | 0.0081909 | 0.0020528 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-116_0_3_load_11 | 24 | 0.0022271 | 0.00055817 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-116_0_3_load_12 | 25 | 0.02187 | 0.0054811 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-116_0_3_load_13 | 26 | 0.0084238 | 0.0021112 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-116_0_3_load_38 | 27 | 0.0097208 | 0.0024363 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-116_0_3_load_26 | 28 | 0.0064339 | 0.0016125 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-116_0_3_load_25 | 30 | 0.0091841 | 0.0023018 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-116_0_3_load_14 | 31 | 0.012538 | 0.0031424 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-116_0_3_load_39 | 33 | 0.030756 | 0.0077082 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-116_0_3_load_22 | 34 | 0.0025022 | 0.0006271 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-116_0_3_load_37 | 37 | 0.0065289 | 0.0016363 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-116_0_3_load_27 | 39 | 0.0064688 | 0.0016212 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-116_0_3_load_31 | 40 | 0.0064091 | 0.0016063 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-116_0_3_line_0 |  | 0 | 1 | 0.0045531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-116_0_3_line_1 |  | 0 | 2 | 0.0058573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-116_0_3_line_2 |  | 1 | 3 | 0.021638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-116_0_3_line_3 |  | 2 | 4 | 0.004577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-116_0_3_line_4 |  | 2 | 5 | 0.015042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1630-116_0_3_line_5 |  | 3 | 6 | 0.018082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-116_0_3_line_6 |  | 3 | 7 | 0.021079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-116_0_3_line_7 |  | 4 | 8 | 0.015918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-116_0_3_line_8 |  | 4 | 9 | 0.013498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-116_0_3_line_9 |  | 5 | 10 | 0.0063346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1630-116_0_3_line_10 |  | 6 | 11 | 0.004017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-116_0_3_line_11 |  | 7 | 12 | 0.003446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-116_0_3_line_12 |  | 8 | 16 | 0.0063903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-116_0_3_line_13 |  | 9 | 17 | 0.0059756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-116_0_3_line_14 |  | 10 | 18 | 0.022218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-116_0_3_line_15 |  | 13 | 14 | 0.016712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-116_0_3_line_16 |  | 13 | 15 | 0.043129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-116_0_3_line_17 |  | 15 | 32 | 0.013142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-116_0_3_line_18 |  | 15 | 18 | 0.010561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-116_0_3_line_19 |  | 17 | 40 | 0.0007159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-116_0_3_line_20 |  | 19 | 20 | 0.01765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-116_0_3_line_21 |  | 19 | 21 | 0.003234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-116_0_3_line_22 |  | 20 | 22 | 0.014865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-116_0_3_line_23 |  | 20 | 23 | 0.005833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-116_0_3_line_24 |  | 21 | 24 | 0.012572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-116_0_3_line_25 |  | 21 | 25 | 0.015921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-116_0_3_line_26 |  | 22 | 26 | 0.0018316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-116_0_3_line_27 |  | 23 | 27 | 0.01054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-116_0_3_line_28 |  | 23 | 28 | 0.016186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-116_0_3_line_29 |  | 25 | 29 | 0.011411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-116_0_3_line_30 |  | 28 | 30 | 0.00070827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-116_0_3_line_31 |  | 29 | 31 | 0.051923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-116_0_3_line_32 |  | 30 | 39 | 0.0053759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-116_0_3_line_33 |  | 32 | 33 | 0.008116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-116_0_3_line_34 |  | 34 | 35 | 0.014017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1630-116_0_3_line_35 |  | 35 | 36 | 0.005065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-116_0_3_line_36 |  | 36 | 37 | 0.043862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-116_0_3_line_37 |  | 37 | 38 | 0.01765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-116_0_3_line_38 |  | 38 | 40 | 0.016217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-116_0_3_line_39 |  | 38 | 39 | 0.022601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-116_0_3_trafo_17 | 0.63 MVA 20/0.4 kV | 41 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2722378.4248 | 1220493.9995 | 2722380.0649 | 1220489.752
1 | 2722376.3151 | 1220499.4636 | 2722378.4248 | 1220493.9995
2 | 2722387.8589 | 1220469.5662 | 2722380.0649 | 1220489.752
3 | 2722374.6036 | 1220503.7095 | 2722376.3151 | 1220499.4636
4 | 2722376.3151 | 1220499.4636 | 2722362.2437 | 1220494.1477
5 | 2722405.3047 | 1220474.5064 | 2722387.8589 | 1220469.5662
6 | 2722370.4894 | 1220462.3927 | 2722388.6527 | 1220467.5032 | 2722387.8589 | 1220469.5662
7 | 2722374.6036 | 1220503.7095 | 2722389.5984 | 1220509.0522
8 | 2722374.6036 | 1220503.7095 | 2722371.2128 | 1220512.1131 | 2722369.4338 | 1220516.1768
9 | 2722362.2437 | 1220494.1477 | 2722356.3179 | 1220491.909
10 | 2722405.3047 | 1220474.5064 | 2722406.4239 | 1220470.6486
11 | 2722370.4894 | 1220462.3927 | 2722371.3322 | 1220459.0518
12 | 2722395.618 | 1220511.1971 | 2722389.5984 | 1220509.0522
13 | 2722367.0375 | 1220521.6509 | 2722369.4338 | 1220516.1768
14 | 2722356.3179 | 1220491.909 | 2722344.3151 | 1220487.3745 | 2722346.2504 | 1220478.1888
15 | 2722363.1487 | 1220427.7592 | 2722347.0044 | 1220423.4419
16 | 2722348.4277 | 1220467.8548 | 2722351.8312 | 1220463.9995 | 2722354.2503 | 1220457.8222 | 2722363.1487 | 1220427.7592
17 | 2722348.4277 | 1220467.8548 | 2722335.6771 | 1220464.5237
18 | 2722348.4277 | 1220467.8548 | 2722346.2504 | 1220478.1888
19 | 2722367.0375 | 1220521.6509 | 2722366.7504 | 1220522.3067
20 | 2722322.1738 | 1220503.7326 | 2722307.4475 | 1220494.004
21 | 2722304.7492 | 1220492.2214 | 2722307.4475 | 1220494.004
22 | 2722322.1738 | 1220503.7326 | 2722324.5023 | 1220498.265 | 2722325.2356 | 1220495.8226 | 2722325.0647 | 1220493.4284 | 2722324.3897 | 1220491.5575 | 2722323.015 | 1220490.1281 | 2722323.015 | 1220490.1281
23 | 2722326.4406 | 1220507.7234 | 2722322.1738 | 1220503.7326
24 | 2722304.7492 | 1220492.2214 | 2722298.2962 | 1220503.0195
25 | 2722304.7492 | 1220492.2214 | 2722291.5129 | 1220483.3732
26 | 2722321.2815 | 1220489.5365 | 2722323.015 | 1220490.1281
27 | 2722326.4406 | 1220507.7234 | 2722321.776 | 1220517.1794
28 | 2722326.4406 | 1220507.7234 | 2722338.3428 | 1220518.6919
29 | 2722282.0266 | 1220477.0318 | 2722291.5129 | 1220483.3732
30 | 2722338.3428 | 1220518.6919 | 2722338.8636 | 1220519.1719
31 | 2722282.0266 | 1220477.0318 | 2722286.1772 | 1220462.6725 | 2722289.1889 | 1220456.8297 | 2722304.1573 | 1220448.6307 | 2722305.8885 | 1220447.4875 | 2722307.9127 | 1220436.41
32 | 2722342.8169 | 1220522.815 | 2722338.8636 | 1220519.1719
33 | 2722335.6771 | 1220464.5237 | 2722337.902 | 1220456.7188
34 | 2722414.9897 | 1220574.4837 | 2722418.9698 | 1220561.0438
35 | 2722410.0835 | 1220573.1707 | 2722414.9897 | 1220574.4837
36 | 2722410.0835 | 1220573.1707 | 2722384.2464 | 1220553.3465 | 2722374.8808 | 1220547.0311
37 | 2722360.2468 | 1220537.163 | 2722374.8808 | 1220547.0311
38 | 2722360.2468 | 1220537.163 | 2722366.7504 | 1220522.3067
39 | 2722360.2468 | 1220537.163 | 2722354.0107 | 1220532.6091 | 2722348.384 | 1220527.9454 | 2722342.8169 | 1220522.815

## bus_geodata
| x | y | coords
0 | 2722378.4248 | 1220493.9995
1 | 2722380.0649 | 1220489.752
2 | 2722376.3151 | 1220499.4636
3 | 2722387.8589 | 1220469.5662
4 | 2722374.6036 | 1220503.7095
5 | 2722362.2437 | 1220494.1477
6 | 2722405.3047 | 1220474.5064
7 | 2722370.4894 | 1220462.3927
8 | 2722389.5984 | 1220509.0522
9 | 2722369.4338 | 1220516.1768
10 | 2722356.3179 | 1220491.909
11 | 2722406.4239 | 1220470.6486
12 | 2722371.3322 | 1220459.0518
13 | 2722363.1487 | 1220427.7592
14 | 2722347.0044 | 1220423.4419
15 | 2722348.4277 | 1220467.8548
16 | 2722395.618 | 1220511.1971
17 | 2722367.0375 | 1220521.6509
18 | 2722346.2504 | 1220478.1888
19 | 2722307.4475 | 1220494.004
20 | 2722322.1738 | 1220503.7326
21 | 2722304.7492 | 1220492.2214
22 | 2722323.015 | 1220490.1281
23 | 2722326.4406 | 1220507.7234
24 | 2722298.2962 | 1220503.0195
25 | 2722291.5129 | 1220483.3732
26 | 2722321.2815 | 1220489.5365
27 | 2722321.776 | 1220517.1794
28 | 2722338.3428 | 1220518.6919
29 | 2722282.0266 | 1220477.0318
30 | 2722338.8636 | 1220519.1719
31 | 2722307.9127 | 1220436.41
32 | 2722335.6771 | 1220464.5237
33 | 2722337.902 | 1220456.7188
34 | 2722418.9698 | 1220561.0438
35 | 2722414.9897 | 1220574.4837
36 | 2722410.0835 | 1220573.1707
37 | 2722374.8808 | 1220547.0311
38 | 2722360.2468 | 1220537.163
39 | 2722342.8169 | 1220522.815
40 | 2722366.7504 | 1220522.3067
41 | 2722376.3151 | 1220499.4636

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99713 | -0.054935 | 0.0085569 | 0.0021446
1 | 0.99675 | -0.062256 | 0.0085781 | 0.0021499
2 | 0.99767 | -0.044647 | 0 | 0
3 | 0.99511 | -0.093856 | 0 | 0
4 | 0.99709 | -0.055584 | 0 | 0
5 | 0.99929 | -0.013534 | 0.0083682 | 0.0020973
6 | 0.99437 | -0.10814 | 0 | 0
7 | 0.99437 | -0.10806 | 0 | 0
8 | 0.99688 | -0.059746 | 0.0083767 | 0.0020994
9 | 0.99559 | -0.084372 | 0.0080968 | 0.0020293
10 | 1 | 0 | -0.30042 | -0.075526
11 | 0.99421 | -0.11132 | 0.044846 | 0.01124
12 | 0.99425 | -0.11039 | 0.038261 | 0.0095891
13 | 0.99802 | -0.037974 | 0 | 0
14 | 0.99783 | -0.041741 | 0.01288 | 0.0032281
15 | 0.99853 | -0.028257 | 0 | 0
16 | 0.99684 | -0.060478 | 0.0065307 | 0.0016368
17 | 0.99497 | -0.096293 | 0.006498 | 0.0016285
18 | 0.99895 | -0.020204 | 0.0084787 | 0.002125
19 | 0.989 | -0.21164 | 0.0063707 | 0.0015966
20 | 0.9897 | -0.19812 | 0 | 0
21 | 0.98889 | -0.21375 | 0 | 0
22 | 0.98947 | -0.20252 | 0.0081909 | 0.0020528
23 | 0.99002 | -0.19193 | 0 | 0
24 | 0.98887 | -0.21425 | 0.0022271 | 0.00055817
25 | 0.98839 | -0.22352 | 0.02187 | 0.0054811
26 | 0.98946 | -0.20279 | 0.0084238 | 0.0021112
27 | 0.98992 | -0.19375 | 0.0097208 | 0.0024363
28 | 0.99105 | -0.17199 | 0.0064339 | 0.0016125
29 | 0.98826 | -0.22607 | 0 | 0
30 | 0.9911 | -0.17104 | 0.0091841 | 0.0023018
31 | 0.98766 | -0.2377 | 0.012538 | 0.0031424
32 | 0.99816 | -0.035325 | 0 | 0
33 | 0.99794 | -0.039693 | 0.030756 | 0.0077082
34 | 0.99312 | -0.13197 | 0.0025022 | 0.0006271
35 | 0.99315 | -0.13135 | 0 | 0
36 | 0.99316 | -0.13113 | 0 | 0
37 | 0.99326 | -0.12919 | 0.0065289 | 0.0016363
38 | 0.99341 | -0.12637 | 0 | 0
39 | 0.99152 | -0.16294 | 0.0064688 | 0.0016212
40 | 0.9949 | -0.09764 | 0.0064091 | 0.0016063
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.09191 | 0.023122 | -0.091878 | -0.023101 | 3.2135e-05 | 2.0507e-05 | 0.13719 | 0.13719 | 0.13719 | 0.99713 | -0.054935 | 0.99675 | -0.062256 | 37.6891
1 | -0.10047 | -0.025266 | 0.10052 | 0.025298 | 4.9393e-05 | 3.1535e-05 | 0.14996 | 0.14996 | 0.14996 | 0.99713 | -0.054935 | 0.99767 | -0.044647 | 41.1972
2 | 0.0833 | 0.020951 | -0.083175 | -0.020871 | 0.00012554 | 8.0062e-05 | 0.12438 | 0.12438 | 0.12438 | 0.99675 | -0.062256 | 0.99511 | -0.093856 | 34.171
3 | 0.13717 | 0.034683 | -0.1371 | -0.034637 | 7.1915e-05 | 4.5966e-05 | 0.20469 | 0.20469 | 0.20469 | 0.99767 | -0.044647 | 0.99709 | -0.055584 | 56.2343
4 | -0.23768 | -0.059981 | 0.23804 | 0.060208 | 0.00035474 | 0.00022664 | 0.35465 | 0.35465 | 0.35465 | 0.99767 | -0.044647 | 0.99929 | -0.013534 | 48.7157
5 | 0.044884 | 0.011263 | -0.044853 | -0.011244 | 3.0549e-05 | 1.9316e-05 | 0.067121 | 0.067121 | 0.067121 | 0.99511 | -0.093856 | 0.99437 | -0.10814 | 18.4398
6 | 0.038291 | 0.0096081 | -0.038265 | -0.0095917 | 2.5919e-05 | 1.6314e-05 | 0.057262 | 0.057262 | 0.057262 | 0.99511 | -0.093856 | 0.99437 | -0.10806 | 15.7313
7 | 0.014911 | 0.0037379 | -0.014908 | -0.0037362 | 2.9558e-06 | 1.6841e-06 | 0.022252 | 0.022252 | 0.022252 | 0.99709 | -0.055584 | 0.99688 | -0.059746 | 6.1133
8 | 0.12218 | 0.030899 | -0.12202 | -0.030792 | 0.00016848 | 0.00010765 | 0.18244 | 0.18244 | 0.18244 | 0.99709 | -0.055584 | 0.99559 | -0.084372 | 50.121
9 | -0.24641 | -0.062305 | 0.24657 | 0.062407 | 0.00016007 | 0.00010228 | 0.36711 | 0.36711 | 0.36711 | 0.99929 | -0.013534 | 1 | 0 | 50.4273
10 | 0.044853 | 0.011244 | -0.044846 | -0.01124 | 6.7865e-06 | 4.2913e-06 | 0.067121 | 0.067121 | 0.067121 | 0.99437 | -0.10814 | 0.99421 | -0.11132 | 18.4398
11 | 0.038265 | 0.0095917 | -0.038261 | -0.0095891 | 4.2372e-06 | 2.6671e-06 | 0.057262 | 0.057262 | 0.057262 | 0.99437 | -0.10806 | 0.99425 | -0.11039 | 15.7313
12 | 0.006531 | 0.0016368 | -0.0065307 | -0.0016368 | 2.2774e-07 | 6.2443e-08 | 0.0097486 | 0.0097486 | 0.0097486 | 0.99688 | -0.059746 | 0.99684 | -0.060478 | 2.6782
13 | 0.11392 | 0.028762 | -0.11385 | -0.028721 | 6.502e-05 | 4.1535e-05 | 0.17034 | 0.17034 | 0.17034 | 0.99559 | -0.084372 | 0.99497 | -0.096293 | 46.7964
14 | 0.052207 | 0.013119 | -0.052157 | -0.013087 | 5.0298e-05 | 3.1899e-05 | 0.077697 | 0.077697 | 0.077697 | 1 | 0 | 0.99895 | -0.020204 | 21.3453
15 | 0.012882 | 0.0032293 | -0.01288 | -0.0032281 | 2.312e-06 | 1.2614e-06 | 0.019207 | 0.019208 | 0.019208 | 0.99802 | -0.037974 | 0.99783 | -0.041741 | 5.2768
16 | -0.012882 | -0.0032293 | 0.012888 | 0.0032326 | 5.9668e-06 | 3.2549e-06 | 0.019207 | 0.019207 | 0.019207 | 0.99802 | -0.037974 | 0.99853 | -0.028257 | 5.2768
17 | 0.030773 | 0.0077186 | -0.030762 | -0.0077122 | 1.0365e-05 | 6.4616e-06 | 0.04586 | 0.04586 | 0.04586 | 0.99853 | -0.028257 | 0.99816 | -0.035325 | 12.5989
18 | -0.043661 | -0.010951 | 0.043678 | 0.010962 | 1.6767e-05 | 1.0593e-05 | 0.065067 | 0.065067 | 0.065067 | 0.99853 | -0.028257 | 0.99895 | -0.020204 | 17.8756
19 | 0.10736 | 0.027092 | -0.10735 | -0.027088 | 6.9261e-06 | 4.4234e-06 | 0.16062 | 0.16062 | 0.16062 | 0.99497 | -0.096293 | 0.9949 | -0.09764 | 44.1267
20 | -0.043034 | -0.010795 | 0.043062 | 0.010813 | 2.775e-05 | 1.7533e-05 | 0.064751 | 0.064751 | 0.064751 | 0.989 | -0.21164 | 0.9897 | -0.19812 | 17.7887
21 | 0.036663 | 0.0091985 | -0.03666 | -0.0091962 | 3.6907e-06 | 2.3206e-06 | 0.055166 | 0.055166 | 0.055166 | 0.989 | -0.21164 | 0.98889 | -0.21375 | 15.1555
22 | 0.016618 | 0.0041661 | -0.016615 | -0.0041641 | 3.4802e-06 | 2.0363e-06 | 0.024986 | 0.024986 | 0.024986 | 0.9897 | -0.19812 | 0.98947 | -0.20252 | 6.8643
23 | -0.05968 | -0.014979 | 0.059698 | 0.01499 | 1.7614e-05 | 1.1198e-05 | 0.089737 | 0.089737 | 0.089737 | 0.9897 | -0.19812 | 0.99002 | -0.19193 | 24.653
24 | 0.0022272 | 0.00055804 | -0.0022271 | -0.00055817 | 5.2948e-08 | -1.274e-07 | 0.0033512 | 0.0033513 | 0.0033513 | 0.98889 | -0.21375 | 0.98887 | -0.21425 | 0.92068
25 | 0.034433 | 0.0086382 | -0.034417 | -0.0086281 | 1.6029e-05 | 1.0055e-05 | 0.051815 | 0.051815 | 0.051815 | 0.98889 | -0.21375 | 0.98839 | -0.22352 | 14.2348
26 | 0.0084239 | 0.0021113 | -0.0084238 | -0.0021112 | 1.1023e-07 | 4.7022e-08 | 0.012668 | 0.012668 | 0.012668 | 0.98947 | -0.20252 | 0.98946 | -0.20279 | 3.4803
27 | 0.0097217 | 0.0024367 | -0.0097208 | -0.0024363 | 8.439e-07 | 4.0458e-07 | 0.014612 | 0.014612 | 0.014612 | 0.99002 | -0.19193 | 0.98992 | -0.19375 | 4.0143
28 | -0.06942 | -0.017427 | 0.069486 | 0.017469 | 6.609e-05 | 4.2089e-05 | 0.10435 | 0.10435 | 0.10435 | 0.99002 | -0.19193 | 0.99105 | -0.17199 | 28.6673
29 | 0.012547 | 0.003147 | -0.012545 | -0.0031462 | 1.5269e-06 | 8.31e-07 | 0.01889 | 0.01889 | 0.01889 | 0.98839 | -0.22352 | 0.98826 | -0.22607 | 5.1896
30 | -0.075919 | -0.019081 | 0.075923 | 0.019083 | 3.4523e-06 | 2.2003e-06 | 0.11401 | 0.11401 | 0.11401 | 0.99105 | -0.17199 | 0.9911 | -0.17104 | 31.3212
31 | 0.012545 | 0.0031462 | -0.012538 | -0.0031424 | 6.9481e-06 | 3.7819e-06 | 0.01889 | 0.01889 | 0.01889 | 0.98826 | -0.22607 | 0.98766 | -0.2377 | 5.1897
32 | -0.085107 | -0.021385 | 0.08514 | 0.021406 | 3.2926e-05 | 2.1003e-05 | 0.1278 | 0.1278 | 0.1278 | 0.9911 | -0.17104 | 0.99152 | -0.16294 | 35.1093
33 | 0.030762 | 0.0077122 | -0.030756 | -0.0077082 | 6.4009e-06 | 3.9905e-06 | 0.04586 | 0.04586 | 0.04586 | 0.99816 | -0.035325 | 0.99794 | -0.039693 | 12.5989
34 | -0.0025022 | -0.0006271 | 0.0025022 | 0.00062697 | 7.3878e-08 | -1.3409e-07 | 0.003749 | 0.003749 | 0.003749 | 0.99312 | -0.13197 | 0.99315 | -0.13135 | 1.03
35 | -0.0025022 | -0.00062697 | 0.0025023 | 0.00062692 | 2.6695e-08 | -4.8458e-08 | 0.003749 | 0.003749 | 0.003749 | 0.99315 | -0.13135 | 0.99316 | -0.13113 | 1.0299
36 | -0.0025023 | -0.00062692 | 0.0025025 | 0.0006265 | 2.3116e-07 | -4.1971e-07 | 0.003749 | 0.0037488 | 0.003749 | 0.99316 | -0.13113 | 0.99326 | -0.12919 | 1.0299
37 | -0.0090314 | -0.0022628 | 0.0090326 | 0.0022633 | 1.2116e-06 | 5.4694e-07 | 0.01353 | 0.01353 | 0.01353 | 0.99326 | -0.12919 | 0.99341 | -0.12637 | 3.717
38 | -0.1008 | -0.025393 | 0.10094 | 0.025482 | 0.00013873 | 8.8577e-05 | 0.15104 | 0.15104 | 0.15104 | 0.99341 | -0.12637 | 0.9949 | -0.09764 | 41.4933
39 | 0.091769 | 0.02313 | -0.091609 | -0.023027 | 0.00016025 | 0.00010227 | 0.13751 | 0.13751 | 0.13751 | 0.99341 | -0.12637 | 0.99152 | -0.16294 | 37.7763

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30877 | 0.077616

## res_load
| p_mw | q_mvar
0 | 0.0085569 | 0.0021446
1 | 0.0085781 | 0.0021499
2 | 0.0083682 | 0.0020973
3 | 0.0083767 | 0.0020994
4 | 0.0080968 | 0.0020293
5 | 0.0083415 | 0.0020906
6 | 0.044846 | 0.01124
7 | 0.038261 | 0.0095891
8 | 0.01288 | 0.0032281
9 | 0.0065307 | 0.0016368
10 | 0.006498 | 0.0016285
11 | 0.0084787 | 0.002125
12 | 0.0063707 | 0.0015966
13 | 0.0081909 | 0.0020528
14 | 0.0022271 | 0.00055817
15 | 0.02187 | 0.0054811
16 | 0.0084238 | 0.0021112
17 | 0.0097208 | 0.0024363
18 | 0.0064339 | 0.0016125
19 | 0.0091841 | 0.0023018
20 | 0.012538 | 0.0031424
21 | 0.030756 | 0.0077082
22 | 0.0025022 | 0.0006271
23 | 0.0065289 | 0.0016363
24 | 0.0064688 | 0.0016212
25 | 0.0064091 | 0.0016063

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1