## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-121_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-121_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-121_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-121_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-121_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-121_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1630-121_0_4_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_1630-121_0_4_node_29 | 0.4 | n |  | TRUE
8 | bus_LV_1630-121_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1630-121_0_4_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_1630-121_0_4_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1630-121_0_4_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1630-121_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1630-121_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1630-121_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1630-121_0_4_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_1630-121_0_4_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_1630-121_0_4_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_1630-121_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1630-121_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1630-121_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1630-121_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1630-121_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1630-121_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1630-121_0_4_node_51 | 0.4 | n |  | TRUE
25 | bus_LV_1630-121_0_4_node_53 | 0.4 | n |  | TRUE
26 | bus_LV_1630-121_0_4_node_54 | 0.4 | n |  | TRUE
27 | bus_LV_1630-121_0_4_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_1630-121_0_4_node_47 | 0.4 | n |  | TRUE
29 | bus_LV_1630-121_0_4_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_1630-121_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1630-121_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1630-121_0_4_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1630-121_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1630-121_0_4_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_1630-121_0_4_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_1630-121_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1630-121_0_4_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_1630-121_0_4_node_49 | 0.4 | n |  | TRUE
39 | bus_LV_1630-121_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_1630-121_0_4_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_1630-121_0_4_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_1630-121_0_4_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_1630-121_0_4_node_50 | 0.4 | n |  | TRUE
44 | bus_LV_1630-121_0_4_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_1630-121_0_4_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_1630-121_0_4_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_1630-121_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_1630-121_0_4_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_1630-121_0_4_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_1630-121_0_4_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_1630-121_0_4_node_45 | 0.4 | n |  | TRUE
52 | bus_MV_54_0_node_86 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-121_0_4_load_0 | 0 | 0.013771 | 0.0034513 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-121_0_4_load_1 | 1 | 0.013623 | 0.0034143 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-121_0_4_load_2 | 2 | 0.0060787 | 0.0015235 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-121_0_4_load_3 | 3 | 0.015877 | 0.0039791 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-121_0_4_load_8 | 5 | 0.010409 | 0.0026087 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-121_0_4_load_29 | 7 | 0.090053 | 0.022569 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-121_0_4_load_6 | 8 | 0.0099555 | 0.0024951 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-121_0_4_load_22 | 9 | 0.0094939 | 0.0023794 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-121_0_4_load_30 | 10 | 0.011527 | 0.002889 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-121_0_4_load_5 | 11 | 0.018697 | 0.0046858 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-121_0_4_load_9 | 13 | 0.022889 | 0.0057366 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-121_0_4_load_10 | 14 | 0.0057048 | 0.0014298 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-121_0_4_load_37 | 15 | 0.015756 | 0.0039489 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-121_0_4_load_38 | 16 | 0.004138 | 0.0010371 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-121_0_4_load_14 | 18 | 0.0092311 | 0.0023135 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-121_0_4_load_11 | 19 | 0.0036536 | 0.00091567 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-121_0_4_load_15 | 22 | 0.001875 | 0.00046992 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-121_0_4_load_53 | 25 | 0.031102 | 0.007795 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-121_0_4_load_54 | 26 | 0.027045 | 0.0067782 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-121_0_4_load_32 | 29 | 0.002454 | 0.00061503 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-121_0_4_load_18 | 31 | 0.0073071 | 0.0018313 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-121_0_4_load_20 | 33 | 0.019311 | 0.0048399 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-121_0_4_load_48 | 37 | 0.014854 | 0.0037228 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-121_0_4_load_24 | 39 | 0.0060306 | 0.0015114 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-121_0_4_load_25 | 40 | 0.0052157 | 0.0013072 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-121_0_4_load_26 | 41 | 0.0032683 | 0.00081911 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-121_0_4_load_33 | 42 | 0.023778 | 0.0059593 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-121_0_4_load_50 | 43 | 0.01073 | 0.0026892 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-121_0_4_load_39 | 44 | 0.006015 | 0.0015075 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-121_0_4_load_43 | 46 | 0.004681 | 0.0011732 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-121_0_4_load_46 | 48 | 0.0055928 | 0.0014017 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1630-121_0_4_load_44 | 49 | 0.0046536 | 0.0011663 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1630-121_0_4_load_52 | 50 | 0.0055522 | 0.0013915 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-121_0_4_line_0 |  | 0 | 1 | 0.020808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-121_0_4_line_1 |  | 0 | 2 | 0.0010446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-121_0_4_line_2 |  | 1 | 3 | 0.002841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1630-121_0_4_line_3 |  | 2 | 4 | 0.01297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-121_0_4_line_4 |  | 3 | 5 | 0.018081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_1630-121_0_4_line_5 |  | 4 | 6 | 0.031153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-121_0_4_line_6 |  | 4 | 7 | 0.020551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-121_0_4_line_7 |  | 5 | 8 | 0.0084104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1630-121_0_4_line_8 |  | 6 | 9 | 0.005523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-121_0_4_line_9 |  | 7 | 10 | 0.011869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-121_0_4_line_10 |  | 8 | 11 | 0.021828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_1630-121_0_4_line_11 |  | 11 | 12 | 0.019082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1630-121_0_4_line_12 |  | 12 | 13 | 0.015028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-121_0_4_line_13 |  | 12 | 14 | 0.0060354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-121_0_4_line_14 |  | 13 | 15 | 0.019548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-121_0_4_line_15 |  | 14 | 16 | 0.0045631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-121_0_4_line_16 |  | 15 | 17 | 0.01518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-121_0_4_line_17 |  | 16 | 18 | 0.010721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-121_0_4_line_18 |  | 17 | 42 | 0.017141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-121_0_4_line_19 |  | 18 | 20 | 0.084462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-121_0_4_line_20 |  | 19 | 20 | 0.04146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-121_0_4_line_21 |  | 19 | 21 | 0.023039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-121_0_4_line_22 |  | 20 | 22 | 0.025766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-121_0_4_line_23 |  | 21 | 23 | 0.015399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-121_0_4_line_24 |  | 22 | 24 | 0.030755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-121_0_4_line_25 |  | 23 | 25 | 0.020872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-121_0_4_line_26 |  | 23 | 26 | 0.017155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-121_0_4_line_27 |  | 24 | 27 | 0.025376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-121_0_4_line_28 |  | 24 | 28 | 0.016765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-121_0_4_line_29 |  | 27 | 41 | 0.012811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-121_0_4_line_30 |  | 28 | 50 | 0.032494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-121_0_4_line_31 |  | 28 | 47 | 0.006371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-121_0_4_line_32 |  | 29 | 30 | 0.017516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-121_0_4_line_33 |  | 30 | 40 | 0.0016258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-121_0_4_line_34 |  | 31 | 32 | 0.014686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1630-121_0_4_line_35 |  | 32 | 33 | 0.016919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-121_0_4_line_36 |  | 33 | 34 | 0.032472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-121_0_4_line_37 |  | 34 | 35 | 0.040176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-121_0_4_line_38 |  | 34 | 36 | 0.045441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-121_0_4_line_39 |  | 35 | 38 | 0.051832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-121_0_4_line_40 |  | 35 | 43 | 0.067803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-121_0_4_line_41 |  | 36 | 42 | 0.014789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-121_0_4_line_42 |  | 37 | 38 | 0.045676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-121_0_4_line_43 |  | 39 | 40 | 0.023535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-121_0_4_line_44 |  | 39 | 41 | 0.020255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1630-121_0_4_line_45 |  | 44 | 45 | 0.0049451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1630-121_0_4_line_46 |  | 45 | 46 | 0.01618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1630-121_0_4_line_47 |  | 46 | 49 | 0.0057873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1630-121_0_4_line_48 |  | 47 | 48 | 0.019153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1630-121_0_4_line_49 |  | 48 | 51 | 0.0069587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1630-121_0_4_line_50 |  | 49 | 51 | 0.014392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-121_0_4_trafo_5 | 0.63 MVA 20/0.4 kV | 52 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2722596.356 | 1221084.0783 | 2722579.468 | 1221071.9231
1 | 2722596.356 | 1221084.0783 | 2722597.2039 | 1221084.6886
2 | 2722579.468 | 1221071.9231 | 2722577.1622 | 1221070.2634
3 | 2722607.7305 | 1221092.2652 | 2722597.2039 | 1221084.6886
4 | 2722566.848 | 1221056.0175 | 2722568.2516 | 1221060.272 | 2722570.3985 | 1221063.9968 | 2722573.1221 | 1221067.3555 | 2722577.1622 | 1221070.2634
5 | 2722587.9214 | 1221116.3097 | 2722598.6084 | 1221103.3306 | 2722607.7305 | 1221092.2652
6 | 2722607.7305 | 1221092.2652 | 2722620.7963 | 1221076.402
7 | 2722564.2131 | 1221048.0305 | 2722566.848 | 1221056.0175
8 | 2722587.9214 | 1221116.3097 | 2722584.4099 | 1221120.5725
9 | 2722628.3424 | 1221067.2404 | 2722620.7963 | 1221076.402
10 | 2722561.459 | 1221027.057 | 2722560.4012 | 1221029.8532 | 2722560.0226 | 1221032.3919 | 2722560.3657 | 1221036.3687 | 2722564.2131 | 1221048.0305
11 | 2722568.2105 | 1221009.2088 | 2722561.459 | 1221027.057
12 | 2722568.2105 | 1221009.2088 | 2722575.8948 | 1221013.4258 | 2722581.2781 | 1221016.6252
13 | 2722568.2105 | 1221009.2088 | 2722562.355 | 1221007.7462
14 | 2722581.2781 | 1221016.6252 | 2722598.0826 | 1221026.6123
15 | 2722562.355 | 1221007.7462 | 2722557.9279 | 1221006.6404
16 | 2722611.1317 | 1221034.3676 | 2722598.0826 | 1221026.6123
17 | 2722547.4151 | 1221004.5448 | 2722557.0513 | 1221006.4215 | 2722557.9279 | 1221006.6404
18 | 2722611.1317 | 1221034.3676 | 2722623.9219 | 1221041.9702 | 2722625.9578 | 1221042.9553
19 | 2722465.6442 | 1220985.2691 | 2722470.3153 | 1220988.401 | 2722475.5277 | 1220990.3096 | 2722482.0309 | 1220991.8112 | 2722547.4151 | 1221004.5448
20 | 2722465.6442 | 1220985.2691 | 2722435.456 | 1221013.6874
21 | 2722418.6844 | 1221029.4829 | 2722430.7108 | 1221018.1545 | 2722435.456 | 1221013.6874
22 | 2722465.6442 | 1220985.2691 | 2722476.4577 | 1220974.2495 | 2722483.1459 | 1220966.3813
23 | 2722418.6844 | 1221029.4829 | 2722422.8851 | 1221033.717 | 2722431.7971 | 1221036.9138
24 | 2722502.4667 | 1220942.4817 | 2722497.1922 | 1220949.8568 | 2722483.1459 | 1220966.3813
25 | 2722431.7971 | 1221036.9138 | 2722445.8988 | 1221052.338
26 | 2722444.37 | 1221025.2075 | 2722431.7971 | 1221036.9138
27 | 2722502.4667 | 1220942.4817 | 2722481.4041 | 1220928.2374
28 | 2722512.2339 | 1220928.8386 | 2722502.4667 | 1220942.4817
29 | 2722481.4041 | 1220928.2374 | 2722477.3611 | 1220935.8824 | 2722474.7316 | 1220939.1092
30 | 2722512.2339 | 1220928.8386 | 2722518.9748 | 1220933.5476 | 2722527.6828 | 1220941.8666 | 2722530.7359 | 1220946.1772 | 2722533.6177 | 1220952.5415
31 | 2722516.1025 | 1220923.7697 | 2722512.2339 | 1220928.8386
32 | 2722444.2536 | 1220972.5861 | 2722437.9862 | 1220978.0615 | 2722430.0214 | 1220982.6535
33 | 2722444.2536 | 1220972.5861 | 2722445.4787 | 1220971.5173
34 | 2722626.6518 | 1220998.9815 | 2722614.8459 | 1220990.2458
35 | 2722626.6518 | 1220998.9815 | 2722630.9765 | 1221003.0849 | 2722639.8465 | 1221009.5185
36 | 2722666.562 | 1221027.7259 | 2722659.0169 | 1221024.1233 | 2722651.8679 | 1221018.2381 | 2722639.8465 | 1221009.5185
37 | 2722666.562 | 1221027.7259 | 2722672.5534 | 1221037.8573 | 2722680.3267 | 1221034.07 | 2722690.629 | 1221029.0894 | 2722698.118 | 1221025.4741
38 | 2722640.3364 | 1221046.0447 | 2722645.3825 | 1221046.0708 | 2722650.6291 | 1221045.5785 | 2722654.4991 | 1221044.8576 | 2722657.1003 | 1221044.2107 | 2722659.6362 | 1221043.4178 | 2722662.1504 | 1221042.5689 | 2722664.5907 | 1221041.6296 | 2722666.9804 | 1221040.5668 | 2722672.5534 | 1221037.8573 | 2722666.562 | 1221027.7259
39 | 2722744.8851 | 1221002.8533 | 2722739.5115 | 1221005.4557 | 2722698.118 | 1221025.4741
40 | 2722698.118 | 1221025.4741 | 2722693.3801 | 1221017.8594 | 2722674.8768 | 1220988.0994 | 2722671.6301 | 1220982.8729 | 2722671.2013 | 1220981.2183 | 2722671.3159 | 1220979.3414 | 2722671.7673 | 1220978.0608 | 2722672.6676 | 1220976.7227 | 2722681.7871 | 1220970.4334
41 | 2722640.3364 | 1221046.0447 | 2722635.1265 | 1221045.4925 | 2722631.3173 | 1221044.7357 | 2722627.3784 | 1221043.6426 | 2722625.9578 | 1221042.9553
42 | 2722744.8851 | 1221002.8533 | 2722739.4849 | 1220991.2885 | 2722735.3098 | 1220983.9856 | 2722730.0314 | 1220976.0818 | 2722721.0825 | 1220965.111 | 2722720.5632 | 1220964.453
43 | 2722461.9361 | 1220954.8107 | 2722455.3121 | 1220962.9392 | 2722445.4787 | 1220971.5173
44 | 2722474.7316 | 1220939.1092 | 2722461.9361 | 1220954.8107
45 | 2722562.9605 | 1220920.3199 | 2722562.2236 | 1220915.4301
46 | 2722562.9605 | 1220920.3199 | 2722563.6282 | 1220924.7483 | 2722552.6398 | 1220928.7698
47 | 2722547.698 | 1220931.7816 | 2722547.698 | 1220931.7816 | 2722552.6398 | 1220928.7698
48 | 2722516.1025 | 1220923.7697 | 2722531.3044 | 1220935.4201
49 | 2722536.8277 | 1220939.653 | 2722531.3044 | 1220935.4201
50 | 2722536.8277 | 1220939.653 | 2722545.1831 | 1220936.7115 | 2722547.698 | 1220931.7816

## bus_geodata
| x | y | coords
0 | 2722596.356 | 1221084.0783
1 | 2722579.468 | 1221071.9231
2 | 2722597.2039 | 1221084.6886
3 | 2722577.1622 | 1221070.2634
4 | 2722607.7305 | 1221092.2652
5 | 2722566.848 | 1221056.0175
6 | 2722587.9214 | 1221116.3097
7 | 2722620.7963 | 1221076.402
8 | 2722564.2131 | 1221048.0305
9 | 2722584.4099 | 1221120.5725
10 | 2722628.3424 | 1221067.2404
11 | 2722561.459 | 1221027.057
12 | 2722568.2105 | 1221009.2088
13 | 2722581.2781 | 1221016.6252
14 | 2722562.355 | 1221007.7462
15 | 2722598.0826 | 1221026.6123
16 | 2722557.9279 | 1221006.6404
17 | 2722611.1317 | 1221034.3676
18 | 2722547.4151 | 1221004.5448
19 | 2722435.456 | 1221013.6874
20 | 2722465.6442 | 1220985.2691
21 | 2722418.6844 | 1221029.4829
22 | 2722483.1459 | 1220966.3813
23 | 2722431.7971 | 1221036.9138
24 | 2722502.4667 | 1220942.4817
25 | 2722445.8988 | 1221052.338
26 | 2722444.37 | 1221025.2075
27 | 2722481.4041 | 1220928.2374
28 | 2722512.2339 | 1220928.8386
29 | 2722430.0214 | 1220982.6535
30 | 2722444.2536 | 1220972.5861
31 | 2722614.8459 | 1220990.2458
32 | 2722626.6518 | 1220998.9815
33 | 2722639.8465 | 1221009.5185
34 | 2722666.562 | 1221027.7259
35 | 2722698.118 | 1221025.4741
36 | 2722640.3364 | 1221046.0447
37 | 2722720.5632 | 1220964.453
38 | 2722744.8851 | 1221002.8533
39 | 2722461.9361 | 1220954.8107
40 | 2722445.4787 | 1220971.5173
41 | 2722474.7316 | 1220939.1092
42 | 2722625.9578 | 1221042.9553
43 | 2722681.7871 | 1220970.4334
44 | 2722562.2236 | 1220915.4301
45 | 2722562.9605 | 1220920.3199
46 | 2722552.6398 | 1220928.7698
47 | 2722516.1025 | 1220923.7697
48 | 2722531.3044 | 1220935.4201
49 | 2722547.698 | 1220931.7816
50 | 2722533.6177 | 1220952.5415
51 | 2722536.8277 | 1220939.653
52 | 2722568.2105 | 1221009.2088

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99353 | -0.12406 | 0.013771 | 0.0034513
1 | 0.99603 | -0.076073 | 0.013623 | 0.0034143
2 | 0.99342 | -0.12622 | 0.0060787 | 0.0015235
3 | 0.99621 | -0.072466 | 0.015877 | 0.0039791
4 | 0.9921 | -0.15169 | 0 | 0
5 | 0.99754 | -0.047029 | 0.010409 | 0.0026087
6 | 0.99183 | -0.15693 | 0 | 0
7 | 0.99019 | -0.18873 | 0.090053 | 0.022569
8 | 0.9982 | -0.034454 | 0.0099555 | 0.0024951
9 | 0.99178 | -0.15786 | 0.0094939 | 0.0023794
10 | 0.99006 | -0.19117 | 0.011527 | 0.002889
11 | 1 | 0 | -0.42719 | -0.10816
12 | 0.99789 | -0.040141 | 0 | 0
13 | 0.99631 | -0.070342 | 0.022889 | 0.0057366
14 | 0.99719 | -0.053485 | 0.0057048 | 0.0014298
15 | 0.99467 | -0.10189 | 0.015756 | 0.0039489
16 | 0.99668 | -0.063129 | 0.004138 | 0.0010371
17 | 0.99361 | -0.12223 | 0 | 0
18 | 0.99553 | -0.085048 | 0.0092311 | 0.0023135
19 | 0.98481 | -0.2915 | 0.0036536 | 0.00091567
20 | 0.98718 | -0.24556 | 0 | 0
21 | 0.98357 | -0.3156 | 0 | 0
22 | 0.9861 | -0.26648 | 0.001875 | 0.00046992
23 | 0.98275 | -0.33175 | 0 | 0
24 | 0.98487 | -0.29047 | 0 | 0
25 | 0.98215 | -0.34347 | 0.031102 | 0.007795
26 | 0.98232 | -0.34012 | 0.027045 | 0.0067782
27 | 0.98447 | -0.29821 | 0 | 0
28 | 0.98446 | -0.29846 | 0 | 0
29 | 0.98381 | -0.31121 | 0.002454 | 0.00061503
30 | 0.98385 | -0.31044 | 0 | 0
31 | 0.98853 | -0.22058 | 0.0073071 | 0.0018313
32 | 0.98863 | -0.21867 | 0 | 0
33 | 0.98874 | -0.21646 | 0.019311 | 0.0048399
34 | 0.98953 | -0.20107 | 0 | 0
35 | 0.98859 | -0.21938 | 0 | 0
36 | 0.99171 | -0.15893 | 0 | 0
37 | 0.98726 | -0.24525 | 0.014854 | 0.0037228
38 | 0.98788 | -0.23313 | 0 | 0
39 | 0.98402 | -0.30712 | 0.0060306 | 0.0015114
40 | 0.98385 | -0.31037 | 0.0052157 | 0.0013072
41 | 0.98427 | -0.30212 | 0.0032683 | 0.00081911
42 | 0.99242 | -0.14525 | 0.023778 | 0.0059593
43 | 0.98792 | -0.23237 | 0.01073 | 0.0026892
44 | 0.98349 | -0.31738 | 0.006015 | 0.0015075
45 | 0.98352 | -0.31685 | 0 | 0
46 | 0.98361 | -0.31509 | 0.004681 | 0.0011732
47 | 0.98434 | -0.30086 | 0 | 0
48 | 0.98397 | -0.30807 | 0.0055928 | 0.0014017
49 | 0.98366 | -0.31398 | 0.0046536 | 0.0011663
50 | 0.98429 | -0.3017 | 0.0055522 | 0.0013915
51 | 0.98387 | -0.31 | 0 | 0
52 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13126 | -0.033024 | 0.13156 | 0.033216 | 0.00030167 | 0.0001928 | 0.19663 | 0.19663 | 0.19663 | 0.99353 | -0.12406 | 0.99603 | -0.076073 | 54.0183
1 | 0.11748 | 0.029572 | -0.11747 | -0.029564 | 1.2135e-05 | 7.7527e-06 | 0.176 | 0.176 | 0.176 | 0.99353 | -0.12406 | 0.99342 | -0.12622 | 48.3521
2 | -0.14518 | -0.036631 | 0.14521 | 0.036647 | 2.5079e-05 | 1.5977e-05 | 0.21698 | 0.21698 | 0.21698 | 0.99603 | -0.076073 | 0.99621 | -0.072466 | 29.8048
3 | 0.11139 | 0.028041 | -0.11126 | -0.027954 | 0.00013548 | 8.6536e-05 | 0.1669 | 0.1669 | 0.1669 | 0.99342 | -0.12622 | 0.9921 | -0.15169 | 45.8507
4 | -0.16108 | -0.040626 | 0.16128 | 0.040751 | 0.00019641 | 0.00012523 | 0.24069 | 0.24069 | 0.24069 | 0.99621 | -0.072466 | 0.99754 | -0.047029 | 33.0623
5 | 0.0094967 | 0.0023807 | -0.0094943 | -0.0023796 | 2.3703e-06 | 1.1148e-06 | 0.014244 | 0.014244 | 0.014244 | 0.9921 | -0.15169 | 0.99183 | -0.15693 | 3.9132
6 | 0.10176 | 0.025574 | -0.10158 | -0.025459 | 0.00017959 | 0.00011467 | 0.15265 | 0.15265 | 0.15265 | 0.9921 | -0.15169 | 0.99019 | -0.18873 | 41.9376
7 | -0.17169 | -0.04336 | 0.17179 | 0.043426 | 0.00010352 | 6.6036e-05 | 0.25622 | 0.25622 | 0.25622 | 0.99754 | -0.047029 | 0.9982 | -0.034454 | 35.195
8 | 0.0094943 | 0.0023796 | -0.0094939 | -0.0023794 | 4.2022e-07 | 1.9767e-07 | 0.014244 | 0.014244 | 0.014244 | 0.99183 | -0.15693 | 0.99178 | -0.15786 | 3.9132
9 | 0.011529 | 0.0028897 | -0.011527 | -0.002889 | 1.3359e-06 | 7.0235e-07 | 0.017325 | 0.017325 | 0.017325 | 0.99019 | -0.18873 | 0.99006 | -0.19117 | 4.7595
10 | -0.18175 | -0.045921 | 0.18205 | 0.046113 | 0.00030071 | 0.00019188 | 0.27106 | 0.27106 | 0.27106 | 0.9982 | -0.034454 | 1 | 0 | 37.2336
11 | 0.24349 | 0.062044 | -0.24302 | -0.061744 | 0.00047063 | 0.0003007 | 0.36268 | 0.36268 | 0.36268 | 1 | 0 | 0.99789 | -0.040141 | 49.8183
12 | 0.1153 | 0.029153 | -0.11513 | -0.029046 | 0.00016675 | 0.00010653 | 0.17202 | 0.17202 | 0.17202 | 0.99789 | -0.040141 | 0.99631 | -0.070342 | 47.2579
13 | 0.12772 | 0.032591 | -0.12764 | -0.032538 | 8.2272e-05 | 5.2575e-05 | 0.19066 | 0.19066 | 0.19066 | 0.99789 | -0.040141 | 0.99719 | -0.053485 | 52.3789
14 | 0.092242 | 0.02331 | -0.092103 | -0.023221 | 0.00013927 | 8.8877e-05 | 0.13783 | 0.13783 | 0.13783 | 0.99631 | -0.070342 | 0.99467 | -0.10189 | 37.8663
15 | 0.12193 | 0.031108 | -0.12188 | -0.031072 | 5.6771e-05 | 3.6274e-05 | 0.18215 | 0.18215 | 0.18215 | 0.99719 | -0.053485 | 0.99668 | -0.063129 | 50.0403
16 | 0.076346 | 0.019272 | -0.076272 | -0.019225 | 7.4319e-05 | 4.7367e-05 | 0.11426 | 0.11426 | 0.11426 | 0.99467 | -0.10189 | 0.99361 | -0.12223 | 31.3907
17 | 0.11774 | 0.030035 | -0.11761 | -0.029956 | 0.00012449 | 7.9534e-05 | 0.17597 | 0.17597 | 0.17597 | 0.99668 | -0.063129 | 0.99553 | -0.085048 | 48.3431
18 | 0.076272 | 0.019225 | -0.076188 | -0.019171 | 8.3921e-05 | 5.3487e-05 | 0.11426 | 0.11426 | 0.11426 | 0.99361 | -0.12223 | 0.99242 | -0.14525 | 31.3907
19 | 0.10838 | 0.027642 | -0.10755 | -0.02711 | 0.00083299 | 0.00053202 | 0.16217 | 0.16217 | 0.16217 | 0.99553 | -0.085048 | 0.98718 | -0.24556 | 44.5526
20 | -0.061941 | -0.015577 | 0.062077 | 0.015664 | 0.00013624 | 8.6665e-05 | 0.09361 | 0.09361 | 0.09361 | 0.98481 | -0.2915 | 0.98718 | -0.24556 | 25.717
21 | 0.058288 | 0.014662 | -0.058221 | -0.014619 | 6.7041e-05 | 4.2613e-05 | 0.08809 | 0.08809 | 0.08809 | 0.98481 | -0.2915 | 0.98357 | -0.3156 | 24.2005
22 | 0.045473 | 0.011446 | -0.045428 | -0.011417 | 4.5419e-05 | 2.8739e-05 | 0.068562 | 0.068562 | 0.068562 | 0.98718 | -0.24556 | 0.9861 | -0.26648 | 18.8357
23 | 0.058221 | 0.014619 | -0.058176 | -0.014591 | 4.481e-05 | 2.8483e-05 | 0.08809 | 0.08809 | 0.08809 | 0.98357 | -0.3156 | 0.98275 | -0.33175 | 24.2005
24 | 0.043553 | 0.010947 | -0.043503 | -0.010916 | 4.9832e-05 | 3.15e-05 | 0.065732 | 0.065733 | 0.065733 | 0.9861 | -0.26648 | 0.98487 | -0.29047 | 18.0584
25 | 0.03112 | 0.0078058 | -0.031102 | -0.007795 | 1.738e-05 | 1.0859e-05 | 0.047122 | 0.047122 | 0.047122 | 0.98275 | -0.33175 | 0.98215 | -0.34347 | 12.9456
26 | 0.027056 | 0.0067848 | -0.027045 | -0.0067782 | 1.0797e-05 | 6.6929e-06 | 0.040968 | 0.040968 | 0.040968 | 0.98275 | -0.33175 | 0.98232 | -0.34012 | 11.2549
27 | 0.016983 | 0.0042604 | -0.016976 | -0.0042567 | 6.2657e-06 | 3.6873e-06 | 0.02566 | 0.02566 | 0.02566 | 0.98487 | -0.29047 | 0.98447 | -0.29821 | 7.0495
28 | 0.026521 | 0.0066553 | -0.026511 | -0.0066491 | 1.0096e-05 | 6.2479e-06 | 0.040073 | 0.040073 | 0.040073 | 0.98487 | -0.29047 | 0.98446 | -0.29846 | 11.009
29 | 0.016976 | 0.0042567 | -0.016973 | -0.0042548 | 3.1632e-06 | 1.8616e-06 | 0.02566 | 0.02566 | 0.02566 | 0.98447 | -0.29821 | 0.98427 | -0.30212 | 7.0495
30 | 0.005553 | 0.0013916 | -0.0055522 | -0.0013915 | 8.5845e-07 | 1.3633e-07 | 0.0083934 | 0.0083935 | 0.0083935 | 0.98446 | -0.29846 | 0.98429 | -0.3017 | 2.3059
31 | 0.020958 | 0.0052574 | -0.020955 | -0.005256 | 2.3977e-06 | 1.4535e-06 | 0.031679 | 0.031679 | 0.031679 | 0.98446 | -0.29846 | 0.98434 | -0.30086 | 8.7031
32 | -0.002454 | -0.00061503 | 0.0024541 | 0.00061487 | 9.0491e-08 | -1.6451e-07 | 0.0037117 | 0.0037116 | 0.0037117 | 0.98381 | -0.31121 | 0.98385 | -0.31044 | 1.0197
33 | -0.0024541 | -0.00061487 | 0.0024541 | 0.00061485 | 8.3987e-09 | -1.527e-08 | 0.0037116 | 0.0037116 | 0.0037116 | 0.98385 | -0.31044 | 0.98385 | -0.31037 | 1.0197
34 | -0.0073071 | -0.0018313 | 0.0073077 | 0.0018316 | 6.663e-07 | 2.3813e-07 | 0.010999 | 0.010999 | 0.010999 | 0.98853 | -0.22058 | 0.98863 | -0.21867 | 3.0218
35 | -0.0073077 | -0.0018316 | 0.0073085 | 0.0018318 | 7.6758e-07 | 2.7428e-07 | 0.010999 | 0.010999 | 0.010999 | 0.98863 | -0.21867 | 0.98874 | -0.21646 | 3.0217
36 | -0.02662 | -0.0066717 | 0.026639 | 0.0066838 | 1.9543e-05 | 1.2091e-05 | 0.040062 | 0.040062 | 0.040062 | 0.98874 | -0.21646 | 0.98953 | -0.20107 | 11.006
37 | 0.025631 | 0.0064396 | -0.025609 | -0.0064258 | 2.2389e-05 | 1.3813e-05 | 0.038549 | 0.038549 | 0.038549 | 0.98953 | -0.20107 | 0.98859 | -0.21938 | 10.5904
38 | -0.052271 | -0.013123 | 0.052376 | 0.01319 | 0.0001053 | 6.6808e-05 | 0.078611 | 0.07861 | 0.078611 | 0.98953 | -0.20107 | 0.99171 | -0.15893 | 21.5963
39 | 0.014872 | 0.0037333 | -0.014863 | -0.0037277 | 9.7423e-06 | 5.5709e-06 | 0.022388 | 0.022388 | 0.022388 | 0.98859 | -0.21938 | 0.98788 | -0.23313 | 6.1506
40 | 0.010737 | 0.0026926 | -0.01073 | -0.0026892 | 6.641e-06 | 3.3815e-06 | 0.016161 | 0.016162 | 0.016162 | 0.98859 | -0.21938 | 0.98792 | -0.23237 | 4.44
41 | -0.052376 | -0.01319 | 0.05241 | 0.013212 | 3.427e-05 | 2.1742e-05 | 0.07861 | 0.07861 | 0.07861 | 0.99171 | -0.15893 | 0.99242 | -0.14525 | 21.5963
42 | -0.014854 | -0.0037228 | 0.014863 | 0.0037277 | 8.5853e-06 | 4.9102e-06 | 0.022388 | 0.022388 | 0.022388 | 0.98726 | -0.24525 | 0.98788 | -0.23313 | 6.1506
43 | 0.007671 | 0.0019225 | -0.0076698 | -0.001922 | 1.1876e-06 | 4.6113e-07 | 0.0116 | 0.0116 | 0.0116 | 0.98402 | -0.30712 | 0.98385 | -0.31037 | 3.1868
44 | -0.013702 | -0.0034339 | 0.013705 | 0.0034357 | 3.2607e-06 | 1.8295e-06 | 0.020719 | 0.020719 | 0.020719 | 0.98402 | -0.30712 | 0.98427 | -0.30212 | 5.6921
45 | -0.006015 | -0.0015075 | 0.0060152 | 0.0015075 | 1.5359e-07 | 3.5542e-08 | 0.0091007 | 0.0091007 | 0.0091007 | 0.98349 | -0.31738 | 0.98352 | -0.31685 | 2.5002
46 | -0.0060152 | -0.0015075 | 0.0060157 | 0.0015077 | 5.0251e-07 | 1.1626e-07 | 0.0091007 | 0.0091006 | 0.0091007 | 0.98352 | -0.31685 | 0.98361 | -0.31509 | 2.5002
47 | -0.010697 | -0.0026808 | 0.010697 | 0.0026811 | 5.6829e-07 | 2.9025e-07 | 0.016182 | 0.016182 | 0.016182 | 0.98361 | -0.31509 | 0.98366 | -0.31398 | 4.4456
48 | 0.020955 | 0.005256 | -0.020948 | -0.0052516 | 7.208e-06 | 4.3698e-06 | 0.031679 | 0.031679 | 0.031679 | 0.98434 | -0.30086 | 0.98397 | -0.30807 | 8.7031
49 | 0.015355 | 0.0038499 | -0.015354 | -0.0038491 | 1.4071e-06 | 8.1219e-07 | 0.023221 | 0.023222 | 0.023222 | 0.98397 | -0.30807 | 0.98387 | -0.31 | 6.3795
50 | -0.015351 | -0.0038474 | 0.015354 | 0.0038491 | 2.9104e-06 | 1.6799e-06 | 0.023222 | 0.023222 | 0.023222 | 0.98366 | -0.31398 | 0.98387 | -0.31 | 6.3796

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44588 | 0.11284

## res_load
| p_mw | q_mvar
0 | 0.013771 | 0.0034513
1 | 0.013623 | 0.0034143
2 | 0.0060787 | 0.0015235
3 | 0.015877 | 0.0039791
4 | 0.010409 | 0.0026087
5 | 0.090053 | 0.022569
6 | 0.0099555 | 0.0024951
7 | 0.0094939 | 0.0023794
8 | 0.011527 | 0.002889
9 | 0.018697 | 0.0046858
10 | 0.022889 | 0.0057366
11 | 0.0057048 | 0.0014298
12 | 0.015756 | 0.0039489
13 | 0.004138 | 0.0010371
14 | 0.0092311 | 0.0023135
15 | 0.0036536 | 0.00091567
16 | 0.001875 | 0.00046992
17 | 0.031102 | 0.007795
18 | 0.027045 | 0.0067782
19 | 0.002454 | 0.00061503
20 | 0.0073071 | 0.0018313
21 | 0.019311 | 0.0048399
22 | 0.014854 | 0.0037228
23 | 0.0060306 | 0.0015114
24 | 0.0052157 | 0.0013072
25 | 0.0032683 | 0.00081911
26 | 0.023778 | 0.0059593
27 | 0.01073 | 0.0026892
28 | 0.006015 | 0.0015075
29 | 0.004681 | 0.0011732
30 | 0.0055928 | 0.0014017
31 | 0.0046536 | 0.0011663
32 | 0.0055522 | 0.0013915

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1