## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-131_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-131_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-131_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-131_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-131_0_2_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_1630-131_0_2_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_1630-131_0_2_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_1630-131_0_2_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_1630-131_0_2_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_1630-131_0_2_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1630-131_0_2_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1630-131_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1630-131_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1630-131_0_2_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_1630-131_0_2_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_1630-131_0_2_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1630-131_0_2_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1630-131_0_2_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1630-131_0_2_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1630-131_0_2_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1630-131_0_2_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1630-131_0_2_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1630-131_0_2_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1630-131_0_2_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1630-131_0_2_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1630-131_0_2_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1630-131_0_2_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1630-131_0_2_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1630-131_0_2_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1630-131_0_2_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1630-131_0_2_node_25 | 0.4 | n |  | TRUE
31 | bus_MV_0_node_20 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-131_0_2_load_0 | 0 | 0.0010617 | 0.00026609 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-131_0_2_load_2 | 2 | 0.0013298 | 0.00033328 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-131_0_2_load_3 | 3 | 0.001077 | 0.00026991 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-131_0_2_load_29 | 4 | 0.0010993 | 0.00027552 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-131_0_2_load_30 | 5 | 0.0011762 | 0.00029478 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-131_0_2_load_28 | 8 | 0.0009776 | 0.00024501 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-131_0_2_load_4 | 9 | 0.0079284 | 0.001987 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-131_0_2_load_5 | 10 | 0.0096185 | 0.0024106 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-131_0_2_load_7 | 12 | 0.0082101 | 0.0020577 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-131_0_2_load_20 | 13 | 0.0025153 | 0.00063038 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-131_0_2_load_21 | 14 | 0.0032721 | 0.00082006 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-131_0_2_load_8 | 15 | 0.0077375 | 0.0019392 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-131_0_2_load_10 | 17 | 0.006706 | 0.0016807 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-131_0_2_load_11 | 18 | 0.0022623 | 0.00056698 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-131_0_2_load_12 | 19 | 0.0025112 | 0.00062936 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-131_0_2_load_19 | 23 | 0.0029832 | 0.00074765 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-131_0_2_load_16 | 24 | 0.0011152 | 0.00027948 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-131_0_2_load_23 | 25 | 0.0022131 | 0.00055465 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-131_0_2_load_26 | 26 | 0.0027149 | 0.00068042 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-131_0_2_load_17 | 27 | 0.001466 | 0.00036742 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-131_0_2_load_22 | 28 | 0.0021934 | 0.00054971 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-131_0_2_load_24 | 29 | 0.0012528 | 0.00031399 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-131_0_2_load_25 | 30 | 0.0012051 | 0.00030203 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-131_0_2_line_0 |  | 0 | 1 | 0.010644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-131_0_2_line_1 |  | 1 | 2 | 0.056571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-131_0_2_line_2 |  | 1 | 3 | 0.025673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-131_0_2_line_3 |  | 3 | 7 | 0.04626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-131_0_2_line_4 |  | 3 | 4 | 0.075536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-131_0_2_line_5 |  | 4 | 5 | 0.045665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-131_0_2_line_6 |  | 4 | 6 | 0.02906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-131_0_2_line_7 |  | 5 | 30 | 0.035736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-131_0_2_line_8 |  | 6 | 27 | 0.0039499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-131_0_2_line_9 |  | 7 | 8 | 0.009657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-131_0_2_line_10 |  | 9 | 10 | 0.012538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-131_0_2_line_11 |  | 9 | 11 | 0.021624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-131_0_2_line_12 |  | 10 | 12 | 0.0015069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-131_0_2_line_13 |  | 11 | 13 | 0.24054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-131_0_2_line_14 |  | 12 | 15 | 0.01049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-131_0_2_line_15 |  | 13 | 14 | 0.0075558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-131_0_2_line_16 |  | 14 | 28 | 0.029507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-131_0_2_line_17 |  | 15 | 16 | 0.037632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-131_0_2_line_18 |  | 16 | 17 | 0.019004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-131_0_2_line_19 |  | 18 | 19 | 0.002373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-131_0_2_line_20 |  | 18 | 20 | 0.0019238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-131_0_2_line_21 |  | 19 | 21 | 0.024264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-131_0_2_line_22 |  | 20 | 22 | 0.10543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-131_0_2_line_23 |  | 21 | 23 | 0.018359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-131_0_2_line_24 |  | 21 | 24 | 0.12092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-131_0_2_line_25 |  | 22 | 25 | 0.0062574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-131_0_2_line_26 |  | 23 | 26 | 0.02154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-131_0_2_line_27 |  | 24 | 27 | 0.022883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-131_0_2_line_28 |  | 26 | 28 | 0.006527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-131_0_2_line_29 |  | 29 | 30 | 0.027136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-131_0_2_trafo_20 | 0.63 MVA 20/0.4 kV | 31 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2716902.7121 | 1216854.7402 | 2716908.1645 | 1216855.9036 | 2716913.2259 | 1216856.1799
1 | 2716902.7121 | 1216854.7402 | 2716911.3819 | 1216858.7355 | 2716919.1803 | 1216861.0903 | 2716929.0192 | 1216863.5629 | 2716933.6337 | 1216866.022 | 2716936.4156 | 1216870.1464 | 2716938.5225 | 1216875.0025 | 2716938.9634 | 1216877.691 | 2716938.9971 | 1216880.2269 | 2716937.4542 | 1216883.7771 | 2716934.853 | 1216887.073
2 | 2716902.7121 | 1216854.7402 | 2716893.4713 | 1216850.8116 | 2716888.0394 | 1216849.7598 | 2716878.0397 | 1216848.3471
3 | 2716843.2256 | 1216823.1276 | 2716843.0366 | 1216827.7274 | 2716845.4313 | 1216831.466 | 2716851.1678 | 1216835.9597 | 2716858.9099 | 1216841.5713 | 2716874.9684 | 1216847.9132 | 2716878.0397 | 1216848.3471
4 | 2716863.6974 | 1216922.5085 | 2716878.0397 | 1216848.3471
5 | 2716863.6974 | 1216922.5085 | 2716863.7767 | 1216922.5057 | 2716869.2997 | 1216924.3265 | 2716873.7264 | 1216927.8382 | 2716877.1148 | 1216934.3429 | 2716879.0965 | 1216941.7096 | 2716878.7543 | 1216946.7622 | 2716874.9917 | 1216955.0725 | 2716871.4082 | 1216958.516 | 2716871.4082 | 1216958.516
6 | 2716835.3769 | 1216918.1679 | 2716839.4089 | 1216920.1262 | 2716849.311 | 1216922.4665 | 2716854.8629 | 1216922.8201 | 2716863.6974 | 1216922.5085
7 | 2716842.1695 | 1216977.9797 | 2716844.2058 | 1216974.4391 | 2716850.5175 | 1216969.3479 | 2716855.1964 | 1216966.582 | 2716871.4082 | 1216958.516
8 | 2716835.3769 | 1216918.1679 | 2716831.6684 | 1216919.5273
9 | 2716843.2256 | 1216823.1276 | 2716852.0703 | 1216819.2509
10 | 2716410.3752 | 1217055.8649 | 2716406.4201 | 1217060.6711 | 2716403.6467 | 1217063.8638 | 2716401.8397 | 1217064.9038
11 | 2716424.4153 | 1217039.7957 | 2716422.6198 | 1217043.8526 | 2716419.6259 | 1217046.674 | 2716416.2179 | 1217049.6986 | 2716413.1563 | 1217052.4854 | 2716410.3752 | 1217055.8649
12 | 2716400.5337 | 1217065.6554 | 2716401.8397 | 1217064.9038
13 | 2716628.0458 | 1216911.7538 | 2716424.4153 | 1217039.7957
14 | 2716400.5337 | 1217065.6554 | 2716398.3398 | 1217066.918 | 2716391.9972 | 1217069.3404 | 2716390.8567 | 1217069.599
15 | 2716628.0458 | 1216911.7538 | 2716633.2571 | 1216907.679 | 2716634.0262 | 1216907.1377
16 | 2716658.5478 | 1216890.7588 | 2716653.5906 | 1216894.2668 | 2716645.1229 | 1216899.3271 | 2716634.0262 | 1216907.1377
17 | 2716353.6339 | 1217074.384 | 2716356.146 | 1217073.677 | 2716359.7749 | 1217073.3365 | 2716365.4915 | 1217073.0256 | 2716374.3036 | 1217072.4639 | 2716382.4247 | 1217071.5107 | 2716390.8567 | 1217069.599
18 | 2716353.6339 | 1217074.384 | 2716348.8701 | 1217076.8484 | 2716337.647 | 1217084.6019
19 | 2716700.7674 | 1216906.5107 | 2716700.3609 | 1216908.8487
20 | 2716700.0314 | 1216910.744 | 2716700.3609 | 1216908.8487
21 | 2716701.4168 | 1216882.2829 | 2716700.4622 | 1216896.8975 | 2716700.7674 | 1216906.5107
22 | 2716676.53 | 1217006.3895 | 2716671.8772 | 1217000.0715 | 2716670.2605 | 1216994.9915 | 2716670.593 | 1216990.4279 | 2716675.1321 | 1216979.6753 | 2716675.6876 | 1216976.5171 | 2716675.5001 | 1216969.4192 | 2716674.6081 | 1216963.008 | 2716675.2026 | 1216957.471 | 2716678.9215 | 1216952.1509 | 2716685.8783 | 1216944.359 | 2716689.838 | 1216938.7656 | 2716696.6305 | 1216917.2712 | 2716700.0314 | 1216910.744
23 | 2716701.4168 | 1216882.2829 | 2716689.8957 | 1216879.2328 | 2716683.7174 | 1216879.4565 | 2716683.459 | 1216879.4629
24 | 2716701.4168 | 1216882.2829 | 2716703.2084 | 1216886.1876 | 2716704.977 | 1216887.779 | 2716707.0946 | 1216888.2208 | 2716719.0729 | 1216885.7646 | 2716724.787 | 1216886.3659 | 2716732.177 | 1216888.6345 | 2716736.0554 | 1216891.0679 | 2716739.4455 | 1216897.4947 | 2716741.6809 | 1216900.0627 | 2716744.2599 | 1216902.1481 | 2716754.8833 | 1216906.4372 | 2716789.9901 | 1216916.8996 | 2716809.3048 | 1216920.8958
25 | 2716676.53 | 1217006.3895 | 2716682.2129 | 1217004.3103 | 2716682.4168 | 1217004.2808
26 | 2716683.459 | 1216879.4629 | 2716677.4873 | 1216879.6124 | 2716669.4002 | 1216883.0789 | 2716663.8757 | 1216886.9884
27 | 2716831.6684 | 1216919.5273 | 2716827.9192 | 1216920.9015 | 2716821.7676 | 1216922.093 | 2716816.5295 | 1216922.3905 | 2716809.3048 | 1216920.8958
28 | 2716663.8757 | 1216886.9884 | 2716658.5478 | 1216890.7588
29 | 2716842.1695 | 1216977.9797 | 2716842.1695 | 1216977.9797 | 2716838.3904 | 1216979.0063 | 2716820.8985 | 1216978.7855 | 2716815.2197 | 1216979.5256

## bus_geodata
| x | y | coords
0 | 2716913.2259 | 1216856.1799
1 | 2716902.7121 | 1216854.7402
2 | 2716934.853 | 1216887.073
3 | 2716878.0398 | 1216848.3471
4 | 2716863.6974 | 1216922.5085
5 | 2716871.4082 | 1216958.516
6 | 2716835.3769 | 1216918.1679
7 | 2716843.2256 | 1216823.1276
8 | 2716852.0703 | 1216819.2509
9 | 2716410.3752 | 1217055.8649
10 | 2716401.8397 | 1217064.9038
11 | 2716424.4153 | 1217039.7957
12 | 2716400.5337 | 1217065.6554
13 | 2716628.0458 | 1216911.7538
14 | 2716634.0262 | 1216907.1377
15 | 2716390.8567 | 1217069.599
16 | 2716353.6339 | 1217074.384
17 | 2716337.647 | 1217084.6019
18 | 2716700.3609 | 1216908.8487
19 | 2716700.7674 | 1216906.5107
20 | 2716700.0314 | 1216910.744
21 | 2716701.4168 | 1216882.2829
22 | 2716676.53 | 1217006.3895
23 | 2716683.459 | 1216879.4629
24 | 2716809.3048 | 1216920.8958
25 | 2716682.4168 | 1217004.2808
26 | 2716663.8757 | 1216886.9884
27 | 2716831.6684 | 1216919.5273
28 | 2716658.5478 | 1216890.7588
29 | 2716815.2197 | 1216979.5256
30 | 2716842.1695 | 1216977.9797
31 | 2716628.0458 | 1216911.7538

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99603 | -0.076402 | 0.0010617 | 0.00026609
1 | 0.99604 | -0.076203 | 0 | 0
2 | 0.99598 | -0.077526 | 0.0013298 | 0.00033328
3 | 0.9961 | -0.075123 | 0.001077 | 0.00026991
4 | 0.99641 | -0.069217 | 0.0010993 | 0.00027552
5 | 0.99625 | -0.072133 | 0.0011762 | 0.00029478
6 | 0.99665 | -0.064529 | 0 | 0
7 | 0.99606 | -0.075919 | 0 | 0
8 | 0.99605 | -0.076084 | 0.0009776 | 0.00024501
9 | 0.99034 | -0.18552 | 0.0079284 | 0.001987
10 | 0.98997 | -0.19271 | 0.0096185 | 0.0024106
11 | 0.99114 | -0.17008 | 0 | 0
12 | 0.98994 | -0.19332 | 0.0082101 | 0.0020577
13 | 1 | 0 | -0.072199 | -0.017837
14 | 0.99979 | -0.0039431 | 0.0032721 | 0.00082006
15 | 0.9898 | -0.19601 | 0.0077375 | 0.0019392
16 | 0.98957 | -0.2005 | 0 | 0
17 | 0.98945 | -0.20277 | 0.006706 | 0.0016807
18 | 0.99803 | -0.037827 | 0.0022623 | 0.00056698
19 | 0.99804 | -0.037641 | 0.0025112 | 0.00062936
20 | 0.99803 | -0.037902 | 0 | 0
21 | 0.9982 | -0.034674 | 0 | 0
22 | 0.99782 | -0.041989 | 0 | 0
23 | 0.99851 | -0.028648 | 0.0029832 | 0.00074765
24 | 0.9969 | -0.059614 | 0.0011152 | 0.00027948
25 | 0.9978 | -0.042232 | 0.0022131 | 0.00055465
26 | 0.99894 | -0.02046 | 0.0027149 | 0.00068042
27 | 0.99668 | -0.063892 | 0.001466 | 0.00036742
28 | 0.99908 | -0.017671 | 0.0021934 | 0.00054971
29 | 0.99614 | -0.074274 | 0.0012528 | 0.00031399
30 | 0.99617 | -0.073677 | 0.0012051 | 0.00030203
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0010617 | -0.00026609 | 0.0010617 | 0.00026596 | 1.0042e-08 | -1.3211e-07 | 0.0015862 | 0.0015861 | 0.0015862 | 0.99603 | -0.076402 | 0.99604 | -0.076203 | 0.43576
1 | 0.0013299 | 0.0003326 | -0.0013298 | -0.00033328 | 8.3728e-08 | -6.8267e-07 | 0.0019865 | 0.0019868 | 0.0019868 | 0.99604 | -0.076203 | 0.99598 | -0.077526 | 0.54582
2 | -0.0023916 | -0.00059856 | 0.0023918 | 0.00059831 | 1.2288e-07 | -2.5553e-07 | 0.0035726 | 0.0035725 | 0.0035726 | 0.99604 | -0.076203 | 0.9961 | -0.075123 | 0.98149
3 | 0.00097764 | 0.00024431 | -0.0009776 | -0.00024489 | 3.6993e-08 | -5.7847e-07 | 0.0014602 | 0.0014604 | 0.0014604 | 0.9961 | -0.075123 | 0.99606 | -0.075919 | 0.40121
4 | -0.0044464 | -0.0011125 | 0.0044476 | 0.0011123 | 1.2494e-06 | -1.8396e-07 | 0.0066415 | 0.0066412 | 0.0066415 | 0.9961 | -0.075123 | 0.99641 | -0.069217 | 1.8246
5 | 0.0036349 | 0.00090985 | -0.0036344 | -0.00091012 | 5.0453e-07 | -2.718e-07 | 0.0054279 | 0.0054281 | 0.0054281 | 0.99641 | -0.069217 | 0.99625 | -0.072133 | 1.4912
6 | -0.0091818 | -0.0022977 | 0.0091839 | 0.0022987 | 2.0486e-06 | 9.3248e-07 | 0.013711 | 0.013711 | 0.013711 | 0.99641 | -0.069217 | 0.99665 | -0.064529 | 3.7667
7 | 0.0024582 | 0.00061534 | -0.002458 | -0.00061569 | 1.8063e-07 | -3.4969e-07 | 0.0036713 | 0.0036715 | 0.0036715 | 0.99625 | -0.072133 | 0.99617 | -0.073677 | 1.0086
8 | -0.0091839 | -0.0022987 | 0.0091842 | 0.0022988 | 2.7844e-07 | 1.2673e-07 | 0.013711 | 0.013711 | 0.013711 | 0.99665 | -0.064529 | 0.99668 | -0.063892 | 3.7667
9 | 0.0009776 | 0.00024489 | -0.0009776 | -0.00024501 | 7.7238e-09 | -1.2075e-07 | 0.0014604 | 0.0014604 | 0.0014604 | 0.99606 | -0.075919 | 0.99605 | -0.076084 | 0.40122
10 | 0.032288 | 0.0080972 | -0.032277 | -0.0080903 | 1.1067e-05 | 6.9215e-06 | 0.048515 | 0.048515 | 0.048515 | 0.99034 | -0.18552 | 0.98997 | -0.19271 | 13.3284
11 | -0.040216 | -0.010084 | 0.040246 | 0.010103 | 2.961e-05 | 1.8672e-05 | 0.060428 | 0.060428 | 0.060428 | 0.99034 | -0.18552 | 0.99114 | -0.17008 | 16.6011
12 | 0.022658 | 0.0056796 | -0.022658 | -0.0056792 | 6.5546e-07 | 4.0012e-07 | 0.034058 | 0.034058 | 0.034058 | 0.98997 | -0.19271 | 0.98994 | -0.19332 | 9.3565
13 | -0.040246 | -0.010103 | 0.040575 | 0.010311 | 0.00032937 | 0.00020767 | 0.060428 | 0.060427 | 0.060428 | 0.99114 | -0.17008 | 1 | 0 | 16.601
14 | 0.014448 | 0.0036216 | -0.014446 | -0.0036205 | 1.8553e-06 | 1.0525e-06 | 0.021717 | 0.021717 | 0.021717 | 0.98994 | -0.19332 | 0.9898 | -0.19601 | 5.9662
15 | 0.029973 | 0.0075268 | -0.029968 | -0.0075233 | 5.6376e-06 | 3.509e-06 | 0.044606 | 0.044606 | 0.044606 | 1 | 0 | 0.99979 | -0.0039431 | 12.2544
16 | 0.026696 | 0.0067032 | -0.026678 | -0.0066924 | 1.7472e-05 | 1.0795e-05 | 0.039736 | 0.039736 | 0.039736 | 0.99979 | -0.0039431 | 0.99908 | -0.017671 | 10.9165
17 | 0.0067082 | 0.0016813 | -0.0067067 | -0.0016809 | 1.4353e-06 | 4.3499e-07 | 0.010085 | 0.010085 | 0.010085 | 0.9898 | -0.19601 | 0.98957 | -0.2005 | 2.7706
18 | 0.0067067 | 0.0016809 | -0.006706 | -0.0016807 | 7.2483e-07 | 2.1977e-07 | 0.010085 | 0.010085 | 0.010085 | 0.98957 | -0.2005 | 0.98945 | -0.20277 | 2.7706
19 | -0.0044758 | -0.0011204 | 0.0044759 | 0.0011204 | 3.9622e-08 | -5.6516e-09 | 0.0066728 | 0.0066728 | 0.0066728 | 0.99803 | -0.037827 | 0.99804 | -0.037641 | 1.8332
20 | 0.0022135 | 0.00055346 | -0.0022135 | -0.00055348 | 7.8553e-09 | -2.0112e-08 | 0.0032998 | 0.0032998 | 0.0032998 | 0.99803 | -0.037827 | 0.99803 | -0.037902 | 0.90655
21 | -0.0069871 | -0.0017498 | 0.0069881 | 0.0017501 | 9.8731e-07 | 3.1475e-07 | 0.010417 | 0.010417 | 0.010417 | 0.99804 | -0.037641 | 0.9982 | -0.034674 | 2.8618
22 | 0.0022135 | 0.00055348 | -0.0022131 | -0.00055458 | 4.3058e-07 | -1.1019e-06 | 0.0032998 | 0.0033003 | 0.0033003 | 0.99803 | -0.037902 | 0.99782 | -0.041989 | 0.90668
23 | -0.01877 | -0.0047043 | 0.018775 | 0.0047075 | 5.3897e-06 | 3.2094e-06 | 0.02798 | 0.02798 | 0.02798 | 0.9982 | -0.034674 | 0.99851 | -0.028648 | 7.6868
24 | 0.011781 | 0.0029541 | -0.011767 | -0.0029468 | 1.3988e-05 | 7.3737e-06 | 0.017563 | 0.017564 | 0.017564 | 0.9982 | -0.034674 | 0.9969 | -0.059614 | 4.8252
25 | 0.0022131 | 0.00055458 | -0.0022131 | -0.00055465 | 2.5559e-08 | -6.5376e-08 | 0.0033003 | 0.0033003 | 0.0033003 | 0.99782 | -0.041989 | 0.9978 | -0.042232 | 0.90669
26 | -0.021758 | -0.0054551 | 0.021767 | 0.0054603 | 8.4928e-06 | 5.1535e-06 | 0.032425 | 0.032425 | 0.032425 | 0.99851 | -0.028648 | 0.99894 | -0.02046 | 8.9081
27 | 0.010652 | 0.0026673 | -0.01065 | -0.0026662 | 2.1692e-06 | 1.09e-06 | 0.015899 | 0.015899 | 0.015899 | 0.9969 | -0.059614 | 0.99668 | -0.063892 | 4.368
28 | -0.024482 | -0.0061407 | 0.024485 | 0.0061427 | 3.2554e-06 | 1.998e-06 | 0.03647 | 0.036469 | 0.03647 | 0.99894 | -0.02046 | 0.99908 | -0.017671 | 10.0191
29 | -0.0012528 | -0.00031399 | 0.0012529 | 0.00031366 | 3.5638e-08 | -3.3047e-07 | 0.0018715 | 0.0018713 | 0.0018715 | 0.99614 | -0.074274 | 0.99617 | -0.073677 | 0.51414

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.074714 | 0.018468

## res_load
| p_mw | q_mvar
0 | 0.0010617 | 0.00026609
1 | 0.0013298 | 0.00033328
2 | 0.001077 | 0.00026991
3 | 0.0010993 | 0.00027552
4 | 0.0011762 | 0.00029478
5 | 0.0009776 | 0.00024501
6 | 0.0079284 | 0.001987
7 | 0.0096185 | 0.0024106
8 | 0.0082101 | 0.0020577
9 | 0.0025153 | 0.00063038
10 | 0.0032721 | 0.00082006
11 | 0.0077375 | 0.0019392
12 | 0.006706 | 0.0016807
13 | 0.0022623 | 0.00056698
14 | 0.0025112 | 0.00062936
15 | 0.0029832 | 0.00074765
16 | 0.0011152 | 0.00027948
17 | 0.0022131 | 0.00055465
18 | 0.0027149 | 0.00068042
19 | 0.001466 | 0.00036742
20 | 0.0021934 | 0.00054971
21 | 0.0012528 | 0.00031399
22 | 0.0012051 | 0.00030203

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1