## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-135_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-135_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-135_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1630-135_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1630-135_0_3_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_1630-135_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1630-135_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1630-135_0_3_node_34 | 0.4 | n |  | TRUE
8 | bus_LV_1630-135_0_3_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1630-135_0_3_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_1630-135_0_3_node_24 | 0.4 | n |  | TRUE
11 | bus_LV_1630-135_0_3_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1630-135_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1630-135_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1630-135_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1630-135_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1630-135_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1630-135_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1630-135_0_3_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1630-135_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1630-135_0_3_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1630-135_0_3_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1630-135_0_3_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_1630-135_0_3_node_31 | 0.4 | n |  | TRUE
24 | bus_LV_1630-135_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1630-135_0_3_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_1630-135_0_3_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_1630-135_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1630-135_0_3_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1630-135_0_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1630-135_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1630-135_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_MV_20_1_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-135_0_3_load_0 | 0 | 0.061592 | 0.015436 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-135_0_3_load_3 | 2 | 0.014994 | 0.003758 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-135_0_3_load_6 | 6 | 0.026217 | 0.0065705 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-135_0_3_load_34 | 7 | 0.061657 | 0.015453 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-135_0_3_load_22 | 9 | 0.01748 | 0.004381 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-135_0_3_load_16 | 11 | 0.02858 | 0.0071627 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-135_0_3_load_7 | 12 | 0.0040457 | 0.0010139 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-135_0_3_load_10 | 15 | 0.0040905 | 0.0010252 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-135_0_3_load_20 | 21 | 0.032709 | 0.0081976 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-135_0_3_load_29 | 22 | 0.04052 | 0.010155 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-135_0_3_load_31 | 23 | 0.0041045 | 0.0010287 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-135_0_3_load_33 | 25 | 0.022808 | 0.0057162 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-135_0_3_load_30 | 26 | 0.046769 | 0.011722 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-135_0_3_load_15 | 27 | 0.01633 | 0.0040927 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-135_0_3_load_26 | 29 | 0.016281 | 0.0040804 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-135_0_3_load_23 | 30 | 0.027131 | 0.0067996 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-135_0_3_load_32 | 31 | 0.0071178 | 0.0017839 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-135_0_3_line_0 |  | 0 | 1 | 0.019695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-135_0_3_line_1 |  | 1 | 2 | 0.018845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-135_0_3_line_2 |  | 1 | 3 | 0.024277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-135_0_3_line_3 |  | 2 | 5 | 0.021775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-135_0_3_line_4 |  | 3 | 7 | 0.048615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-135_0_3_line_5 |  | 3 | 8 | 0.025439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1630-135_0_3_line_6 |  | 4 | 5 | 0.014702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-135_0_3_line_7 |  | 4 | 6 | 0.026487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-135_0_3_line_8 |  | 5 | 9 | 0.010485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-135_0_3_line_9 |  | 8 | 10 | 0.016407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1630-135_0_3_line_10 |  | 8 | 11 | 0.021618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-135_0_3_line_11 |  | 10 | 30 | 0.015488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1630-135_0_3_line_12 |  | 10 | 24 | 0.043574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1630-135_0_3_line_13 |  | 11 | 27 | 0.03705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-135_0_3_line_14 |  | 12 | 13 | 0.010687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-135_0_3_line_15 |  | 12 | 14 | 0.0057572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-135_0_3_line_16 |  | 13 | 15 | 0.0099042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-135_0_3_line_17 |  | 14 | 16 | 0.016444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-135_0_3_line_18 |  | 14 | 17 | 0.002888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-135_0_3_line_19 |  | 15 | 18 | 0.01093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-135_0_3_line_20 |  | 16 | 22 | 0.030441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-135_0_3_line_21 |  | 17 | 21 | 0.040221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-135_0_3_line_22 |  | 18 | 23 | 0.01888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-135_0_3_line_23 |  | 18 | 24 | 0.043486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1630-135_0_3_line_24 |  | 19 | 20 | 0.060389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-135_0_3_line_25 |  | 19 | 21 | 0.011159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-135_0_3_line_26 |  | 20 | 25 | 0.022605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-135_0_3_line_27 |  | 23 | 26 | 0.0041553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-135_0_3_line_28 |  | 24 | 28 | 0.045181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-135_0_3_line_29 |  | 24 | 29 | 0.024985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-135_0_3_line_30 |  | 28 | 31 | 0.016691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-135_0_3_trafo_23 | 0.63 MVA 20/0.4 kV | 32 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2720345.4133 | 1223526.5886 | 2720343.7265 | 1223519.6045 | 2720351.3433 | 1223509.68
1 | 2720345.4133 | 1223526.5886 | 2720361.0853 | 1223516.1235
2 | 2720345.4133 | 1223526.5886 | 2720337.5546 | 1223531.8338 | 2720346.6866 | 1223543.5164
3 | 2720379.1938 | 1223504.0316 | 2720361.0853 | 1223516.1235
4 | 2720311.6677 | 1223554.9398 | 2720321.622 | 1223566.0942 | 2720346.6866 | 1223543.5164
5 | 2720346.6866 | 1223543.5164 | 2720352.2841 | 1223550.6796 | 2720358.7998 | 1223559.6962 | 2720361.6847 | 1223564.0802
6 | 2720379.1938 | 1223504.0316 | 2720370.852 | 1223491.909
7 | 2720370.852 | 1223491.909 | 2720392.8141 | 1223477.1034
8 | 2720379.1938 | 1223504.0316 | 2720387.9128 | 1223498.2089
9 | 2720362.4682 | 1223576.717 | 2720367.2127 | 1223572.4207 | 2720361.6847 | 1223564.0802
10 | 2720361.6847 | 1223564.0802 | 2720378.6535 | 1223557.7183 | 2720381.9753 | 1223556.6292
11 | 2720362.4682 | 1223576.717 | 2720355.4593 | 1223583.0803 | 2720351.0889 | 1223587.2228
12 | 2720362.4682 | 1223576.717 | 2720367.2127 | 1223572.4207 | 2720377.6719 | 1223588.2334 | 2720387.7188 | 1223603.4262
13 | 2720412.4335 | 1223536.9157 | 2720409.3279 | 1223537.9564 | 2720392.5822 | 1223553.1519 | 2720381.9753 | 1223556.6292
14 | 2720351.761 | 1223642.8968 | 2720342.236 | 1223638.0501
15 | 2720337.1049 | 1223635.4391 | 2720342.236 | 1223638.0501
16 | 2720351.761 | 1223642.8968 | 2720359.9653 | 1223637.3484
17 | 2720337.1049 | 1223635.4391 | 2720330.122 | 1223631.8952 | 2720323.1949 | 1223626.7178
18 | 2720337.1049 | 1223635.4391 | 2720334.588 | 1223636.8672
19 | 2720369.0192 | 1223631.2255 | 2720359.9653 | 1223637.3484
20 | 2720323.1949 | 1223626.7178 | 2720311.0402 | 1223615.5968 | 2720298.8386 | 1223608.8017
21 | 2720334.588 | 1223636.8672 | 2720323.5843 | 1223643.0941 | 2720319.5175 | 1223645.3915 | 2720316.1251 | 1223646.6016 | 2720312.5393 | 1223647.2408 | 2720296.8877 | 1223646.6628
22 | 2720369.0192 | 1223631.2255 | 2720372.1122 | 1223637.315 | 2720384.0593 | 1223638.8874
23 | 2720369.0192 | 1223631.2255 | 2720394.6452 | 1223613.8856 | 2720387.7188 | 1223603.4262
24 | 2720237.8652 | 1223641.7167 | 2720250.0964 | 1223645.678 | 2720260.8806 | 1223649.1763 | 2720276.9269 | 1223653.5372 | 2720286.3807 | 1223656.0524 | 2720296.0615 | 1223657.4714
25 | 2720296.0615 | 1223657.4714 | 2720296.561 | 1223646.6508 | 2720296.8877 | 1223646.6628
26 | 2720237.8652 | 1223641.7167 | 2720244.7858 | 1223620.1952
27 | 2720388.1791 | 1223639.4297 | 2720384.0593 | 1223638.8874
28 | 2720387.7188 | 1223603.4262 | 2720394.6452 | 1223613.8856 | 2720421.7965 | 1223595.7761
29 | 2720387.7188 | 1223603.4262 | 2720377.051 | 1223610.6718 | 2720376.4894 | 1223613.685 | 2720369.0745 | 1223618.828
30 | 2720421.7965 | 1223595.7761 | 2720431.0315 | 1223609.6794

## bus_geodata
| x | y | coords
0 | 2720351.3433 | 1223509.68
1 | 2720345.4133 | 1223526.5886
2 | 2720361.0853 | 1223516.1235
3 | 2720346.6866 | 1223543.5164
4 | 2720370.852 | 1223491.909
5 | 2720379.1938 | 1223504.0316
6 | 2720392.8141 | 1223477.1034
7 | 2720311.6677 | 1223554.9398
8 | 2720361.6847 | 1223564.0802
9 | 2720387.9128 | 1223498.2089
10 | 2720362.4682 | 1223576.717
11 | 2720381.9754 | 1223556.6292
12 | 2720342.236 | 1223638.0501
13 | 2720351.761 | 1223642.8968
14 | 2720337.1049 | 1223635.4391
15 | 2720359.9653 | 1223637.3484
16 | 2720323.1949 | 1223626.7178
17 | 2720334.588 | 1223636.8672
18 | 2720369.0192 | 1223631.2255
19 | 2720296.0615 | 1223657.4714
20 | 2720237.8652 | 1223641.7167
21 | 2720296.8877 | 1223646.6628
22 | 2720298.8386 | 1223608.8017
23 | 2720384.0593 | 1223638.8874
24 | 2720387.7188 | 1223603.4262
25 | 2720244.7858 | 1223620.1952
26 | 2720388.1791 | 1223639.4297
27 | 2720412.4335 | 1223536.9157
28 | 2720421.7965 | 1223595.7761
29 | 2720369.0745 | 1223618.828
30 | 2720351.0889 | 1223587.2228
31 | 2720431.0315 | 1223609.6794
32 | 2720362.4682 | 1223576.717

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99105 | -0.17201 | 0.061592 | 0.015436
1 | 0.99216 | -0.15051 | 0 | 0
2 | 0.99114 | -0.17011 | 0.014994 | 0.003758
3 | 0.99483 | -0.098945 | 0 | 0
4 | 0.98992 | -0.19387 | 0 | 0
5 | 0.99027 | -0.18701 | 0 | 0
6 | 0.98928 | -0.20622 | 0.026217 | 0.0065705
7 | 0.99209 | -0.15188 | 0.061657 | 0.015453
8 | 0.99695 | -0.058275 | 0 | 0
9 | 0.99011 | -0.19027 | 0.01748 | 0.004381
10 | 0.99808 | -0.036543 | 0 | 0
11 | 0.99607 | -0.075316 | 0.02858 | 0.0071627
12 | 0.98967 | -0.19823 | 0.0040457 | 0.0010139
13 | 0.99066 | -0.17921 | 0 | 0
14 | 0.98916 | -0.20807 | 0 | 0
15 | 0.99157 | -0.16162 | 0.0040905 | 0.0010252
16 | 0.98855 | -0.21995 | 0 | 0
17 | 0.98902 | -0.21093 | 0 | 0
18 | 0.99261 | -0.14146 | 0 | 0
19 | 0.98673 | -0.25536 | 0 | 0
20 | 0.98546 | -0.28005 | 0 | 0
21 | 0.98696 | -0.2508 | 0.032709 | 0.0081976
22 | 0.98742 | -0.24197 | 0.04052 | 0.010155
23 | 0.99174 | -0.15846 | 0.0041045 | 0.0010287
24 | 0.99571 | -0.082003 | 0 | 0
25 | 0.98499 | -0.2893 | 0.022808 | 0.0057162
26 | 0.99156 | -0.16191 | 0.046769 | 0.011722
27 | 0.99551 | -0.085951 | 0.01633 | 0.0040927
28 | 0.99541 | -0.08766 | 0 | 0
29 | 0.99534 | -0.089157 | 0.016281 | 0.0040804
30 | 1 | 0 | -0.41037 | -0.10376
31 | 0.99531 | -0.08975 | 0.0071178 | 0.0017839
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.061592 | -0.015436 | 0.061655 | 0.015476 | 6.3163e-05 | 4.017e-05 | 0.092477 | 0.092477 | 0.092477 | 0.99105 | -0.17201 | 0.99216 | -0.15051 | 25.4058
1 | 0.058808 | 0.014783 | -0.058753 | -0.014748 | 5.4994e-05 | 3.4953e-05 | 0.088215 | 0.088215 | 0.088215 | 0.99216 | -0.15051 | 0.99114 | -0.17011 | 24.235
2 | -0.12046 | -0.03026 | 0.12076 | 0.03045 | 0.00029723 | 0.00018992 | 0.18069 | 0.18069 | 0.18069 | 0.99216 | -0.15051 | 0.99483 | -0.098945 | 49.6407
3 | 0.043759 | 0.01099 | -0.043724 | -0.010968 | 3.525e-05 | 2.228e-05 | 0.065704 | 0.065704 | 0.065704 | 0.99114 | -0.17011 | 0.99027 | -0.18701 | 18.0506
4 | 0.061813 | 0.015552 | -0.061657 | -0.015453 | 0.00015591 | 9.9154e-05 | 0.092478 | 0.092478 | 0.092478 | 0.99483 | -0.098945 | 0.99209 | -0.15188 | 25.4061
5 | -0.18257 | -0.046001 | 0.18293 | 0.046229 | 0.00035593 | 0.00022713 | 0.27317 | 0.27317 | 0.27317 | 0.99483 | -0.098945 | 0.99695 | -0.058275 | 37.5233
6 | -0.026232 | -0.0065801 | 0.026241 | 0.0065854 | 8.573e-06 | 5.2977e-06 | 0.039433 | 0.039433 | 0.039433 | 0.98992 | -0.19387 | 0.99027 | -0.18701 | 10.8333
7 | 0.026232 | 0.0065801 | -0.026217 | -0.0065705 | 1.5445e-05 | 9.5445e-06 | 0.039433 | 0.039434 | 0.039434 | 0.98992 | -0.19387 | 0.98928 | -0.20622 | 10.8334
8 | 0.017483 | 0.0043826 | -0.01748 | -0.004381 | 2.7135e-06 | 1.6018e-06 | 0.026271 | 0.026271 | 0.026271 | 0.99027 | -0.18701 | 0.99011 | -0.19027 | 7.2173
9 | -0.22788 | -0.057512 | 0.22812 | 0.057663 | 0.00023746 | 0.00015133 | 0.34027 | 0.34027 | 0.34027 | 0.99695 | -0.058275 | 0.99808 | -0.036543 | 31.1605
10 | 0.044954 | 0.011283 | -0.044918 | -0.01126 | 3.6504e-05 | 2.3081e-05 | 0.067103 | 0.067104 | 0.067104 | 0.99695 | -0.058275 | 0.99607 | -0.075316 | 18.435
11 | -0.408 | -0.1033 | 0.40872 | 0.10376 | 0.00071721 | 0.00045841 | 0.60865 | 0.60865 | 0.60865 | 0.99808 | -0.036543 | 1 | 0 | 55.7372
12 | 0.17988 | 0.045635 | -0.17949 | -0.045386 | 0.00039231 | 0.00024937 | 0.26838 | 0.26838 | 0.26838 | 0.99808 | -0.036543 | 0.99571 | -0.082003 | 24.5768
13 | 0.016338 | 0.0040975 | -0.01633 | -0.0040927 | 8.2777e-06 | 4.8157e-06 | 0.024409 | 0.024409 | 0.024409 | 0.99607 | -0.075316 | 0.99551 | -0.085951 | 6.7057
14 | -0.10035 | -0.025251 | 0.10044 | 0.025309 | 9.1277e-05 | 5.828e-05 | 0.15091 | 0.15091 | 0.15091 | 0.98967 | -0.19823 | 0.99066 | -0.17921 | 41.4602
15 | 0.096303 | 0.024237 | -0.096258 | -0.024208 | 4.5287e-05 | 2.891e-05 | 0.14483 | 0.14483 | 0.14483 | 0.98967 | -0.19823 | 0.98916 | -0.20807 | 39.7891
16 | -0.10044 | -0.025309 | 0.10052 | 0.025363 | 8.459e-05 | 5.401e-05 | 0.15091 | 0.15091 | 0.15091 | 0.99066 | -0.17921 | 0.99157 | -0.16162 | 41.4601
17 | 0.040586 | 0.010197 | -0.040563 | -0.010182 | 2.2993e-05 | 1.4505e-05 | 0.061063 | 0.061063 | 0.061063 | 0.98916 | -0.20807 | 0.98855 | -0.21995 | 16.7755
18 | 0.055672 | 0.014011 | -0.055664 | -0.014007 | 7.5997e-06 | 4.8268e-06 | 0.083769 | 0.083769 | 0.083769 | 0.98916 | -0.20807 | 0.98902 | -0.21093 | 23.0135
19 | -0.10462 | -0.026389 | 0.10472 | 0.026453 | 0.0001011 | 6.4562e-05 | 0.15705 | 0.15705 | 0.15705 | 0.99157 | -0.16162 | 0.99261 | -0.14146 | 43.1465
20 | 0.040563 | 0.010182 | -0.04052 | -0.010155 | 4.2564e-05 | 2.6851e-05 | 0.061063 | 0.061063 | 0.061063 | 0.98855 | -0.21995 | 0.98742 | -0.24197 | 16.7756
21 | 0.055664 | 0.014007 | -0.055559 | -0.013939 | 0.00010584 | 6.7223e-05 | 0.083769 | 0.083769 | 0.083769 | 0.98902 | -0.21093 | 0.98696 | -0.2508 | 23.0136
22 | 0.050923 | 0.012781 | -0.050881 | -0.012755 | 4.1266e-05 | 2.6166e-05 | 0.076344 | 0.076344 | 0.076344 | 0.99261 | -0.14146 | 0.99174 | -0.15846 | 20.9738
23 | -0.15564 | -0.039234 | 0.15608 | 0.039517 | 0.00044417 | 0.00028314 | 0.2334 | 0.2334 | 0.2334 | 0.99261 | -0.14146 | 0.99571 | -0.082003 | 32.0601
24 | 0.022845 | 0.0057388 | -0.022818 | -0.0057223 | 2.6885e-05 | 1.6436e-05 | 0.034455 | 0.034456 | 0.034456 | 0.98673 | -0.25536 | 0.98546 | -0.28005 | 9.4658
25 | -0.022845 | -0.0057388 | 0.02285 | 0.0057418 | 4.9679e-06 | 3.0369e-06 | 0.034455 | 0.034455 | 0.034455 | 0.98673 | -0.25536 | 0.98696 | -0.2508 | 9.4658
26 | 0.022818 | 0.0057223 | -0.022808 | -0.0057162 | 1.0064e-05 | 6.1529e-06 | 0.034456 | 0.034456 | 0.034456 | 0.98546 | -0.28005 | 0.98499 | -0.2893 | 9.4659
27 | 0.046777 | 0.011726 | -0.046769 | -0.011722 | 7.6761e-06 | 4.8591e-06 | 0.070186 | 0.070186 | 0.070186 | 0.99174 | -0.15846 | 0.99156 | -0.16191 | 19.2819
28 | 0.0071205 | 0.0017848 | -0.0071185 | -0.0017841 | 1.9186e-06 | 6.4038e-07 | 0.010641 | 0.010641 | 0.010641 | 0.99571 | -0.082003 | 0.99541 | -0.08766 | 2.9234
29 | 0.016287 | 0.0040836 | -0.016281 | -0.0040804 | 5.5506e-06 | 3.2276e-06 | 0.02434 | 0.02434 | 0.02434 | 0.99571 | -0.082003 | 0.99534 | -0.089157 | 6.6868
30 | 0.0071185 | 0.0017841 | -0.0071178 | -0.0017839 | 7.0877e-07 | 2.3667e-07 | 0.010641 | 0.010641 | 0.010641 | 0.99541 | -0.08766 | 0.99531 | -0.08975 | 2.9235

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4375 | 0.11056

## res_load
| p_mw | q_mvar
0 | 0.061592 | 0.015436
1 | 0.014994 | 0.003758
2 | 0.026217 | 0.0065705
3 | 0.061657 | 0.015453
4 | 0.01748 | 0.004381
5 | 0.02858 | 0.0071627
6 | 0.0040457 | 0.0010139
7 | 0.0040905 | 0.0010252
8 | 0.032709 | 0.0081976
9 | 0.04052 | 0.010155
10 | 0.0041045 | 0.0010287
11 | 0.022808 | 0.0057162
12 | 0.046769 | 0.011722
13 | 0.01633 | 0.0040927
14 | 0.016281 | 0.0040804
15 | 0.027131 | 0.0067996
16 | 0.0071178 | 0.0017839

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1