## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-140_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-140_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-140_0_2_node_38 | 0.4 | n |  | TRUE
3 | bus_LV_1630-140_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-140_0_2_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_1630-140_0_2_node_2 | 0.4 | n |  | TRUE
6 | bus_LV_1630-140_0_2_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_1630-140_0_2_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_1630-140_0_2_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1630-140_0_2_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_1630-140_0_2_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_1630-140_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1630-140_0_2_node_26 | 0.4 | n |  | TRUE
13 | bus_LV_1630-140_0_2_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_1630-140_0_2_node_70 | 0.4 | n |  | TRUE
15 | bus_LV_1630-140_0_2_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1630-140_0_2_node_4 | 0.4 | n |  | TRUE
17 | bus_LV_1630-140_0_2_node_6 | 0.4 | n |  | TRUE
18 | bus_LV_1630-140_0_2_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1630-140_0_2_node_64 | 0.4 | n |  | TRUE
20 | bus_LV_1630-140_0_2_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1630-140_0_2_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1630-140_0_2_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_1630-140_0_2_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1630-140_0_2_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1630-140_0_2_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1630-140_0_2_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1630-140_0_2_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1630-140_0_2_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1630-140_0_2_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_1630-140_0_2_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_1630-140_0_2_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1630-140_0_2_node_47 | 0.4 | n |  | TRUE
33 | bus_LV_1630-140_0_2_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_1630-140_0_2_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_1630-140_0_2_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_1630-140_0_2_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_1630-140_0_2_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_1630-140_0_2_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_1630-140_0_2_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1630-140_0_2_node_67 | 0.4 | n |  | TRUE
41 | bus_LV_1630-140_0_2_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_1630-140_0_2_node_65 | 0.4 | n |  | TRUE
43 | bus_LV_1630-140_0_2_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_1630-140_0_2_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_1630-140_0_2_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_1630-140_0_2_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_1630-140_0_2_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_1630-140_0_2_node_55 | 0.4 | n |  | TRUE
49 | bus_LV_1630-140_0_2_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_1630-140_0_2_node_66 | 0.4 | n |  | TRUE
51 | bus_LV_1630-140_0_2_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_1630-140_0_2_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_1630-140_0_2_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_1630-140_0_2_node_61 | 0.4 | n |  | TRUE
55 | bus_LV_1630-140_0_2_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_1630-140_0_2_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_1630-140_0_2_node_69 | 0.4 | n |  | TRUE
58 | bus_LV_1630-140_0_2_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_1630-140_0_2_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_1630-140_0_2_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_1630-140_0_2_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_1630-140_0_2_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_1630-140_0_2_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_1630-140_0_2_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_1630-140_0_2_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_1630-140_0_2_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_1630-140_0_2_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_1630-140_0_2_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_1630-140_0_2_node_58 | 0.4 | n |  | TRUE
70 | bus_MV_0_node_4 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-140_0_2_load_0 | 0 | 0.00049537 | 0.00012415 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-140_0_2_load_27 | 6 | 0.00044857 | 0.00011242 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-140_0_2_load_24 | 7 | 0.00054985 | 0.00013781 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-140_0_2_load_10 | 9 | 0.00065118 | 0.0001632 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-140_0_2_load_25 | 10 | 0.00049595 | 0.0001243 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-140_0_2_load_7 | 11 | 0.00032281 | 8.0904e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-140_0_2_load_26 | 12 | 0.0060609 | 0.001519 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-140_0_2_load_5 | 13 | 0.00026058 | 6.5308e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-140_0_2_load_70 | 14 | 0.0018718 | 0.00046911 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-140_0_2_load_11 | 15 | 0.0005318 | 0.00013328 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-140_0_2_load_4 | 16 | 0.00067175 | 0.00016836 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-140_0_2_load_64 | 19 | 0.00066894 | 0.00016765 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-140_0_2_load_17 | 21 | 0.0005831 | 0.00014614 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-140_0_2_load_23 | 22 | 0.0031619 | 0.00079245 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-140_0_2_load_22 | 23 | 0.0015493 | 0.00038829 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-140_0_2_load_13 | 25 | 0.001478 | 0.00037042 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-140_0_2_load_14 | 26 | 0.00023246 | 5.826e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-140_0_2_load_15 | 27 | 0.00058472 | 0.00014654 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-140_0_2_load_29 | 30 | 0.00029979 | 7.5135e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-140_0_2_load_16 | 31 | 0.00028238 | 7.077e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-140_0_2_load_47 | 32 | 0.00030313 | 7.5971e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-140_0_2_load_35 | 33 | 0.00042169 | 0.00010568 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-140_0_2_load_20 | 35 | 0.00039096 | 9.7983e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-140_0_2_load_30 | 36 | 0.00050306 | 0.00012608 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-140_0_2_load_32 | 37 | 0.00037168 | 9.3151e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-140_0_2_load_39 | 38 | 0.00066195 | 0.0001659 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-140_0_2_load_67 | 40 | 0.00028425 | 7.124e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-140_0_2_load_34 | 44 | 0.00042291 | 0.00010599 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-140_0_2_load_46 | 45 | 0.00022717 | 5.6934e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-140_0_2_load_40 | 46 | 0.00038318 | 9.6034e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-140_0_2_load_45 | 47 | 0.00045519 | 0.00011408 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1630-140_0_2_load_42 | 49 | 0.00027243 | 6.8277e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1630-140_0_2_load_66 | 50 | 0.00041934 | 0.0001051 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1630-140_0_2_load_36 | 51 | 0.0013881 | 0.00034789 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1630-140_0_2_load_62 | 52 | 0.00046457 | 0.00011643 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1630-140_0_2_load_60 | 53 | 0.00046373 | 0.00011622 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1630-140_0_2_load_41 | 55 | 0.00023725 | 5.946e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1630-140_0_2_load_43 | 56 | 0.00026 | 6.5161e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1630-140_0_2_load_69 | 57 | 0.00021614 | 5.4171e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1630-140_0_2_load_48 | 59 | 0.00026015 | 6.52e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1630-140_0_2_load_52 | 61 | 0.00033984 | 8.5172e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1630-140_0_2_load_63 | 64 | 0.00021486 | 5.3849e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1630-140_0_2_load_68 | 65 | 0.00020796 | 5.2119e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1630-140_0_2_load_56 | 66 | 0.00029714 | 7.4471e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1630-140_0_2_load_57 | 68 | 0.00037 | 9.273e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-140_0_2_line_0 |  | 0 | 1 | 0.10001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-140_0_2_line_1 |  | 0 | 2 | 0.20701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-140_0_2_line_2 |  | 1 | 3 | 0.23085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-140_0_2_line_3 |  | 2 | 4 | 0.10908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-140_0_2_line_4 |  | 3 | 8 | 0.0096134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-140_0_2_line_5 |  | 3 | 9 | 0.14356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-140_0_2_line_6 |  | 4 | 19 | 0.039856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-140_0_2_line_7 |  | 4 | 17 | 0.14503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-140_0_2_line_8 |  | 5 | 6 | 0.026582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-140_0_2_line_9 |  | 5 | 7 | 0.079656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-140_0_2_line_10 |  | 7 | 10 | 0.012673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-140_0_2_line_11 |  | 8 | 14 | 0.029088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-140_0_2_line_12 |  | 9 | 15 | 0.015091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-140_0_2_line_13 |  | 10 | 12 | 0.010848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-140_0_2_line_14 |  | 11 | 12 | 0.13947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-140_0_2_line_15 |  | 11 | 13 | 0.24855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-140_0_2_line_16 |  | 13 | 16 | 0.19571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-140_0_2_line_17 |  | 16 | 17 | 0.020114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-140_0_2_line_18 |  | 17 | 18 | 0.24098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-140_0_2_line_19 |  | 18 | 20 | 0.021672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-140_0_2_line_20 |  | 18 | 21 | 0.077462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-140_0_2_line_21 |  | 20 | 22 | 0.026429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-140_0_2_line_22 |  | 20 | 23 | 0.01269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-140_0_2_line_23 |  | 21 | 24 | 0.0097463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-140_0_2_line_24 |  | 22 | 38 | 0.27472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-140_0_2_line_25 |  | 24 | 34 | 0.11209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-140_0_2_line_26 |  | 24 | 35 | 0.039132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-140_0_2_line_27 |  | 25 | 26 | 0.025289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-140_0_2_line_28 |  | 26 | 27 | 0.0087791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-140_0_2_line_29 |  | 27 | 28 | 0.017172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-140_0_2_line_30 |  | 28 | 29 | 0.33464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-140_0_2_line_31 |  | 28 | 30 | 0.10708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-140_0_2_line_32 |  | 29 | 40 | 0.092424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-140_0_2_line_33 |  | 29 | 41 | 0.023306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-140_0_2_line_34 |  | 29 | 42 | 0.20246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1630-140_0_2_line_35 |  | 30 | 34 | 0.012825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-140_0_2_line_36 |  | 31 | 32 | 0.15271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-140_0_2_line_37 |  | 32 | 33 | 0.0064392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-140_0_2_line_38 |  | 33 | 43 | 0.028733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-140_0_2_line_39 |  | 34 | 36 | 0.090019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-140_0_2_line_40 |  | 35 | 37 | 0.10833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-140_0_2_line_41 |  | 38 | 39 | 0.058301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-140_0_2_line_42 |  | 39 | 46 | 0.022921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-140_0_2_line_43 |  | 39 | 51 | 0.01876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-140_0_2_line_44 |  | 41 | 48 | 0.22647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1630-140_0_2_line_45 |  | 41 | 49 | 0.032211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1630-140_0_2_line_46 |  | 42 | 50 | 0.029428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1630-140_0_2_line_47 |  | 43 | 44 | 0.017004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1630-140_0_2_line_48 |  | 43 | 45 | 0.26096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1630-140_0_2_line_49 |  | 45 | 47 | 0.12354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1630-140_0_2_line_50 |  | 46 | 47 | 0.037117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1630-140_0_2_line_51 |  | 48 | 57 | 0.032348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1630-140_0_2_line_52 |  | 48 | 58 | 0.048197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1630-140_0_2_line_53 |  | 49 | 55 | 0.0031853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1630-140_0_2_line_54 |  | 51 | 52 | 0.061267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1630-140_0_2_line_55 |  | 52 | 54 | 0.058994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1630-140_0_2_line_56 |  | 53 | 54 | 0.037464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1630-140_0_2_line_57 |  | 55 | 56 | 0.064151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1630-140_0_2_line_58 |  | 58 | 66 | 0.054069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1630-140_0_2_line_59 |  | 58 | 60 | 0.1116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1630-140_0_2_line_60 |  | 59 | 60 | 0.026961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1630-140_0_2_line_61 |  | 60 | 61 | 0.009444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1630-140_0_2_line_62 |  | 60 | 62 | 0.21355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1630-140_0_2_line_63 |  | 62 | 65 | 0.012833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1630-140_0_2_line_64 |  | 62 | 63 | 0.21766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1630-140_0_2_line_65 |  | 63 | 64 | 0.12589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1630-140_0_2_line_66 |  | 64 | 67 | 0.14588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1630-140_0_2_line_67 |  | 67 | 69 | 0.12799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1630-140_0_2_line_68 |  | 68 | 69 | 0.0098366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-140_0_2_trafo_4 | 0.63 MVA 20/0.4 kV | 70 | 16 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30
0 | 2721826.3577 | 1218070.6996 | 2721826.2338 | 1218067.1053 | 2721826.1265 | 1218053.4259 | 2721822.9104 | 1218040.6502 | 2721810.7023 | 1218023.8988 | 2721801.9307 | 1218017.6813 | 2721792.2957 | 1218008.3883 | 2721784.4975 | 1218004.6927 | 2721778.3532 | 1218003.6663 | 2721774.8234 | 1218003.2494 | 2721769.1697 | 1218000.5096
1 | 2721575.2289 | 1218072.9057 | 2721769.1697 | 1218000.5096
2 | 2721968.9824 | 1218120.6003 | 2721965.4551 | 1218128.9679 | 2721964.0281 | 1218137.1006 | 2721964.5092 | 1218146.9737 | 2721965.5908 | 1218153.4786 | 2721967.0948 | 1218158.6357 | 2721968.1025 | 1218166.151 | 2721967.7447 | 1218171.7591 | 2721962.5775 | 1218166.4048 | 2721954.6539 | 1218151.7979 | 2721941.6373 | 1218135.252 | 2721912.2145 | 1218122.7069 | 2721878.7068 | 1218109.0442 | 2721870.0391 | 1218102.9511 | 2721852.5464 | 1218093.2636 | 2721843.2821 | 1218085.9018 | 2721826.3577 | 1218070.6996
3 | 2721575.2289 | 1218072.9057 | 2721572.6562 | 1218075.8222 | 2721558.951 | 1218081.7916 | 2721554.0452 | 1218085.1831 | 2721548.6315 | 1218094.8579 | 2721544.4495 | 1218104.0798 | 2721541.4946 | 1218107.1219 | 2721538.8885 | 1218108.3252 | 2721535.5636 | 1218109.0357 | 2721505.6457 | 1218107.3131 | 2721498.0197 | 1218109.6928 | 2721492.5547 | 1218113.3287 | 2721487.2329 | 1218119.625
4 | 2721968.9824 | 1218120.6003 | 2721971.2745 | 1218115.0874 | 2721972.0232 | 1218111.5222
5 | 2721968.9824 | 1218120.6003 | 2721972.1349 | 1218133.1301 | 2721973.6304 | 1218143.1463 | 2721975.6451 | 1218148.5806 | 2721980.4525 | 1218155.9292 | 2721988.7661 | 1218174.8474 | 2721993.5587 | 1218186.6213 | 2722000.7961 | 1218200.9918 | 2722005.3702 | 1218217.1313 | 2722007.0109 | 1218220.8011 | 2722010.3181 | 1218223.5487 | 2722020.4872 | 1218224.9024 | 2722024.1995 | 1218226.0349 | 2722027.1869 | 1218228.0865 | 2722034.1388 | 1218239.7898
6 | 2721487.2329 | 1218119.625 | 2721478.8162 | 1218122.0553 | 2721466.4996 | 1218123.9835 | 2721447.7573 | 1218123.7903
7 | 2721487.2329 | 1218119.625 | 2721483.4254 | 1218129.4773 | 2721480.0231 | 1218155.1945 | 2721480.165 | 1218180.9841 | 2721480.8186 | 1218191.3721 | 2721486.6167 | 1218201.9207 | 2721501.3 | 1218217.9547 | 2721513.8849 | 1218232.6338 | 2721518.2927 | 1218243.2208 | 2721518.3614 | 1218251.0172
8 | 2721965.6324 | 1218327.1366 | 2721971.2484 | 1218326.8847 | 2721991.0886 | 1218333.8629
9 | 2721965.6324 | 1218327.1366 | 2721970.285 | 1218331.2906 | 2722004.5643 | 1218396.2151
10 | 2722004.5643 | 1218396.2151 | 2722006.6387 | 1218400.1439 | 2722009.8707 | 1218407.7125
11 | 2721972.0232 | 1218111.5222 | 2721964.0424 | 1218106.0101 | 2721958.5064 | 1218100.4925 | 2721954.2172 | 1218089.7075
12 | 2722034.1388 | 1218239.7898 | 2722034.7831 | 1218240.8743 | 2722038.2489 | 1218244.7705 | 2722043.3333 | 1218247.4879 | 2722046.0973 | 1218248.1834
13 | 2722010.8345 | 1218418.4329 | 2722010.4566 | 1218409.0846 | 2722009.8707 | 1218407.7125
14 | 2721877.4749 | 1218459.2799 | 2722010.8345 | 1218418.4329
15 | 2721877.4749 | 1218459.2799 | 2721878.6766 | 1218445.0823 | 2721868.6044 | 1218429.7422 | 2721841.7264 | 1218387.8822 | 2721834.5207 | 1218377.1488 | 2721828.7959 | 1218372.706 | 2721814.849 | 1218367.8727 | 2721788.8568 | 1218355.0537 | 2721777.7059 | 1218353.4578 | 2721760.0463 | 1218351.9625 | 2721736.8397 | 1218336.5764 | 2721723.2117 | 1218322.0756 | 2721716.6058 | 1218310.2203 | 2721715.2167 | 1218300.1731 | 2721714.3685 | 1218298.5418
16 | 2721537 | 1218258.5796 | 2721551.0571 | 1218264.2832 | 2721561.7485 | 1218271.6626 | 2721564.4324 | 1218274.4528 | 2721570.2189 | 1218284.8122 | 2721572.9256 | 1218286.1129 | 2721579.211 | 1218285.7965 | 2721586.6452 | 1218285.37 | 2721622.969 | 1218284.1771 | 2721643.4613 | 1218286.7641 | 2721649.8585 | 1218286.55 | 2721667.9225 | 1218279.4133 | 2721675.0121 | 1218278.7576 | 2721679.4413 | 1218280.1046 | 2721698.8255 | 1218286.7612 | 2721712.47 | 1218294.8906 | 2721714.3685 | 1218298.5418
17 | 2721518.3614 | 1218251.0172 | 2721537 | 1218258.5796
18 | 2721335.018 | 1218393.3468 | 2721340.8243 | 1218388.5947 | 2721353.3952 | 1218380.1219 | 2721369.83 | 1218371.3054 | 2721392.6862 | 1218358.4833 | 2721403.5081 | 1218348.6628 | 2721412.705 | 1218339.9768 | 2721419.9243 | 1218332.9518 | 2721430.3923 | 1218328.9509 | 2721449.2975 | 1218325.5891 | 2721463.762 | 1218321.4474 | 2721477.1938 | 1218310.6128 | 2721481.9651 | 1218306.3624 | 2721486.7864 | 1218299.6555 | 2721497.8562 | 1218282.1676 | 2721506.177 | 1218271.7737 | 2721513.4816 | 1218264.6727 | 2721516.7729 | 1218257.4231 | 2721518.3614 | 1218251.0172
19 | 2721335.018 | 1218393.3468 | 2721313.3348 | 1218391.8375
20 | 2721335.018 | 1218393.3468 | 2721326.3935 | 1218400.41 | 2721313.2529 | 1218409.2716 | 2721302.7811 | 1218412.7277 | 2721296.375 | 1218413.3867 | 2721272.3829 | 1218415.2776 | 2721263.8378 | 1218417.8751
21 | 2721313.3348 | 1218391.8375 | 2721300.0814 | 1218368.9722
22 | 2721313.3348 | 1218391.8375 | 2721302.5545 | 1218398.5318
23 | 2721255.6283 | 1218423.0315 | 2721262.6119 | 1218418.2477 | 2721263.8378 | 1218417.8751
24 | 2721300.0814 | 1218368.9722 | 2721160.9666 | 1218132.0807
25 | 2721255.6283 | 1218423.0315 | 2721248.2122 | 1218430.0416 | 2721241.8737 | 1218438.5637 | 2721229.4586 | 1218456.1803 | 2721224.0719 | 1218460.841 | 2721217.97 | 1218463.341 | 2721208.6779 | 1218465.5425 | 2721197.2246 | 1218467.2442 | 2721187.345 | 1218470.3346 | 2721180.767 | 1218473.8479 | 2721176.0927 | 1218479.3238 | 2721174.5402 | 1218485.0967 | 2721174.6932 | 1218489.1474
26 | 2721255.6283 | 1218423.0315 | 2721263.9631 | 1218423.4793 | 2721271.2248 | 1218421.0696 | 2721278.7695 | 1218420.4227 | 2721286.8929 | 1218422.3006 | 2721293.0573 | 1218426.0664
27 | 2721245.7474 | 1218529.2272 | 2721220.8233 | 1218524.9436
28 | 2721245.7474 | 1218529.2272 | 2721248.294 | 1218529.6649 | 2721254.0889 | 1218531.8556
29 | 2721270.8433 | 1218534.85 | 2721263.3195 | 1218534.4744 | 2721259.113 | 1218533.7549 | 2721254.0889 | 1218531.8556
30 | 2721270.8433 | 1218534.85 | 2721268.0314 | 1218543.9332 | 2721257.8073 | 1218563.9406 | 2721256.827 | 1218568.8356 | 2721258.3125 | 1218573.0579 | 2721306.8819 | 1218632.159 | 2721318.25 | 1218645.0561 | 2721333.5266 | 1218659.5117 | 2721342.6699 | 1218664.9688 | 2721363.318 | 1218673.2624 | 2721376.0037 | 1218680.3596 | 2721389.7415 | 1218690.2138 | 2721396.7525 | 1218695.9945 | 2721400.8468 | 1218701.093 | 2721401.8935 | 1218705.9847 | 2721403.4677 | 1218715.9023 | 2721404.9835 | 1218719.3803 | 2721407.249 | 1218722.9515 | 2721410.2798 | 1218725.8488 | 2721413.8256 | 1218728.4342 | 2721432.4858 | 1218735.9091 | 2721437.0516 | 1218740.5947 | 2721440.2462 | 1218745.1411 | 2721443.5574 | 1218752.5255 | 2721447.2706 | 1218760.6741 | 2721452.1933 | 1218767.591 | 2721453.9276 | 1218770.0282 | 2721458.3661 | 1218774.2553
31 | 2721270.8433 | 1218534.85 | 2721271.2716 | 1218527.2417 | 2721269.0212 | 1218520.3128 | 2721265.4647 | 1218514.5137 | 2721260.6649 | 1218509.7456 | 2721254.2001 | 1218505.8333 | 2721241.9333 | 1218502.7479 | 2721228.5391 | 1218500.9629 | 2721196.458 | 1218499.309 | 2721185.8312 | 1218498.0808 | 2721183.9649 | 1218497.1964
32 | 2721458.3661 | 1218774.2553 | 2721482.3854 | 1218774.6898 | 2721484.3776 | 1218773.4183 | 2721484.4195 | 1218771.362 | 2721482.1773 | 1218770.0041 | 2721476.7433 | 1218768.8035 | 2721469.036 | 1218768.8798 | 2721466.7009 | 1218767.6089 | 2721465.9946 | 1218765.0148 | 2721465.4591 | 1218761.123 | 2721466.0896 | 1218756.2655 | 2721468.7161 | 1218751.0705 | 2721472.2856 | 1218748.0298 | 2721481.4856 | 1218745.8602 | 2721483.5035 | 1218744.0777 | 2721484.318 | 1218741.7369 | 2721485.4101 | 1218732.8634
33 | 2721458.3661 | 1218774.2553 | 2721460.6001 | 1218776.3914 | 2721474.6261 | 1218785.1286 | 2721477.4769 | 1218787.5441
34 | 2721289.3805 | 1218688.5242 | 2721303.5794 | 1218693.6395 | 2721325.0783 | 1218698.1807 | 2721331.5668 | 1218701.66 | 2721342.3619 | 1218707.2731 | 2721349.2638 | 1218709.0928 | 2721367.3046 | 1218711.2064 | 2721378.1072 | 1218716.4527 | 2721392.2989 | 1218727.1279 | 2721399.6555 | 1218730.8473 | 2721407.8229 | 1218732.0369 | 2721411.4204 | 1218731.343 | 2721413.8256 | 1218728.4342 | 2721432.4858 | 1218735.9091 | 2721437.0516 | 1218740.5947 | 2721440.2462 | 1218745.1411 | 2721443.5574 | 1218752.5255 | 2721447.2706 | 1218760.6741 | 2721452.1933 | 1218767.591 | 2721453.9276 | 1218770.0282 | 2721458.3661 | 1218774.2553
35 | 2721174.6932 | 1218489.1474 | 2721176.3952 | 1218492.807 | 2721179.5298 | 1218495.0948 | 2721183.9649 | 1218497.1964
36 | 2720808.5191 | 1218383.7516 | 2720849.2665 | 1218530.924
37 | 2720813.9279 | 1218380.2799 | 2720812.8096 | 1218381.1933 | 2720808.5191 | 1218383.7516
38 | 2720814.1535 | 1218360.2377 | 2720822.3633 | 1218364.9745 | 2720823.3867 | 1218368.4201 | 2720822.4632 | 1218372.0264 | 2720819.5185 | 1218375.714 | 2720813.9279 | 1218380.2799
39 | 2721174.6932 | 1218489.1474 | 2721168.9292 | 1218486.239 | 2721166.8889 | 1218482.7837 | 2721164.2864 | 1218478.9723 | 2721164.1582 | 1218476.6902 | 2721165.6185 | 1218472.461 | 2721170.0412 | 1218465.5456 | 2721172.5931 | 1218460.6493 | 2721173.3282 | 1218458.1067 | 2721174.2246 | 1218450.6191 | 2721173.8395 | 1218441.5598 | 2721177.2325 | 1218431.8991 | 2721178.3796 | 1218428.5087 | 2721178.218 | 1218425.2585 | 2721177.5372 | 1218422.5203 | 2721173.8298 | 1218419.6538 | 2721166.3389 | 1218417.2885 | 2721163.5874 | 1218417.1737
40 | 2721346.9994 | 1218518.0392 | 2721342.9617 | 1218513.5684 | 2721325.4515 | 1218482.0319 | 2721316.1336 | 1218463.5167 | 2721310.9684 | 1218447.9884 | 2721306.0518 | 1218437.0242 | 2721301.6436 | 1218432.0417 | 2721297.0989 | 1218428.5354 | 2721293.0573 | 1218426.0664
41 | 2721132.5268 | 1218081.2187 | 2721143.1693 | 1218102.9853 | 2721160.9666 | 1218132.0807
42 | 2721132.5268 | 1218081.2187 | 2721125.06 | 1218081.3782 | 2721109.6161 | 1218081.879
43 | 2721132.5268 | 1218081.2187 | 2721138.921 | 1218078.9247 | 2721149.7538 | 1218073.84
44 | 2721468.4673 | 1218856.2916 | 2721474.599 | 1218857.1506 | 2721481.8949 | 1218859.0008 | 2721490.9404 | 1218863.2774 | 2721500.3642 | 1218869.1074 | 2721504.82 | 1218873.2237 | 2721506.9192 | 1218877.1251 | 2721507.7888 | 1218881.7576 | 2721508.0784 | 1218886.9119 | 2721508.8663 | 1218892.1987 | 2721510.284 | 1218894.8964 | 2721512.6999 | 1218897.4143 | 2721515.744 | 1218899.6559 | 2721518.1591 | 1218900.3502 | 2721521.6977 | 1218900.6781 | 2721525.7024 | 1218899.748 | 2721528.5328 | 1218897.9488 | 2721537.3189 | 1218889.6438 | 2721540.0981 | 1218885.5195 | 2721541.4873 | 1218882.1785 | 2721542.3984 | 1218878.8279 | 2721543.5304 | 1218873.5802 | 2721543.9801 | 1218867.5403 | 2721543.79 | 1218863.4665 | 2721543.2811 | 1218859.3863 | 2721541.0229 | 1218852.4905 | 2721537.9047 | 1218847.1894 | 2721529.0425 | 1218835.7887 | 2721520.5928 | 1218825.753 | 2721510.366 | 1218815.3697 | 2721477.4769 | 1218787.5441
45 | 2721477.4769 | 1218787.5441 | 2721492.0763 | 1218789.3877 | 2721495.4512 | 1218788.8116 | 2721496.9928 | 1218788.0424 | 2721500.3566 | 1218782.0619 | 2721504.2589 | 1218778.2039
46 | 2721289.3805 | 1218688.5242 | 2721275.7361 | 1218675.9367 | 2721266.6111 | 1218669.9464
47 | 2720814.1535 | 1218360.2377 | 2720807.3075 | 1218358.631 | 2720797.3972 | 1218357.526
48 | 2720814.1535 | 1218360.2377 | 2720983.8018 | 1218161.9485
49 | 2721073.8937 | 1218089.2479 | 2721072.1304 | 1218090.7654 | 2721068.4076 | 1218096.483 | 2721057.316 | 1218120.3206 | 2721055.5223 | 1218125.2657 | 2721053.3579 | 1218129.0247 | 2721048.9284 | 1218133.2824 | 2721026.4418 | 1218148.8377 | 2721019.3326 | 1218152.6963 | 2721010.647 | 1218156.0447 | 2721000.9728 | 1218159.0951 | 2720993.0438 | 1218161.0801 | 2720986.4896 | 1218161.9143 | 2720983.8018 | 1218161.9485
50 | 2721109.6161 | 1218081.879 | 2721094.5021 | 1218082.369 | 2721079.9388 | 1218085.7535 | 2721075.6775 | 1218087.7129 | 2721073.8937 | 1218089.2479
51 | 2721468.4673 | 1218856.2916 | 2721454.8228 | 1218843.0031 | 2721465.61 | 1218841.5441 | 2721465.0137 | 1218839.1412
52 | 2721420.2986 | 1218857.7442 | 2721435.3926 | 1218857.6629 | 2721468.4673 | 1218856.2916
53 | 2721506.8623 | 1218776.422 | 2721505.1062 | 1218777.3662 | 2721504.2589 | 1218778.2039
54 | 2721149.7538 | 1218073.84 | 2721181.8314 | 1218021.6418
55 | 2721161.9705 | 1217996.5519 | 2721160.5068 | 1218001.6927 | 2721156.7711 | 1218009.534 | 2721150.5792 | 1218016.4356 | 2721149.4804 | 1218018.5705 | 2721149.6811 | 1218019.1528 | 2721150.5003 | 1218020.3148 | 2721181.8314 | 1218021.6418
56 | 2721161.9705 | 1217996.5519 | 2721171.5959 | 1217997.0368 | 2721186.0089 | 1217992.0928 | 2721197.069 | 1217986.0792
57 | 2721569.1744 | 1218781.4096 | 2721557.0707 | 1218784.1314 | 2721548.6683 | 1218784.4158 | 2721541.2136 | 1218783.652 | 2721530.8755 | 1218781.6952 | 2721518.6808 | 1218777.3431 | 2721513.7597 | 1218775.5635 | 2721508.6525 | 1218775.4593 | 2721506.8623 | 1218776.422
58 | 2721420.2986 | 1218857.7442 | 2721438.0641 | 1218870.7275 | 2721449.0475 | 1218876.0221 | 2721458.7757 | 1218879.2118 | 2721464.4968 | 1218880.1069 | 2721468.3402 | 1218880.0509
59 | 2721347.147 | 1218839.3952 | 2721340.8124 | 1218831.7269 | 2721337.2591 | 1218825.7833 | 2721340.5375 | 1218827.7071 | 2721344.9711 | 1218830.3105 | 2721351.7102 | 1218832.6607 | 2721356.3526 | 1218833.5893 | 2721360.9877 | 1218834.5067 | 2721365.7929 | 1218834.8937 | 2721369.3675 | 1218836.0675 | 2721372.1255 | 1218838.192 | 2721375.5887 | 1218841.4762 | 2721386.9838 | 1218854.8854 | 2721389.9267 | 1218857.6253 | 2721392.8302 | 1218858.941 | 2721395.7691 | 1218859.2678 | 2721401.9069 | 1218858.7146 | 2721413.678 | 1218857.776 | 2721420.2986 | 1218857.7442
60 | 2721347.147 | 1218839.3952 | 2721348.2974 | 1218842.9214 | 2721347.9761 | 1218846.3953 | 2721345.01 | 1218865.9352
61 | 2721347.147 | 1218839.3952 | 2721356.0068 | 1218842.7338
62 | 2721282.4182 | 1218829.7921 | 2721279.8957 | 1218826.5382 | 2721274.2326 | 1218823.5428 | 2721265.0313 | 1218818.3293 | 2721252.2882 | 1218811.0754 | 2721249.2143 | 1218806.5649 | 2721223.1099 | 1218801.541 | 2721220.3525 | 1218798.2601 | 2721237.1795 | 1218796.5901 | 2721251.5234 | 1218796.8155 | 2721279.0963 | 1218798.7003 | 2721294.4952 | 1218801.1713 | 2721306.6376 | 1218804.7435 | 2721313.4815 | 1218807.5405 | 2721319.2177 | 1218811.0489 | 2721325.9254 | 1218817.1792 | 2721331.6967 | 1218821.9448 | 2721337.2591 | 1218825.7833 | 2721340.8124 | 1218831.7269 | 2721347.147 | 1218839.3952
63 | 2721292.7873 | 1218833.9508 | 2721290.9614 | 1218830.0439 | 2721282.4182 | 1218829.7921
64 | 2721125.7088 | 1218828.3475 | 2721140.4785 | 1218838.2333 | 2721156.1361 | 1218849.6271 | 2721167.4719 | 1218857.0189 | 2721172.8854 | 1218858.1076 | 2721179.7554 | 1218862.6064 | 2721187.5183 | 1218863.5206 | 2721198.2478 | 1218861.1592 | 2721216.0713 | 1218851.1807 | 2721221.3317 | 1218851.588 | 2721270.1152 | 1218864.6687 | 2721273.8488 | 1218864.7447 | 2721276.4841 | 1218862.8302 | 2721278.4044 | 1218850.9268 | 2721280.5012 | 1218848.9902 | 2721286.5327 | 1218856.263 | 2721284.2207 | 1218835.2219 | 2721282.4182 | 1218829.7921
65 | 2721125.7088 | 1218828.3475 | 2721119.6742 | 1218823.4544 | 2721111.9836 | 1218817.4934 | 2721093.0142 | 1218794.9793 | 2721088.5754 | 1218791.1306 | 2721082.6524 | 1218787.841 | 2721070.909 | 1218783.31 | 2721031.1352 | 1218775.1178 | 2721018.1833 | 1218773.1467
66 | 2720904.4889 | 1218730.6343 | 2720905.252 | 1218732.6847 | 2720905.545 | 1218736.9495 | 2720905.1505 | 1218741.4227 | 2720903.2738 | 1218747.4782 | 2720902.2276 | 1218753.7619 | 2720903.2172 | 1218757.7406 | 2720905.5078 | 1218761.212 | 2720908.9039 | 1218763.327 | 2720914.5283 | 1218764.1306 | 2720939.9448 | 1218763.4237 | 2720997.4861 | 1218769.997 | 2721018.1833 | 1218773.1467
67 | 2720794.0548 | 1218774.5729 | 2720808.1318 | 1218762.8826 | 2720822.901 | 1218753.3747 | 2720828.5827 | 1218751.355 | 2720835.8638 | 1218749.8348 | 2720841.0778 | 1218748.4172 | 2720859.5214 | 1218738.5392 | 2720874.5632 | 1218728.3253 | 2720880.4407 | 1218725.2644 | 2720885.4362 | 1218723.7646 | 2720892.9471 | 1218722.8941 | 2720898.1619 | 1218723.6783 | 2720901.3307 | 1218725.3995 | 2720904.0207 | 1218729.3905 | 2720904.4889 | 1218730.6343
68 | 2720794.0548 | 1218774.5729 | 2720786.0354 | 1218780.2691

## bus_geodata
| x | y | coords
0 | 2721769.1697 | 1218000.5096
1 | 2721826.3577 | 1218070.6996
2 | 2721575.2289 | 1218072.9057
3 | 2721968.9824 | 1218120.6003
4 | 2721487.2329 | 1218119.625
5 | 2721965.6324 | 1218327.1366
6 | 2721991.0886 | 1218333.8629
7 | 2722004.5643 | 1218396.2151
8 | 2721972.0232 | 1218111.5222
9 | 2722034.1388 | 1218239.7898
10 | 2722009.8707 | 1218407.7125
11 | 2721877.4749 | 1218459.2799
12 | 2722010.8345 | 1218418.4329
13 | 2721714.3685 | 1218298.5418
14 | 2721954.2172 | 1218089.7075
15 | 2722046.0973 | 1218248.1834
16 | 2721537 | 1218258.5796
17 | 2721518.3614 | 1218251.0172
18 | 2721335.018 | 1218393.3468
19 | 2721447.7573 | 1218123.7903
20 | 2721313.3348 | 1218391.8375
21 | 2721263.8378 | 1218417.8751
22 | 2721300.0814 | 1218368.9722
23 | 2721302.5545 | 1218398.5318
24 | 2721255.6283 | 1218423.0315
25 | 2721220.8233 | 1218524.9436
26 | 2721245.7474 | 1218529.2272
27 | 2721254.0889 | 1218531.8556
28 | 2721270.8433 | 1218534.85
29 | 2721458.3661 | 1218774.2553
30 | 2721183.9649 | 1218497.1964
31 | 2720849.2665 | 1218530.924
32 | 2720808.5191 | 1218383.7516
33 | 2720813.9279 | 1218380.2799
34 | 2721174.6932 | 1218489.1474
35 | 2721293.0573 | 1218426.0664
36 | 2721163.5874 | 1218417.1737
37 | 2721346.9994 | 1218518.0392
38 | 2721160.9666 | 1218132.0807
39 | 2721132.5268 | 1218081.2187
40 | 2721485.4101 | 1218732.8634
41 | 2721477.4769 | 1218787.5441
42 | 2721289.3805 | 1218688.5242
43 | 2720814.1535 | 1218360.2377
44 | 2720797.3972 | 1218357.526
45 | 2720983.8018 | 1218161.9485
46 | 2721109.6161 | 1218081.879
47 | 2721073.8937 | 1218089.2479
48 | 2721468.4673 | 1218856.2916
49 | 2721504.2589 | 1218778.2039
50 | 2721266.6111 | 1218669.9464
51 | 2721149.7538 | 1218073.84
52 | 2721181.8314 | 1218021.6418
53 | 2721197.069 | 1217986.0792
54 | 2721161.9705 | 1217996.5519
55 | 2721506.8623 | 1218776.422
56 | 2721569.1744 | 1218781.4096
57 | 2721465.0137 | 1218839.1412
58 | 2721420.2986 | 1218857.7442
59 | 2721345.01 | 1218865.9352
60 | 2721347.147 | 1218839.3952
61 | 2721356.0068 | 1218842.7338
62 | 2721282.4182 | 1218829.7921
63 | 2721125.7088 | 1218828.3475
64 | 2721018.1833 | 1218773.1467
65 | 2721292.7873 | 1218833.9508
66 | 2721468.3402 | 1218880.0509
67 | 2720904.4889 | 1218730.6343
68 | 2720786.0354 | 1218780.2691
69 | 2720794.0548 | 1218774.5729
70 | 2721537 | 1218258.5796

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99802 | -0.038361 | 0.00049537 | 0.00012415
1 | 0.99774 | -0.043737 | 0 | 0
2 | 0.99869 | -0.025433 | 0 | 0
3 | 0.9971 | -0.056134 | 0 | 0
4 | 0.99904 | -0.018618 | 0 | 0
5 | 0.99575 | -0.081878 | 0 | 0
6 | 0.99574 | -0.082087 | 0.00044857 | 0.00011242
7 | 0.99578 | -0.081246 | 0.00054985 | 0.00013781
8 | 0.99708 | -0.056449 | 0 | 0
9 | 0.99695 | -0.059119 | 0.00065118 | 0.0001632
10 | 0.99579 | -0.081023 | 0.00049595 | 0.0001243
11 | 0.99677 | -0.062217 | 0.00032281 | 8.0904e-05
12 | 0.99581 | -0.080737 | 0.0060609 | 0.001519
13 | 0.99855 | -0.027872 | 0.00026058 | 6.5308e-05
14 | 0.99703 | -0.057404 | 0.0018718 | 0.00046911
15 | 0.99694 | -0.05926 | 0.0005318 | 0.00013328
16 | 1 | 0 | -0.032158 | -0.0076239
17 | 0.99959 | -0.0078571 | 0 | 0
18 | 0.99564 | -0.08443 | 0 | 0
19 | 0.99901 | -0.019084 | 0.00066894 | 0.00016765
20 | 0.99544 | -0.088327 | 0 | 0
21 | 0.99509 | -0.095214 | 0.0005831 | 0.00014614
22 | 0.99523 | -0.092361 | 0.0031619 | 0.00079245
23 | 0.99542 | -0.088673 | 0.0015493 | 0.00038829
24 | 0.99502 | -0.096471 | 0 | 0
25 | 0.99366 | -0.12327 | 0.001478 | 0.00037042
26 | 0.99369 | -0.12261 | 0.00023246 | 5.826e-05
27 | 0.9937 | -0.12235 | 0.00058472 | 0.00014654
28 | 0.99374 | -0.12165 | 0 | 0
29 | 0.99271 | -0.14202 | 0 | 0
30 | 0.99429 | -0.11079 | 0.00029979 | 7.5135e-05
31 | 0.99288 | -0.13807 | 0.00028238 | 7.077e-05
32 | 0.99292 | -0.1373 | 0.00030313 | 7.5971e-05
33 | 0.99293 | -0.13724 | 0.00042169 | 0.00010568
34 | 0.99436 | -0.10942 | 0 | 0
35 | 0.995 | -0.096999 | 0.00039096 | 9.7983e-05
36 | 0.99432 | -0.11022 | 0.00050306 | 0.00012608
37 | 0.99496 | -0.097712 | 0.00037168 | 9.3151e-05
38 | 0.99386 | -0.11902 | 0.00066195 | 0.0001659
39 | 0.9936 | -0.124 | 0 | 0
40 | 0.99269 | -0.14248 | 0.00028425 | 7.124e-05
41 | 0.99265 | -0.14314 | 0 | 0
42 | 0.99263 | -0.14353 | 0 | 0
43 | 0.99295 | -0.13672 | 0 | 0
44 | 0.99295 | -0.13685 | 0.00042291 | 0.00010599
45 | 0.99329 | -0.13008 | 0.00022717 | 5.6934e-05
46 | 0.99355 | -0.12502 | 0.00038318 | 9.6034e-05
47 | 0.99348 | -0.12642 | 0.00045519 | 0.00011408
48 | 0.99226 | -0.15095 | 0 | 0
49 | 0.99263 | -0.14358 | 0.00027243 | 6.8277e-05
50 | 0.99262 | -0.14375 | 0.00041934 | 0.0001051
51 | 0.99356 | -0.12477 | 0.0013881 | 0.00034789
52 | 0.99351 | -0.12578 | 0.00046457 | 0.00011643
53 | 0.99347 | -0.12658 | 0.00046373 | 0.00011622
54 | 0.99349 | -0.12627 | 0 | 0
55 | 0.99263 | -0.14361 | 0.00023725 | 5.946e-05
56 | 0.99261 | -0.1439 | 0.00026 | 6.5161e-05
57 | 0.99225 | -0.15107 | 0.00021614 | 5.4171e-05
58 | 0.99219 | -0.15242 | 0 | 0
59 | 0.99204 | -0.15536 | 0.00026015 | 6.52e-05
60 | 0.99204 | -0.15523 | 0 | 0
61 | 0.99204 | -0.15529 | 0.00033984 | 8.5172e-05
62 | 0.99189 | -0.15832 | 0 | 0
63 | 0.99178 | -0.16065 | 0 | 0
64 | 0.99171 | -0.16198 | 0.00021486 | 5.3849e-05
65 | 0.99189 | -0.15837 | 0.00020796 | 5.2119e-05
66 | 0.99217 | -0.1527 | 0.00029714 | 7.4471e-05
67 | 0.99166 | -0.16295 | 0 | 0
68 | 0.99161 | -0.16386 | 0.00037 | 9.273e-05
69 | 0.99162 | -0.1638 | 0 | 0
70 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0030576 | 0.00076053 | -0.0030568 | -0.00076134 | 7.7884e-07 | -8.0808e-07 | 0.0045568 | 0.0045572 | 0.0045572 | 0.99802 | -0.038361 | 0.99774 | -0.043737 | 1.252
1 | -0.003553 | -0.00088468 | 0.0035552 | 0.00088337 | 2.1764e-06 | -1.314e-06 | 0.0052954 | 0.0052944 | 0.0052954 | 0.99802 | -0.038361 | 0.99869 | -0.025433 | 1.4548
2 | 0.0030568 | 0.00076134 | -0.003055 | -0.0007632 | 1.7983e-06 | -1.862e-06 | 0.0045572 | 0.0045583 | 0.0045583 | 0.99774 | -0.043737 | 0.9971 | -0.056134 | 1.2523
3 | -0.0035552 | -0.00088337 | 0.0035563 | 0.00088268 | 1.1465e-06 | -6.9404e-07 | 0.0052944 | 0.0052939 | 0.0052944 | 0.99869 | -0.025433 | 0.99904 | -0.018618 | 1.4545
4 | 0.0018719 | 0.00046868 | -0.0018719 | -0.00046879 | 2.813e-08 | -1.0739e-07 | 0.0027933 | 0.0027934 | 0.0027934 | 0.9971 | -0.056134 | 0.99708 | -0.056449 | 0.76741
5 | 0.0011831 | 0.00029452 | -0.001183 | -0.00029629 | 1.6777e-07 | -1.7649e-06 | 0.001765 | 0.0017656 | 0.0017656 | 0.9971 | -0.056134 | 0.99695 | -0.059119 | 0.48506
6 | 0.00066895 | 0.00016714 | -0.00066894 | -0.00016765 | 1.4835e-08 | -5.1237e-07 | 0.00099619 | 0.00099637 | 0.00099637 | 0.99904 | -0.018618 | 0.99901 | -0.019084 | 0.27373
7 | -0.0042253 | -0.0010498 | 0.0042274 | 0.0010493 | 2.1516e-06 | -5.2306e-07 | 0.0062901 | 0.0062895 | 0.0062901 | 0.99904 | -0.018618 | 0.99959 | -0.0078571 | 1.7281
8 | 0.00044858 | 0.00011208 | -0.00044857 | -0.00011242 | 4.4785e-09 | -3.4291e-07 | 0.00067022 | 0.00067034 | 0.00067034 | 0.99575 | -0.081878 | 0.99574 | -0.082087 | 0.18416
9 | -0.00044858 | -0.00011208 | 0.00044859 | 0.00011105 | 1.341e-08 | -1.0276e-06 | 0.00067022 | 0.00066986 | 0.00067022 | 0.99575 | -0.081878 | 0.99578 | -0.081246 | 0.18413
10 | -0.00099844 | -0.00024886 | 0.00099845 | 0.0002487 | 1.0571e-08 | -1.5809e-07 | 0.0014915 | 0.0014914 | 0.0014915 | 0.99578 | -0.081246 | 0.99579 | -0.081023 | 0.40975
11 | 0.0018719 | 0.00046879 | -0.0018718 | -0.00046911 | 8.5119e-08 | -3.249e-07 | 0.0027934 | 0.0027935 | 0.0027935 | 0.99708 | -0.056449 | 0.99703 | -0.057404 | 0.76745
12 | 0.0005318 | 0.00013309 | -0.0005318 | -0.00013328 | 3.5652e-09 | -1.945e-07 | 0.00079368 | 0.00079375 | 0.00079375 | 0.99695 | -0.059119 | 0.99694 | -0.05926 | 0.21806
13 | -0.0014944 | -0.000373 | 0.0014944 | 0.00037287 | 2.0275e-08 | -1.2815e-07 | 0.0022325 | 0.0022325 | 0.0022325 | 0.99579 | -0.081023 | 0.99581 | -0.080737 | 0.61334
14 | 0.007562 | 0.0018943 | -0.0075553 | -0.0018919 | 6.6654e-06 | 2.4496e-06 | 0.011289 | 0.011289 | 0.011289 | 0.99677 | -0.062217 | 0.99581 | -0.080737 | 3.1014
15 | -0.0078848 | -0.0019752 | 0.0078977 | 0.0019802 | 1.2912e-05 | 5.0179e-06 | 0.01177 | 0.011769 | 0.01177 | 0.99677 | -0.062217 | 0.99855 | -0.027872 | 3.2336
16 | -0.0081583 | -0.0020455 | 0.0081691 | 0.0020499 | 1.0847e-05 | 4.3781e-06 | 0.012158 | 0.012157 | 0.012158 | 0.99855 | -0.027872 | 1 | 0 | 3.34
17 | 0.022339 | 0.0055739 | -0.022331 | -0.0055688 | 8.3302e-06 | 5.0675e-06 | 0.033232 | 0.033232 | 0.033232 | 1 | 0 | 0.99959 | -0.0078571 | 9.1297
18 | 0.018103 | 0.0045195 | -0.018038 | -0.0044807 | 6.5601e-05 | 3.8838e-05 | 0.026943 | 0.026944 | 0.026944 | 0.99959 | -0.0078571 | 0.99564 | -0.08443 | 7.4021
19 | 0.010198 | 0.002545 | -0.010196 | -0.0025441 | 1.8869e-06 | 9.2585e-07 | 0.015237 | 0.015238 | 0.015238 | 0.99564 | -0.08443 | 0.99544 | -0.088327 | 4.1861
20 | 0.0078396 | 0.0019356 | -0.0078356 | -0.0019341 | 3.9808e-06 | 1.5409e-06 | 0.011706 | 0.011707 | 0.011707 | 0.99564 | -0.08443 | 0.99509 | -0.095214 | 3.2161
21 | 0.0086468 | 0.002156 | -0.0086451 | -0.0021553 | 1.6548e-06 | 7.1557e-07 | 0.012922 | 0.012922 | 0.012922 | 0.99544 | -0.088327 | 0.99523 | -0.092361 | 3.5499
22 | 0.0015493 | 0.00038814 | -0.0015493 | -0.00038829 | 2.5523e-08 | -1.4863e-07 | 0.0023159 | 0.002316 | 0.002316 | 0.99544 | -0.088327 | 0.99542 | -0.088673 | 0.63625
23 | 0.0072525 | 0.0017879 | -0.0072521 | -0.0017878 | 4.2905e-07 | 1.4799e-07 | 0.010835 | 0.010835 | 0.010835 | 0.99509 | -0.095214 | 0.99502 | -0.096471 | 2.9766
24 | 0.0054832 | 0.0013628 | -0.0054763 | -0.0013619 | 6.9183e-06 | 8.6281e-07 | 0.0081942 | 0.0081955 | 0.0081955 | 0.99523 | -0.092361 | 0.99386 | -0.11902 | 2.2515
25 | 0.0064894 | 0.0015985 | -0.0064855 | -0.0015975 | 3.9509e-06 | 1.0736e-06 | 0.0096949 | 0.0096954 | 0.0096954 | 0.99502 | -0.096471 | 0.99436 | -0.10942 | 2.6636
26 | 0.00076267 | 0.00018924 | -0.00076265 | -0.00018973 | 1.9069e-08 | -4.9606e-07 | 0.0011399 | 0.00114 | 0.00114 | 0.99502 | -0.096471 | 0.995 | -0.096999 | 0.3132
27 | -0.001478 | -0.00037042 | 0.001478 | 0.00037012 | 4.6454e-08 | -2.9786e-07 | 0.0022133 | 0.0022132 | 0.0022133 | 0.99366 | -0.12327 | 0.99369 | -0.12261 | 0.60805
28 | -0.0017105 | -0.00042838 | 0.0017105 | 0.00042828 | 2.1597e-08 | -9.9906e-08 | 0.0025613 | 0.0025612 | 0.0025613 | 0.99369 | -0.12261 | 0.9937 | -0.12235 | 0.70365
29 | -0.0022952 | -0.00057482 | 0.0022953 | 0.00057465 | 7.606e-08 | -1.7378e-07 | 0.0034368 | 0.0034367 | 0.0034368 | 0.9937 | -0.12235 | 0.99374 | -0.12165 | 0.94418
30 | 0.003384 | 0.00082222 | -0.0033808 | -0.0008245 | 3.2116e-06 | -2.2755e-06 | 0.0050582 | 0.0050597 | 0.0050597 | 0.99374 | -0.12165 | 0.99271 | -0.14202 | 1.39
31 | -0.0056793 | -0.0013969 | 0.0056822 | 0.0013973 | 2.8975e-06 | 4.6637e-07 | 0.0084949 | 0.0084944 | 0.0084949 | 0.99374 | -0.12165 | 0.99429 | -0.11079 | 2.3338
32 | 0.00028426 | 7.0049e-05 | -0.00028425 | -7.124e-05 | 6.2861e-09 | -1.1909e-06 | 0.00042567 | 0.00042608 | 0.00042608 | 0.99271 | -0.14202 | 0.99269 | -0.14248 | 0.11706
33 | 0.0026772 | 0.00065233 | -0.002677 | -0.00065254 | 1.4029e-07 | -2.1151e-07 | 0.0040064 | 0.0040065 | 0.0040065 | 0.99271 | -0.14202 | 0.99265 | -0.14314 | 1.1007
34 | 0.00041937 | 0.00010212 | -0.00041934 | -0.00010472 | 2.9945e-08 | -2.5982e-06 | 0.00062757 | 0.00062849 | 0.00062849 | 0.99271 | -0.14202 | 0.99263 | -0.14353 | 0.17266
35 | -0.005982 | -0.0014725 | 0.0059824 | 0.0014725 | 3.8463e-07 | 7.9817e-08 | 0.008943 | 0.008943 | 0.008943 | 0.99429 | -0.11079 | 0.99436 | -0.10942 | 2.4569
36 | -0.00028238 | -7.077e-05 | 0.00028239 | 6.8802e-05 | 1.0239e-08 | -1.9686e-06 | 0.00042319 | 0.0004225 | 0.00042319 | 0.99288 | -0.13807 | 0.99292 | -0.1373 | 0.11626
37 | -0.00058551 | -0.00014477 | 0.00058552 | 0.00014469 | 1.8562e-09 | -8.2099e-08 | 0.00087677 | 0.00087674 | 0.00087677 | 0.99292 | -0.1373 | 0.99293 | -0.13724 | 0.24087
38 | -0.0010072 | -0.00025037 | 0.0010072 | 0.00025002 | 2.4523e-08 | -3.5595e-07 | 0.0015087 | 0.0015086 | 0.0015087 | 0.99293 | -0.13724 | 0.99295 | -0.13672 | 0.41447
39 | 0.00050308 | 0.00012492 | -0.00050306 | -0.00012608 | 1.9122e-08 | -1.1554e-06 | 0.00075243 | 0.00075284 | 0.00075284 | 0.99436 | -0.10942 | 0.99432 | -0.11022 | 0.20682
40 | 0.00037169 | 9.1752e-05 | -0.00037168 | -9.3151e-05 | 1.2541e-08 | -1.399e-06 | 0.00055537 | 0.00055586 | 0.00055586 | 0.995 | -0.096999 | 0.99496 | -0.097712 | 0.15271
41 | 0.0048143 | 0.001196 | -0.0048132 | -0.0011961 | 1.1348e-06 | -2.9043e-08 | 0.0072044 | 0.0072046 | 0.0072046 | 0.99386 | -0.11902 | 0.9936 | -0.124 | 1.9793
42 | 0.0024967 | 0.00061772 | -0.0024965 | -0.00061794 | 1.1998e-07 | -2.2006e-07 | 0.0037362 | 0.0037363 | 0.0037363 | 0.9936 | -0.124 | 0.99355 | -0.12502 | 1.0265
43 | 0.0023165 | 0.00057835 | -0.0023165 | -0.00057854 | 8.4634e-08 | -1.888e-07 | 0.0034685 | 0.0034685 | 0.0034685 | 0.9936 | -0.124 | 0.99356 | -0.12477 | 0.9529
44 | 0.0019073 | 0.00046091 | -0.0019066 | -0.0004634 | 6.9161e-07 | -2.4838e-06 | 0.0028532 | 0.0028542 | 0.0028542 | 0.99265 | -0.14314 | 0.99226 | -0.15095 | 0.78413
45 | 0.00076969 | 0.00019162 | -0.00076968 | -0.00019203 | 1.607e-08 | -4.0611e-07 | 0.0011533 | 0.0011535 | 0.0011535 | 0.99265 | -0.14314 | 0.99263 | -0.14358 | 0.31689
46 | 0.00041934 | 0.00010472 | -0.00041934 | -0.0001051 | 4.3599e-09 | -3.7761e-07 | 0.00062849 | 0.00062862 | 0.00062862 | 0.99263 | -0.14353 | 0.99262 | -0.14375 | 0.1727
47 | 0.00042291 | 0.00010577 | -0.00042291 | -0.00010599 | 2.5608e-09 | -2.183e-07 | 0.00063369 | 0.00063377 | 0.00063377 | 0.99295 | -0.13672 | 0.99295 | -0.13685 | 0.17411
48 | -0.0014301 | -0.00035579 | 0.0014306 | 0.0003527 | 4.4885e-07 | -3.0894e-06 | 0.0021422 | 0.0021411 | 0.0021422 | 0.99295 | -0.13672 | 0.99329 | -0.13008 | 0.58853
49 | -0.0016578 | -0.00040964 | 0.001658 | 0.00040822 | 2.8517e-07 | -1.4168e-06 | 0.0024814 | 0.0024808 | 0.0024814 | 0.99329 | -0.13008 | 0.99348 | -0.12642 | 0.6817
50 | 0.0021134 | 0.00052191 | -0.0021132 | -0.0005223 | 1.3921e-07 | -3.9156e-07 | 0.0031624 | 0.0031626 | 0.0031626 | 0.99355 | -0.12502 | 0.99348 | -0.12642 | 0.86884
51 | 0.00021614 | 5.3753e-05 | -0.00021614 | -5.417e-05 | 1.2739e-09 | -4.1702e-07 | 0.00032399 | 0.00032414 | 0.00032414 | 0.99226 | -0.15095 | 0.99225 | -0.15107 | 0.089048
52 | 0.0016905 | 0.00040965 | -0.0016904 | -0.00041019 | 1.1572e-07 | -5.4846e-07 | 0.0025302 | 0.0025304 | 0.0025304 | 0.99226 | -0.15095 | 0.99219 | -0.15242 | 0.69518
53 | 0.00049725 | 0.00012375 | -0.00049725 | -0.00012379 | 6.6316e-10 | -4.075e-08 | 0.0007451 | 0.00074512 | 0.00074512 | 0.99263 | -0.14358 | 0.99263 | -0.14361 | 0.2047
54 | 0.00092836 | 0.00023065 | -0.00092832 | -0.00023142 | 4.4377e-08 | -7.6502e-07 | 0.0013897 | 0.0013899 | 0.0013899 | 0.99356 | -0.12477 | 0.99351 | -0.12578 | 0.38185
55 | 0.00046375 | 0.00011498 | -0.00046374 | -0.00011574 | 1.0663e-08 | -7.5711e-07 | 0.00069413 | 0.0006944 | 0.0006944 | 0.99351 | -0.12578 | 0.99349 | -0.12627 | 0.19077
56 | -0.00046373 | -0.00011622 | 0.00046374 | 0.00011574 | 6.776e-09 | -4.8078e-07 | 0.00069457 | 0.0006944 | 0.00069457 | 0.99347 | -0.12658 | 0.99349 | -0.12627 | 0.19082
57 | 0.00026 | 6.4334e-05 | -0.00026 | -6.5161e-05 | 3.6517e-09 | -8.269e-07 | 0.00038947 | 0.00038976 | 0.00038976 | 0.99263 | -0.14361 | 0.99261 | -0.1439 | 0.10708
58 | 0.00029715 | 7.3775e-05 | -0.00029714 | -7.4471e-05 | 4.0245e-09 | -6.9572e-07 | 0.0004454 | 0.00044564 | 0.00044564 | 0.99219 | -0.15242 | 0.99217 | -0.1527 | 0.12243
59 | 0.0013932 | 0.00033642 | -0.0013931 | -0.00033774 | 1.8199e-07 | -1.3247e-06 | 0.0020851 | 0.0020856 | 0.0020856 | 0.99219 | -0.15242 | 0.99204 | -0.15523 | 0.57295
60 | -0.00026015 | -6.52e-05 | 0.00026015 | 6.4853e-05 | 1.5391e-09 | -3.4712e-07 | 0.00039022 | 0.00039009 | 0.00039022 | 0.99204 | -0.15536 | 0.99204 | -0.15523 | 0.1072
61 | 0.00033984 | 8.5051e-05 | -0.00033984 | -8.5172e-05 | 9.2016e-10 | -1.2135e-07 | 0.0005097 | 0.00050975 | 0.00050975 | 0.99204 | -0.15523 | 0.99204 | -0.15529 | 0.14004
62 | 0.00079306 | 0.00018784 | -0.00079295 | -0.00019052 | 1.1269e-07 | -2.6847e-06 | 0.0011858 | 0.0011867 | 0.0011867 | 0.99204 | -0.15523 | 0.99189 | -0.15832 | 0.32602
63 | 0.00020796 | 5.1954e-05 | -0.00020796 | -5.2119e-05 | 4.683e-10 | -1.6534e-07 | 0.00031192 | 0.00031198 | 0.00031198 | 0.99189 | -0.15832 | 0.99189 | -0.15837 | 0.085708
64 | 0.00058499 | 0.00013857 | -0.00058493 | -0.00014134 | 6.2534e-08 | -2.769e-06 | 0.00087482 | 0.00087577 | 0.00087577 | 0.99189 | -0.15832 | 0.99178 | -0.16065 | 0.2406
65 | 0.00058493 | 0.00014134 | -0.00058489 | -0.00014294 | 3.623e-08 | -1.6012e-06 | 0.00087577 | 0.00087633 | 0.00087633 | 0.99178 | -0.16065 | 0.99171 | -0.16198 | 0.24075
66 | 0.00037003 | 8.9091e-05 | -0.00037001 | -9.0962e-05 | 1.6807e-08 | -1.8714e-06 | 0.00055395 | 0.0005546 | 0.0005546 | 0.99171 | -0.16198 | 0.99166 | -0.16295 | 0.15236
67 | 0.00037001 | 9.0962e-05 | -0.00037 | -9.2604e-05 | 1.4778e-08 | -1.6418e-06 | 0.0005546 | 0.00055518 | 0.00055518 | 0.99166 | -0.16295 | 0.99162 | -0.1638 | 0.15252
68 | -0.00037 | -9.273e-05 | 0.00037 | 9.2604e-05 | 1.137e-09 | -1.2617e-07 | 0.00055522 | 0.00055518 | 0.00055522 | 0.99161 | -0.16386 | 0.99162 | -0.1638 | 0.15253

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.03283 | 0.0077923

## res_load
| p_mw | q_mvar
0 | 0.00049537 | 0.00012415
1 | 0.00044857 | 0.00011242
2 | 0.00054985 | 0.00013781
3 | 0.00065118 | 0.0001632
4 | 0.00049595 | 0.0001243
5 | 0.00032281 | 8.0904e-05
6 | 0.0060609 | 0.001519
7 | 0.00026058 | 6.5308e-05
8 | 0.0018718 | 0.00046911
9 | 0.0005318 | 0.00013328
10 | 0.00067175 | 0.00016836
11 | 0.00066894 | 0.00016765
12 | 0.0005831 | 0.00014614
13 | 0.0031619 | 0.00079245
14 | 0.0015493 | 0.00038829
15 | 0.001478 | 0.00037042
16 | 0.00023246 | 5.826e-05
17 | 0.00058472 | 0.00014654
18 | 0.00029979 | 7.5135e-05
19 | 0.00028238 | 7.077e-05
20 | 0.00030313 | 7.5971e-05
21 | 0.00042169 | 0.00010568
22 | 0.00039096 | 9.7983e-05
23 | 0.00050306 | 0.00012608
24 | 0.00037168 | 9.3151e-05
25 | 0.00066195 | 0.0001659
26 | 0.00028425 | 7.124e-05
27 | 0.00042291 | 0.00010599
28 | 0.00022717 | 5.6934e-05
29 | 0.00038318 | 9.6034e-05
30 | 0.00045519 | 0.00011408
31 | 0.00027243 | 6.8277e-05
32 | 0.00041934 | 0.0001051
33 | 0.0013881 | 0.00034789
34 | 0.00046457 | 0.00011643
35 | 0.00046373 | 0.00011622
36 | 0.00023725 | 5.946e-05
37 | 0.00026 | 6.5161e-05
38 | 0.00021614 | 5.4171e-05
39 | 0.00026015 | 6.52e-05
40 | 0.00033984 | 8.5172e-05
41 | 0.00021486 | 5.3849e-05
42 | 0.00020796 | 5.2119e-05
43 | 0.00029714 | 7.4471e-05
44 | 0.00037 | 9.273e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1