## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-142_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-142_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-142_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-142_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-142_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1630-142_0_5_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_1630-142_0_5_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1630-142_0_5_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1630-142_0_5_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_1630-142_0_5_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_1630-142_0_5_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1630-142_0_5_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_1630-142_0_5_node_41 | 0.4 | n |  | TRUE
13 | bus_LV_1630-142_0_5_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1630-142_0_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1630-142_0_5_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1630-142_0_5_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1630-142_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1630-142_0_5_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_1630-142_0_5_node_42 | 0.4 | n |  | TRUE
20 | bus_LV_1630-142_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1630-142_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1630-142_0_5_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_1630-142_0_5_node_39 | 0.4 | n |  | TRUE
24 | bus_LV_1630-142_0_5_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1630-142_0_5_node_44 | 0.4 | n |  | TRUE
26 | bus_LV_1630-142_0_5_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1630-142_0_5_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_1630-142_0_5_node_36 | 0.4 | n |  | TRUE
29 | bus_LV_1630-142_0_5_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1630-142_0_5_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1630-142_0_5_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1630-142_0_5_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1630-142_0_5_node_40 | 0.4 | n |  | TRUE
34 | bus_LV_1630-142_0_5_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1630-142_0_5_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_1630-142_0_5_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1630-142_0_5_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_1630-142_0_5_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1630-142_0_5_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_1630-142_0_5_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1630-142_0_5_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_1630-142_0_5_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1630-142_0_5_node_45 | 0.4 | n |  | TRUE
44 | bus_MV_20_1_node_135 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-142_0_5_load_0 | 0 | 0.026235 | 0.0065751 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-142_0_5_load_1 | 1 | 0.02621 | 0.006569 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-142_0_5_load_3 | 3 | 0.00295 | 0.00073934 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-142_0_5_load_19 | 5 | 0.021237 | 0.0053226 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-142_0_5_load_18 | 9 | 0.01271 | 0.0031855 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-142_0_5_load_30 | 11 | 0.0076812 | 0.0019251 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-142_0_5_load_41 | 12 | 0.021618 | 0.0054181 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-142_0_5_load_17 | 13 | 0.017779 | 0.0044557 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-142_0_5_load_6 | 14 | 0.016306 | 0.0040868 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-142_0_5_load_42 | 19 | 0.0016516 | 0.00041393 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-142_0_5_load_34 | 22 | 0.0057477 | 0.0014405 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-142_0_5_load_39 | 23 | 0.0068397 | 0.0017142 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-142_0_5_load_20 | 24 | 0.013261 | 0.0033235 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-142_0_5_load_44 | 25 | 0.0017953 | 0.00044994 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-142_0_5_load_35 | 27 | 0.049187 | 0.012327 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-142_0_5_load_23 | 31 | 0.062662 | 0.015705 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-142_0_5_load_33 | 32 | 0.0099104 | 0.0024838 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-142_0_5_load_40 | 33 | 0.0027142 | 0.00068024 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-142_0_5_load_29 | 34 | 0.026467 | 0.0066332 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-142_0_5_load_21 | 35 | 0.074119 | 0.018576 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-142_0_5_load_22 | 36 | 0.021259 | 0.0053281 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-142_0_5_load_37 | 37 | 0.024789 | 0.0062127 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-142_0_5_load_32 | 40 | 0.0099402 | 0.0024912 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-142_0_5_load_31 | 41 | 0.019387 | 0.0048589 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-142_0_5_load_43 | 42 | 0.0041265 | 0.0010342 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-142_0_5_load_45 | 43 | 0.028746 | 0.0072043 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-142_0_5_line_0 |  | 0 | 1 | 0.021785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-142_0_5_line_1 |  | 0 | 2 | 0.020283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-142_0_5_line_2 |  | 1 | 3 | 0.016583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-142_0_5_line_3 |  | 2 | 4 | 0.011329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-142_0_5_line_4 |  | 3 | 5 | 0.0071405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-142_0_5_line_5 |  | 4 | 8 | 0.017646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-142_0_5_line_6 |  | 4 | 9 | 0.017887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-142_0_5_line_7 |  | 5 | 6 | 0.011732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1630-142_0_5_line_8 |  | 6 | 7 | 0.034921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_1630-142_0_5_line_9 |  | 7 | 10 | 0.050012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_1630-142_0_5_line_10 |  | 7 | 11 | 0.012495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1630-142_0_5_line_11 |  | 8 | 12 | 0.01721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-142_0_5_line_12 |  | 9 | 13 | 0.037441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-142_0_5_line_13 |  | 10 | 24 | 0.017491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1630-142_0_5_line_14 |  | 11 | 34 | 0.0074968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1630-142_0_5_line_15 |  | 13 | 16 | 0.018111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-142_0_5_line_16 |  | 14 | 15 | 0.020933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-142_0_5_line_17 |  | 15 | 16 | 0.04021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-142_0_5_line_18 |  | 17 | 18 | 0.006081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-142_0_5_line_19 |  | 17 | 19 | 0.013523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-142_0_5_line_20 |  | 18 | 25 | 0.015444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-142_0_5_line_21 |  | 18 | 26 | 0.017997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-142_0_5_line_22 |  | 20 | 21 | 0.038764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-142_0_5_line_23 |  | 20 | 22 | 0.017188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-142_0_5_line_24 |  | 21 | 23 | 0.011507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-142_0_5_line_25 |  | 22 | 32 | 0.012585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-142_0_5_line_26 |  | 23 | 33 | 0.011385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-142_0_5_line_27 |  | 24 | 35 | 0.018949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1630-142_0_5_line_28 |  | 25 | 42 | 0.010854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-142_0_5_line_29 |  | 26 | 37 | 0.027183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-142_0_5_line_30 |  | 27 | 28 | 0.017186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-142_0_5_line_31 |  | 28 | 37 | 0.02582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-142_0_5_line_32 |  | 28 | 36 | 0.016739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-142_0_5_line_33 |  | 29 | 30 | 0.007292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-142_0_5_line_34 |  | 29 | 31 | 0.021917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1630-142_0_5_line_35 |  | 30 | 40 | 0.013645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-142_0_5_line_36 |  | 31 | 38 | 0.027586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-142_0_5_line_37 |  | 32 | 40 | 0.012493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-142_0_5_line_38 |  | 34 | 39 | 0.018045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1630-142_0_5_line_39 |  | 35 | 36 | 0.025844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-142_0_5_line_40 |  | 38 | 39 | 0.021748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-142_0_5_line_41 |  | 39 | 41 | 0.019606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-142_0_5_line_42 |  | 42 | 43 | 0.011964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-142_0_5_trafo_28 | 0.63 MVA 20/0.4 kV | 44 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2720468.5659 | 1223469.6969 | 2720482.4092 | 1223486.5181
1 | 2720471.8701 | 1223455.635 | 2720462.9765 | 1223462.9052 | 2720468.5659 | 1223469.6969
2 | 2720492.9471 | 1223499.3229 | 2720482.4092 | 1223486.5181
3 | 2720464.2651 | 1223447.219 | 2720471.8701 | 1223455.635
4 | 2720492.9471 | 1223499.3229 | 2720497.4845 | 1223504.8363
5 | 2720464.2651 | 1223447.219 | 2720451.3557 | 1223435.1483
6 | 2720464.2651 | 1223447.219 | 2720449.3899 | 1223457.153
7 | 2720506.5708 | 1223497.4144 | 2720497.4845 | 1223504.8363
8 | 2720528.8813 | 1223524.3316 | 2720506.5708 | 1223497.4144
9 | 2720528.8813 | 1223524.3316 | 2720543.3839 | 1223514.6621 | 2720552.7471 | 1223527.2727 | 2720560.294 | 1223536.2992 | 2720563.5905 | 1223540.2024
10 | 2720528.8813 | 1223524.3316 | 2720523.9984 | 1223527.5908 | 2720518.4873 | 1223531.267
11 | 2720451.3557 | 1223435.1483 | 2720437.5697 | 1223437.1488 | 2720434.8631 | 1223435.2964
12 | 2720449.3899 | 1223457.153 | 2720418.2541 | 1223477.9463
13 | 2720563.5905 | 1223540.2024 | 2720549.8419 | 1223551.0151
14 | 2720512.2507 | 1223535.4271 | 2720518.4873 | 1223531.267
15 | 2720403.1932 | 1223488.0044 | 2720418.2541 | 1223477.9463
16 | 2720421.9185 | 1223523.4219 | 2720441.855 | 1223517.0409
17 | 2720421.9185 | 1223523.4219 | 2720419.6486 | 1223516.0147 | 2720403.1932 | 1223488.0044
18 | 2720483.8414 | 1223632.7493 | 2720484.4471 | 1223638.7996
19 | 2720484.4471 | 1223638.7996 | 2720470.9759 | 1223637.6222
20 | 2720483.8414 | 1223632.7493 | 2720492.9479 | 1223631.8106 | 2720497.9256 | 1223627.9661
21 | 2720483.8414 | 1223632.7493 | 2720482.1485 | 1223614.8343
22 | 2720425.003 | 1223593.6393 | 2720421.7965 | 1223595.7761 | 2720441.1124 | 1223624.8563
23 | 2720425.003 | 1223593.6393 | 2720429.3587 | 1223599.9323 | 2720437.3504 | 1223594.7324
24 | 2720441.1124 | 1223624.8563 | 2720450.6658 | 1223618.4424
25 | 2720437.3504 | 1223594.7324 | 2720447.8992 | 1223587.8686
26 | 2720450.6658 | 1223618.4424 | 2720460.1181 | 1223612.0963
27 | 2720534.9473 | 1223562.7292 | 2720549.8419 | 1223551.0151
28 | 2720506.516 | 1223621.3311 | 2720497.9256 | 1223627.9661
29 | 2720482.1485 | 1223614.8343 | 2720497.4763 | 1223612.7207 | 2720507.2085 | 1223606.2075
30 | 2720528.6664 | 1223591.8468 | 2720540.136 | 1223604.6458
31 | 2720528.6664 | 1223591.8468 | 2720507.2085 | 1223606.2075
32 | 2720528.6664 | 1223591.8468 | 2720517.8879 | 1223579.0401
33 | 2720452.5236 | 1223575.2817 | 2720458.5984 | 1223571.2236
34 | 2720452.5236 | 1223575.2817 | 2720447.6774 | 1223568.1113 | 2720458.6548 | 1223560.669
35 | 2720458.5984 | 1223571.2236 | 2720463.0042 | 1223578.0403 | 2720458.3703 | 1223581.0555
36 | 2720481.4882 | 1223545.1886 | 2720458.6548 | 1223560.669
37 | 2720447.8992 | 1223587.8686 | 2720458.3703 | 1223581.0555
38 | 2720497.2386 | 1223545.4409 | 2720512.2507 | 1223535.4271
39 | 2720517.8879 | 1223579.0401 | 2720516.4221 | 1223577.2986 | 2720534.9473 | 1223562.7292
40 | 2720481.4882 | 1223545.1886 | 2720486.5961 | 1223552.5422 | 2720497.2386 | 1223545.4409
41 | 2720497.2386 | 1223545.4409 | 2720508.0656 | 1223561.8062
42 | 2720513.9505 | 1223629.6563 | 2720507.1735 | 1223620.8233 | 2720506.516 | 1223621.3311

## bus_geodata
| x | y | coords
0 | 2720468.5659 | 1223469.6969
1 | 2720482.4092 | 1223486.5181
2 | 2720471.8701 | 1223455.635
3 | 2720492.9471 | 1223499.3229
4 | 2720464.2651 | 1223447.219
5 | 2720497.4845 | 1223504.8363
6 | 2720506.5708 | 1223497.4144
7 | 2720528.8813 | 1223524.3316
8 | 2720451.3557 | 1223435.1483
9 | 2720449.3899 | 1223457.153
10 | 2720563.5905 | 1223540.2024
11 | 2720518.4873 | 1223531.267
12 | 2720434.8631 | 1223435.2964
13 | 2720418.2541 | 1223477.9463
14 | 2720441.855 | 1223517.0409
15 | 2720421.9185 | 1223523.4219
16 | 2720403.1932 | 1223488.0044
17 | 2720484.4471 | 1223638.7996
18 | 2720483.8414 | 1223632.7493
19 | 2720470.9758 | 1223637.6222
20 | 2720425.003 | 1223593.6393
21 | 2720441.1124 | 1223624.8563
22 | 2720437.3504 | 1223594.7324
23 | 2720450.6658 | 1223618.4424
24 | 2720549.8419 | 1223551.0151
25 | 2720497.9256 | 1223627.9661
26 | 2720482.1485 | 1223614.8343
27 | 2720540.136 | 1223604.6458
28 | 2720528.6664 | 1223591.8468
29 | 2720452.5236 | 1223575.2817
30 | 2720458.5984 | 1223571.2236
31 | 2720458.6548 | 1223560.669
32 | 2720447.8992 | 1223587.8686
33 | 2720460.1181 | 1223612.0963
34 | 2720512.2507 | 1223535.4271
35 | 2720534.9473 | 1223562.7292
36 | 2720517.8879 | 1223579.0401
37 | 2720507.2085 | 1223606.2075
38 | 2720481.4882 | 1223545.1886
39 | 2720497.2386 | 1223545.4409
40 | 2720458.3703 | 1223581.0555
41 | 2720508.0656 | 1223561.8062
42 | 2720506.516 | 1223621.3311
43 | 2720513.9505 | 1223629.6563
44 | 2720486.5961 | 1223552.5422

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98867 | -0.21737 | 0.026235 | 0.0065751
1 | 0.99056 | -0.18067 | 0.02621 | 0.006569
2 | 0.98739 | -0.24214 | 0 | 0
3 | 0.99241 | -0.14513 | 0.00295 | 0.00073934
4 | 0.98668 | -0.25601 | 0 | 0
5 | 0.99322 | -0.1295 | 0.021237 | 0.0053226
6 | 0.994 | -0.11447 | 0 | 0
7 | 0.99555 | -0.084735 | 0 | 0
8 | 0.98633 | -0.26284 | 0 | 0
9 | 0.98591 | -0.27101 | 0.01271 | 0.0031855
10 | 0.99219 | -0.14914 | 0 | 0
11 | 0.99694 | -0.05811 | 0.0076812 | 0.0019251
12 | 0.98598 | -0.26951 | 0.021618 | 0.0054181
13 | 0.98473 | -0.29392 | 0.017779 | 0.0044557
14 | 0.98354 | -0.31718 | 0.016306 | 0.0040868
15 | 0.98385 | -0.31103 | 0 | 0
16 | 0.98446 | -0.29923 | 0 | 0
17 | 0.98139 | -0.35857 | 0 | 0
18 | 0.9814 | -0.35839 | 0 | 0
19 | 0.98137 | -0.35898 | 0.0016516 | 0.00041393
20 | 0.99361 | -0.12287 | 0 | 0
21 | 0.99328 | -0.12941 | 0 | 0
22 | 0.99376 | -0.11997 | 0.0057477 | 0.0014405
23 | 0.99318 | -0.13135 | 0.0068397 | 0.0017142
24 | 0.99101 | -0.17177 | 0.013261 | 0.0033235
25 | 0.98091 | -0.36809 | 0.0017953 | 0.00044994
26 | 0.98201 | -0.34657 | 0 | 0
27 | 0.9836 | -0.31553 | 0.049187 | 0.012327
28 | 0.98438 | -0.30032 | 0 | 0
29 | 0.9949 | -0.098042 | 0 | 0
30 | 0.99466 | -0.10256 | 0 | 0
31 | 0.9956 | -0.084484 | 0.062662 | 0.015705
32 | 0.99394 | -0.11657 | 0.0099104 | 0.0024838
33 | 0.99315 | -0.1319 | 0.0027142 | 0.00068024
34 | 0.9978 | -0.041835 | 0.026467 | 0.0066332
35 | 0.98922 | -0.20641 | 0.074119 | 0.018576
36 | 0.98608 | -0.26717 | 0.021259 | 0.0053281
37 | 0.98292 | -0.32874 | 0.024789 | 0.0062127
38 | 0.99806 | -0.037151 | 0 | 0
39 | 1 | 0 | -0.52206 | -0.13239
40 | 0.99423 | -0.11101 | 0.0099402 | 0.0024912
41 | 0.99966 | -0.0066275 | 0.019387 | 0.0048589
42 | 0.98058 | -0.37455 | 0.0041265 | 0.0010342
43 | 0.98026 | -0.38079 | 0.028746 | 0.0072043
44 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.094878 | -0.023865 | 0.095045 | 0.023972 | 0.00016666 | 0.00010638 | 0.14283 | 0.14283 | 0.14283 | 0.98867 | -0.21737 | 0.99056 | -0.18067 | 39.2388
1 | 0.068643 | 0.01729 | -0.068562 | -0.017239 | 8.1233e-05 | 5.1729e-05 | 0.10334 | 0.10334 | 0.10334 | 0.98867 | -0.21737 | 0.98739 | -0.24214 | 28.3911
2 | -0.12126 | -0.030541 | 0.12146 | 0.030673 | 0.00020645 | 0.00013191 | 0.1822 | 0.1822 | 0.1822 | 0.99056 | -0.18067 | 0.99241 | -0.14513 | 50.0555
3 | 0.068562 | 0.017239 | -0.068516 | -0.01721 | 4.5372e-05 | 2.8893e-05 | 0.10334 | 0.10334 | 0.10334 | 0.98739 | -0.24214 | 0.98668 | -0.25601 | 28.3911
4 | -0.12441 | -0.031412 | 0.1245 | 0.031472 | 9.3261e-05 | 5.9595e-05 | 0.18663 | 0.18663 | 0.18663 | 0.99241 | -0.14513 | 0.99322 | -0.1295 | 51.2706
5 | 0.021632 | 0.0054265 | -0.021625 | -0.0054222 | 7.0436e-06 | 4.2826e-06 | 0.032626 | 0.032626 | 0.032626 | 0.98668 | -0.25601 | 0.98633 | -0.26284 | 8.9631
6 | 0.046884 | 0.011783 | -0.046851 | -0.011762 | 3.3546e-05 | 2.1241e-05 | 0.070718 | 0.070718 | 0.070718 | 0.98668 | -0.25601 | 0.98591 | -0.27101 | 19.4281
7 | -0.14574 | -0.036794 | 0.14585 | 0.036861 | 0.00010497 | 6.6876e-05 | 0.21844 | 0.21844 | 0.21844 | 0.99322 | -0.1295 | 0.994 | -0.11447 | 30.0058
8 | -0.14585 | -0.036861 | 0.14606 | 0.036993 | 0.00020829 | 0.00013195 | 0.21844 | 0.21844 | 0.21844 | 0.994 | -0.11447 | 0.99555 | -0.084735 | 20.0039
9 | 0.22096 | 0.056164 | -0.22028 | -0.055728 | 0.00068304 | 0.0004352 | 0.33055 | 0.33055 | 0.33055 | 0.99555 | -0.084735 | 0.99219 | -0.14914 | 30.2699
10 | -0.36702 | -0.093157 | 0.36749 | 0.093457 | 0.00047075 | 0.00030079 | 0.54899 | 0.54899 | 0.54899 | 0.99555 | -0.084735 | 0.99694 | -0.05811 | 50.2737
11 | 0.021625 | 0.0054222 | -0.021618 | -0.0054181 | 6.8697e-06 | 4.177e-06 | 0.032626 | 0.032626 | 0.032626 | 0.98633 | -0.26284 | 0.98598 | -0.26951 | 8.9631
12 | 0.03414 | 0.0085765 | -0.034103 | -0.0085531 | 3.7289e-05 | 2.3388e-05 | 0.051535 | 0.051535 | 0.051535 | 0.98591 | -0.27101 | 0.98473 | -0.29392 | 14.158
13 | 0.22028 | 0.055728 | -0.22004 | -0.055576 | 0.00023889 | 0.00015221 | 0.33055 | 0.33055 | 0.33055 | 0.99219 | -0.14914 | 0.99101 | -0.17177 | 30.2699
14 | -0.37517 | -0.095382 | 0.37547 | 0.095571 | 0.00029435 | 0.00018809 | 0.56045 | 0.56045 | 0.56045 | 0.99694 | -0.05811 | 0.9978 | -0.041835 | 51.3235
15 | 0.016325 | 0.0040973 | -0.01632 | -0.0040949 | 4.1334e-06 | 2.415e-06 | 0.02467 | 0.02467 | 0.02467 | 0.98473 | -0.29392 | 0.98446 | -0.29923 | 6.7775
16 | -0.016306 | -0.0040868 | 0.016311 | 0.0040896 | 4.7776e-06 | 2.7919e-06 | 0.02467 | 0.02467 | 0.02467 | 0.98354 | -0.31718 | 0.98385 | -0.31103 | 6.7776
17 | -0.016311 | -0.0040896 | 0.01632 | 0.0040949 | 9.1772e-06 | 5.3624e-06 | 0.02467 | 0.02467 | 0.02467 | 0.98385 | -0.31103 | 0.98446 | -0.29923 | 6.7775
18 | -0.0016516 | -0.00041378 | 0.0016516 | 0.00041371 | 1.43e-08 | -6.7686e-08 | 0.0025042 | 0.0025042 | 0.0025042 | 0.98139 | -0.35857 | 0.9814 | -0.35839 | 0.68796
19 | 0.0016516 | 0.00041378 | -0.0016516 | -0.00041393 | 3.1801e-08 | -1.5051e-07 | 0.0025042 | 0.0025042 | 0.0025042 | 0.98139 | -0.35857 | 0.98137 | -0.35898 | 0.68798
20 | 0.034702 | 0.0087102 | -0.034686 | -0.0087001 | 1.6036e-05 | 1.0068e-05 | 0.05262 | 0.05262 | 0.05262 | 0.9814 | -0.35839 | 0.98091 | -0.36809 | 14.4562
21 | -0.036354 | -0.0091239 | 0.036374 | 0.0091368 | 2.0508e-05 | 1.2898e-05 | 0.055125 | 0.055124 | 0.055125 | 0.9814 | -0.35839 | 0.98201 | -0.34657 | 15.1441
22 | 0.0095578 | 0.0023961 | -0.0095548 | -0.0023947 | 2.9783e-06 | 1.4042e-06 | 0.014314 | 0.014314 | 0.014314 | 0.99361 | -0.12287 | 0.99328 | -0.12941 | 3.9324
23 | -0.0095578 | -0.0023961 | 0.0095591 | 0.0023968 | 1.3206e-06 | 6.2251e-07 | 0.014314 | 0.014314 | 0.014314 | 0.99361 | -0.12287 | 0.99376 | -0.11997 | 3.9324
24 | 0.0095548 | 0.0023947 | -0.0095539 | -0.0023943 | 8.8411e-07 | 4.1691e-07 | 0.014314 | 0.014314 | 0.014314 | 0.99328 | -0.12941 | 0.99318 | -0.13135 | 3.9324
25 | -0.015307 | -0.0038373 | 0.015309 | 0.0038387 | 2.4793e-06 | 1.4237e-06 | 0.02292 | 0.02292 | 0.02292 | 0.99376 | -0.11997 | 0.99394 | -0.11657 | 6.2967
26 | 0.0027142 | 0.00068013 | -0.0027142 | -0.00068024 | 7.0603e-08 | -1.0214e-07 | 0.0040665 | 0.0040666 | 0.0040666 | 0.99318 | -0.13135 | 0.99315 | -0.1319 | 1.1172
27 | 0.20678 | 0.052253 | -0.20644 | -0.052034 | 0.00034284 | 0.00021893 | 0.31064 | 0.31064 | 0.31064 | 0.99101 | -0.17177 | 0.98922 | -0.20641 | 42.6698
28 | 0.032891 | 0.0082502 | -0.032881 | -0.0082438 | 1.0134e-05 | 6.3489e-06 | 0.049897 | 0.049897 | 0.049897 | 0.98091 | -0.36809 | 0.98058 | -0.37455 | 13.708
29 | -0.036374 | -0.0091368 | 0.036405 | 0.0091563 | 3.0976e-05 | 1.948e-05 | 0.055124 | 0.055124 | 0.055124 | 0.98201 | -0.34657 | 0.98292 | -0.32874 | 15.1441
30 | -0.049187 | -0.012327 | 0.049223 | 0.01235 | 3.5686e-05 | 2.262e-05 | 0.074412 | 0.074412 | 0.074412 | 0.9836 | -0.31553 | 0.98438 | -0.30032 | 20.4428
31 | 0.061277 | 0.015422 | -0.061194 | -0.015369 | 8.3118e-05 | 5.2868e-05 | 0.092652 | 0.092652 | 0.092652 | 0.98438 | -0.30032 | 0.98292 | -0.32874 | 25.4537
32 | -0.1105 | -0.027772 | 0.11068 | 0.027884 | 0.00017519 | 0.00011191 | 0.16706 | 0.16706 | 0.16706 | 0.98438 | -0.30032 | 0.98608 | -0.26717 | 45.8964
33 | 0.035188 | 0.0088315 | -0.035181 | -0.0088267 | 7.5754e-06 | 4.7536e-06 | 0.052634 | 0.052634 | 0.052634 | 0.9949 | -0.098042 | 0.99466 | -0.10256 | 14.4598
34 | -0.035188 | -0.0088315 | 0.035211 | 0.0088458 | 2.2769e-05 | 1.4287e-05 | 0.052634 | 0.052634 | 0.052634 | 0.9949 | -0.098042 | 0.9956 | -0.084484 | 14.4598
35 | 0.035181 | 0.0088267 | -0.035167 | -0.0088178 | 1.4175e-05 | 8.8952e-06 | 0.052634 | 0.052634 | 0.052634 | 0.99466 | -0.10256 | 0.99423 | -0.11101 | 14.4598
36 | -0.097873 | -0.02455 | 0.098095 | 0.024692 | 0.00022138 | 0.00014133 | 0.14629 | 0.14629 | 0.14629 | 0.9956 | -0.084484 | 0.99806 | -0.037151 | 40.189
37 | -0.02522 | -0.0063225 | 0.025226 | 0.0063266 | 6.6784e-06 | 4.1122e-06 | 0.037757 | 0.037757 | 0.037757 | 0.99394 | -0.11657 | 0.99423 | -0.11101 | 10.3727
38 | -0.40193 | -0.1022 | 0.40274 | 0.10272 | 0.00081184 | 0.00051887 | 0.59992 | 0.59992 | 0.59992 | 0.9978 | -0.041835 | 1 | 0 | 54.9379
39 | 0.13232 | 0.033458 | -0.13193 | -0.033212 | 0.00038435 | 0.00024565 | 0.19914 | 0.19914 | 0.19914 | 0.98922 | -0.20641 | 0.98608 | -0.26717 | 54.7099
40 | -0.098095 | -0.024692 | 0.098269 | 0.024803 | 0.00017453 | 0.00011141 | 0.14629 | 0.14629 | 0.14629 | 0.99806 | -0.037151 | 1 | 0 | 40.189
41 | 0.019393 | 0.0048626 | -0.019387 | -0.0048589 | 6.1231e-06 | 3.6616e-06 | 0.028859 | 0.028859 | 0.028859 | 1 | 0 | 0.99966 | -0.0066275 | 7.9282
42 | 0.028754 | 0.0072096 | -0.028746 | -0.0072043 | 8.5425e-06 | 5.3163e-06 | 0.043635 | 0.043635 | 0.043635 | 0.98058 | -0.37455 | 0.98026 | -0.38079 | 11.9877

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52206 | 0.13239

## res_load
| p_mw | q_mvar
0 | 0.026235 | 0.0065751
1 | 0.02621 | 0.006569
2 | 0.00295 | 0.00073934
3 | 0.021237 | 0.0053226
4 | 0.01271 | 0.0031855
5 | 0.0076812 | 0.0019251
6 | 0.021618 | 0.0054181
7 | 0.017779 | 0.0044557
8 | 0.016306 | 0.0040868
9 | 0.0016516 | 0.00041393
10 | 0.0057477 | 0.0014405
11 | 0.0068397 | 0.0017142
12 | 0.013261 | 0.0033235
13 | 0.0017953 | 0.00044994
14 | 0.049187 | 0.012327
15 | 0.062662 | 0.015705
16 | 0.0099104 | 0.0024838
17 | 0.0027142 | 0.00068024
18 | 0.026467 | 0.0066332
19 | 0.074119 | 0.018576
20 | 0.021259 | 0.0053281
21 | 0.024789 | 0.0062127
22 | 0.0099402 | 0.0024912
23 | 0.019387 | 0.0048589
24 | 0.0041265 | 0.0010342
25 | 0.028746 | 0.0072043

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1