## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-14_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-14_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-14_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-14_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-14_0_3_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_1630-14_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1630-14_0_3_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_1630-14_0_3_node_31 | 0.4 | n |  | TRUE
8 | bus_LV_1630-14_0_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_1630-14_0_3_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1630-14_0_3_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_1630-14_0_3_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_1630-14_0_3_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1630-14_0_3_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1630-14_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1630-14_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1630-14_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1630-14_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1630-14_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1630-14_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1630-14_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1630-14_0_3_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1630-14_0_3_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1630-14_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1630-14_0_3_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1630-14_0_3_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1630-14_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1630-14_0_3_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1630-14_0_3_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1630-14_0_3_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1630-14_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_MV_54_0_node_98 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-14_0_3_load_0 | 0 | 0.0023305 | 0.00058408 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-14_0_3_load_3 | 3 | 0.0015029 | 0.00037666 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-14_0_3_load_30 | 6 | 0.020324 | 0.0050937 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-14_0_3_load_31 | 7 | 0.017368 | 0.0043528 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-14_0_3_load_4 | 9 | 0.0021953 | 0.00055021 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-14_0_3_load_29 | 10 | 0.019424 | 0.0048682 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-14_0_3_load_5 | 12 | 0.00066133 | 0.00016575 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-14_0_3_load_16 | 13 | 0.010566 | 0.0026481 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-14_0_3_load_7 | 15 | 0.029308 | 0.0073453 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-14_0_3_load_9 | 17 | 0.02936 | 0.0073583 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-14_0_3_load_12 | 19 | 0.010544 | 0.0026425 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-14_0_3_load_19 | 20 | 0.037832 | 0.0094816 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-14_0_3_load_13 | 21 | 0.0080048 | 0.0020062 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-14_0_3_load_14 | 23 | 0.0080751 | 0.0020238 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-14_0_3_load_22 | 24 | 0.0080303 | 0.0020126 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-14_0_3_load_24 | 25 | 0.012314 | 0.0030861 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-14_0_3_load_17 | 26 | 0.011886 | 0.0029788 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-14_0_3_load_18 | 27 | 0.011941 | 0.0029927 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-14_0_3_load_23 | 28 | 0.011041 | 0.0027672 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-14_0_3_load_21 | 29 | 0.037726 | 0.0094549 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-14_0_3_load_25 | 30 | 0.012227 | 0.0030643 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-14_0_3_line_0 |  | 0 | 1 | 0.021531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-14_0_3_line_1 |  | 1 | 2 | 0.03612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-14_0_3_line_2 |  | 2 | 3 | 0.01256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-14_0_3_line_3 |  | 2 | 4 | 0.044324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-14_0_3_line_4 |  | 3 | 9 | 0.0054019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-14_0_3_line_5 |  | 4 | 10 | 0.007894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-14_0_3_line_6 |  | 4 | 11 | 0.028814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-14_0_3_line_7 |  | 5 | 6 | 0.014543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-14_0_3_line_8 |  | 5 | 7 | 0.01197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-14_0_3_line_9 |  | 5 | 8 | 0.069273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-14_0_3_line_10 |  | 7 | 11 | 0.063626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-14_0_3_line_11 |  | 8 | 13 | 0.022206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_1630-14_0_3_line_12 |  | 8 | 14 | 0.029463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1630-14_0_3_line_13 |  | 9 | 12 | 0.001946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-14_0_3_line_14 |  | 11 | 30 | 0.014463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-14_0_3_line_15 |  | 13 | 26 | 0.0064143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1630-14_0_3_line_16 |  | 14 | 19 | 0.019737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-14_0_3_line_17 |  | 14 | 16 | 0.005501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-14_0_3_line_18 |  | 15 | 16 | 0.020754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-14_0_3_line_19 |  | 15 | 17 | 0.013048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-14_0_3_line_20 |  | 16 | 18 | 0.063464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-14_0_3_line_21 |  | 18 | 20 | 0.020353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-14_0_3_line_22 |  | 19 | 21 | 0.0063439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-14_0_3_line_23 |  | 20 | 22 | 0.031717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-14_0_3_line_24 |  | 21 | 23 | 0.007533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-14_0_3_line_25 |  | 22 | 29 | 0.017687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-14_0_3_line_26 |  | 23 | 24 | 0.0067137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-14_0_3_line_27 |  | 24 | 25 | 0.0080407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-14_0_3_line_28 |  | 26 | 27 | 0.0066554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-14_0_3_line_29 |  | 27 | 28 | 0.0061767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-14_0_3_trafo_17 | 0.63 MVA 20/0.4 kV | 31 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2722911.184 | 1221333.9098 | 2722906.4528 | 1221337.3815 | 2722896.281 | 1221349.2921
1 | 2722911.184 | 1221333.9098 | 2722914.5541 | 1221338.6497 | 2722925.9474 | 1221352.4735 | 2722931.7117 | 1221359.5981 | 2722933.9235 | 1221362.0012
2 | 2722933.9235 | 1221362.0012 | 2722924.9705 | 1221370.8102
3 | 2722933.9235 | 1221362.0012 | 2722976.9262 | 1221372.7419
4 | 2722924.9705 | 1221370.8102 | 2722921.12 | 1221374.5988
5 | 2722982.3271 | 1221366.9711 | 2722980.876 | 1221368.5201 | 2722976.9262 | 1221372.7419
6 | 2722976.9262 | 1221372.7419 | 2722999.1597 | 1221391.1488
7 | 2722932.5719 | 1221425.223 | 2722946.4094 | 1221429.8234
8 | 2722940.8107 | 1221416.5196 | 2722932.5719 | 1221425.223
9 | 2722873.5832 | 1221435.3025 | 2722875.3264 | 1221433.9374 | 2722886.4786 | 1221427.4624 | 2722911.2583 | 1221417.755 | 2722917.3487 | 1221414.6005 | 2722919.8948 | 1221412.9406 | 2722932.5719 | 1221425.223
10 | 2722940.8107 | 1221416.5196 | 2722999.1597 | 1221391.1488
11 | 2722873.5832 | 1221435.3025 | 2722880.3586 | 1221440.502 | 2722883.2988 | 1221442.909 | 2722890.9598 | 1221449.1246
12 | 2722852.0202 | 1221455.3512 | 2722865.1717 | 1221442.4568 | 2722869.0046 | 1221439.111 | 2722871.3153 | 1221437.0905 | 2722873.5832 | 1221435.3025
13 | 2722919.7328 | 1221375.9637 | 2722921.12 | 1221374.5988
14 | 2722999.1597 | 1221391.1488 | 2723007.5328 | 1221397.9827 | 2723010.6066 | 1221399.9607
15 | 2722895.9409 | 1221453.1658 | 2722890.9598 | 1221449.1246
16 | 2722852.0202 | 1221455.3512 | 2722859.6693 | 1221461.6028 | 2722862.5798 | 1221463.9758 | 2722867.3045 | 1221467.8386
17 | 2722848.0857 | 1221459.2064 | 2722852.0202 | 1221455.3512
18 | 2722848.0857 | 1221459.2064 | 2722862.5236 | 1221474.1158
19 | 2722867.064 | 1221483.8507 | 2722868.9872 | 1221481.8554 | 2722866.6373 | 1221479.5273 | 2722866.2596 | 1221477.9739 | 2722862.5236 | 1221474.1158
20 | 2722802.7613 | 1221503.6288 | 2722824.4474 | 1221482.3816 | 2722827.801 | 1221479.0926 | 2722838.0556 | 1221469.0406 | 2722848.0857 | 1221459.2064
21 | 2722802.7613 | 1221503.6288 | 2722816.9708 | 1221518.2003
22 | 2722872.2159 | 1221471.854 | 2722867.3045 | 1221467.8386
23 | 2722839.1142 | 1221540.9079 | 2722816.9708 | 1221518.2003
24 | 2722872.2159 | 1221471.854 | 2722872.3333 | 1221471.95 | 2722872.8552 | 1221475.3412 | 2722875.9631 | 1221477.7795
25 | 2722839.1142 | 1221540.9079 | 2722851.8514 | 1221528.6368
26 | 2722881.2452 | 1221481.9235 | 2722875.9631 | 1221477.7795
27 | 2722887.5714 | 1221486.8867 | 2722881.2452 | 1221481.9235
28 | 2722901.1092 | 1221457.3591 | 2722895.9409 | 1221453.1658
29 | 2722901.1092 | 1221457.3591 | 2722905.9058 | 1221461.2506

## bus_geodata
| x | y | coords
0 | 2722896.281 | 1221349.2921
1 | 2722911.184 | 1221333.9098
2 | 2722933.9235 | 1221362.0012
3 | 2722924.9705 | 1221370.8102
4 | 2722976.9262 | 1221372.7419
5 | 2722932.5719 | 1221425.223
6 | 2722946.4094 | 1221429.8234
7 | 2722940.8107 | 1221416.5196
8 | 2722873.5832 | 1221435.3025
9 | 2722921.12 | 1221374.5988
10 | 2722982.3271 | 1221366.9711
11 | 2722999.1597 | 1221391.1488
12 | 2722919.7328 | 1221375.9637
13 | 2722890.9598 | 1221449.1246
14 | 2722852.0202 | 1221455.3512
15 | 2722862.5236 | 1221474.1158
16 | 2722848.0857 | 1221459.2064
17 | 2722867.064 | 1221483.8507
18 | 2722802.7613 | 1221503.6288
19 | 2722867.3045 | 1221467.8386
20 | 2722816.9708 | 1221518.2003
21 | 2722872.2159 | 1221471.854
22 | 2722839.1142 | 1221540.9079
23 | 2722875.9631 | 1221477.7795
24 | 2722881.2452 | 1221481.9235
25 | 2722887.5714 | 1221486.8867
26 | 2722895.9409 | 1221453.1658
27 | 2722901.1092 | 1221457.3591
28 | 2722905.9058 | 1221461.2506
29 | 2722851.8514 | 1221528.6368
30 | 2723010.6066 | 1221399.9607
31 | 2722908.1072 | 1221463.0367

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98783 | -0.23419 | 0.0023305 | 0.00058408
1 | 0.98788 | -0.2333 | 0 | 0
2 | 0.98796 | -0.23179 | 0 | 0
3 | 0.98791 | -0.23277 | 0.0015029 | 0.00037666
4 | 0.98823 | -0.2265 | 0 | 0
5 | 0.99177 | -0.15786 | 0 | 0
6 | 0.9915 | -0.1631 | 0.020324 | 0.0050937
7 | 0.99116 | -0.16969 | 0.017368 | 0.0043528
8 | 0.9966 | -0.064973 | 0 | 0
9 | 0.98789 | -0.23305 | 0.0021953 | 0.00055021
10 | 0.98809 | -0.22923 | 0.019424 | 0.0048682
11 | 0.98892 | -0.21308 | 0 | 0
12 | 0.98789 | -0.23307 | 0.00066133 | 0.00016575
13 | 0.99921 | -0.014982 | 0.010566 | 0.0026481
14 | 0.99415 | -0.11193 | 0 | 0
15 | 0.99236 | -0.14649 | 0.029308 | 0.0073453
16 | 0.99347 | -0.12496 | 0 | 0
17 | 0.99201 | -0.15327 | 0.02936 | 0.0073583
18 | 0.98907 | -0.21002 | 0 | 0
19 | 0.9933 | -0.12829 | 0.010544 | 0.0026425
20 | 0.98765 | -0.23746 | 0.037832 | 0.0094816
21 | 0.99309 | -0.13238 | 0.0080048 | 0.0020062
22 | 0.98655 | -0.25887 | 0 | 0
23 | 0.9929 | -0.13616 | 0.0080751 | 0.0020238
24 | 0.99277 | -0.13858 | 0.0080303 | 0.0020126
25 | 0.99268 | -0.14033 | 0.012314 | 0.0030861
26 | 1 | 0 | -0.29481 | -0.074392
27 | 0.99986 | -0.0026663 | 0.011941 | 0.0029927
28 | 0.9998 | -0.0038554 | 0.011041 | 0.0027672
29 | 0.98594 | -0.27082 | 0.037726 | 0.0094549
30 | 0.98876 | -0.21623 | 0.012227 | 0.0030643
31 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0023305 | -0.00058408 | 0.0023306 | 0.00058387 | 9.9503e-08 | -2.1197e-07 | 0.0035105 | 0.0035104 | 0.0035105 | 0.98783 | -0.23419 | 0.98788 | -0.2333 | 0.96443
1 | -0.0023306 | -0.00058387 | 0.0023308 | 0.00058351 | 1.6691e-07 | -3.5567e-07 | 0.0035104 | 0.0035103 | 0.0035104 | 0.98788 | -0.2333 | 0.98796 | -0.23179 | 0.96441
2 | 0.0043598 | 0.0010925 | -0.0043596 | -0.0010925 | 2.0309e-07 | -3.0847e-08 | 0.0065665 | 0.0065666 | 0.0065666 | 0.98796 | -0.23179 | 0.98791 | -0.23277 | 1.804
3 | -0.0066906 | -0.001676 | 0.0066923 | 0.0016765 | 1.6877e-06 | 5.1241e-07 | 0.010077 | 0.010077 | 0.010077 | 0.98796 | -0.23179 | 0.98823 | -0.2265 | 2.7683
4 | 0.0028567 | 0.00071588 | -0.0028567 | -0.00071593 | 3.7506e-08 | -4.5161e-08 | 0.0043028 | 0.0043029 | 0.0043029 | 0.98791 | -0.23277 | 0.98789 | -0.23305 | 1.1821
5 | 0.019427 | 0.0048697 | -0.019424 | -0.0048682 | 2.533e-06 | 1.52e-06 | 0.029252 | 0.029252 | 0.029252 | 0.98823 | -0.2265 | 0.98809 | -0.22923 | 8.0363
6 | -0.026119 | -0.0065462 | 0.026136 | 0.0065566 | 1.6713e-05 | 1.0327e-05 | 0.039329 | 0.039328 | 0.039329 | 0.98823 | -0.2265 | 0.98892 | -0.21308 | 10.8046
7 | 0.020329 | 0.0050967 | -0.020324 | -0.0050937 | 5.0738e-06 | 3.0596e-06 | 0.030502 | 0.030502 | 0.030502 | 0.99177 | -0.15786 | 0.9915 | -0.1631 | 8.3796
8 | 0.055843 | 0.014045 | -0.055812 | -0.014025 | 3.1524e-05 | 2.0021e-05 | 0.083803 | 0.083803 | 0.083803 | 0.99177 | -0.15786 | 0.99116 | -0.16969 | 23.0228
9 | -0.076172 | -0.019141 | 0.076512 | 0.019358 | 0.0003394 | 0.00021632 | 0.1143 | 0.1143 | 0.1143 | 0.99177 | -0.15786 | 0.9966 | -0.064973 | 31.4023
10 | 0.038444 | 0.0096719 | -0.038364 | -0.0096219 | 7.9515e-05 | 5.0072e-05 | 0.057729 | 0.057729 | 0.057729 | 0.99116 | -0.16969 | 0.98892 | -0.21308 | 15.8596
11 | -0.25879 | -0.065459 | 0.25941 | 0.065857 | 0.00062232 | 0.0003977 | 0.38661 | 0.38661 | 0.38661 | 0.9966 | -0.064973 | 0.99921 | -0.014982 | 53.1058
12 | 0.18228 | 0.046101 | -0.18187 | -0.04584 | 0.00040964 | 0.0002614 | 0.27231 | 0.27231 | 0.27231 | 0.9966 | -0.064973 | 0.99415 | -0.11193 | 37.4048
13 | 0.00066133 | 0.00016572 | -0.00066133 | -0.00016575 | 7.2414e-10 | -2.4453e-08 | 0.00099612 | 0.00099613 | 0.00099613 | 0.98789 | -0.23305 | 0.98789 | -0.23307 | 0.27366
14 | 0.012229 | 0.0030653 | -0.012227 | -0.0030643 | 1.8363e-06 | 9.8971e-07 | 0.0184 | 0.0184 | 0.0184 | 0.98892 | -0.21308 | 0.98876 | -0.21623 | 5.0551
15 | -0.26998 | -0.068505 | 0.27017 | 0.06863 | 0.00019469 | 0.00012443 | 0.40235 | 0.40235 | 0.40235 | 0.99921 | -0.014982 | 1 | 0 | 55.2672
16 | 0.04702 | 0.011804 | -0.046983 | -0.011781 | 3.6667e-05 | 2.3211e-05 | 0.070385 | 0.070385 | 0.070385 | 0.99415 | -0.11193 | 0.9933 | -0.12829 | 19.3366
17 | 0.13485 | 0.034036 | -0.13476 | -0.033982 | 8.4108e-05 | 5.3758e-05 | 0.20192 | 0.20192 | 0.20192 | 0.99415 | -0.11193 | 0.99347 | -0.12496 | 55.4729
18 | -0.058678 | -0.01471 | 0.058738 | 0.014748 | 6.0252e-05 | 3.8293e-05 | 0.087987 | 0.087987 | 0.087987 | 0.99236 | -0.14649 | 0.99347 | -0.12496 | 24.1722
19 | 0.02937 | 0.0073642 | -0.02936 | -0.0073583 | 9.4903e-06 | 5.9053e-06 | 0.04404 | 0.04404 | 0.04404 | 0.99236 | -0.14649 | 0.99201 | -0.15327 | 12.0989
20 | 0.076026 | 0.019234 | -0.075717 | -0.019037 | 0.00030894 | 0.0001969 | 0.11393 | 0.11394 | 0.11394 | 0.99347 | -0.12496 | 0.98907 | -0.21002 | 31.3009
21 | 0.075717 | 0.019037 | -0.075618 | -0.018974 | 9.9077e-05 | 6.3148e-05 | 0.11394 | 0.11394 | 0.11394 | 0.98907 | -0.21002 | 0.98765 | -0.23746 | 31.3009
22 | 0.03644 | 0.0091383 | -0.036432 | -0.0091339 | 7.0895e-06 | 4.4552e-06 | 0.05459 | 0.05459 | 0.05459 | 0.9933 | -0.12829 | 0.99309 | -0.13238 | 14.9973
23 | 0.037786 | 0.0094927 | -0.037747 | -0.0094685 | 3.8557e-05 | 2.4271e-05 | 0.056937 | 0.056937 | 0.056937 | 0.98765 | -0.23746 | 0.98655 | -0.25887 | 15.642
24 | 0.028428 | 0.0071277 | -0.028423 | -0.0071245 | 5.1256e-06 | 3.1829e-06 | 0.042596 | 0.042596 | 0.042596 | 0.99309 | -0.13238 | 0.9929 | -0.13616 | 11.7022
25 | 0.037747 | 0.0094685 | -0.037726 | -0.0094549 | 2.1501e-05 | 1.3535e-05 | 0.056937 | 0.056937 | 0.056937 | 0.98655 | -0.25887 | 0.98594 | -0.27082 | 15.642
26 | 0.020347 | 0.0051007 | -0.020345 | -0.0050993 | 2.3412e-06 | 1.4115e-06 | 0.030494 | 0.030494 | 0.030494 | 0.9929 | -0.13616 | 0.99277 | -0.13858 | 8.3776
27 | 0.012315 | 0.0030867 | -0.012314 | -0.0030861 | 1.0273e-06 | 5.5352e-07 | 0.018458 | 0.018458 | 0.018458 | 0.99277 | -0.13858 | 0.99268 | -0.14033 | 5.0709
28 | 0.022986 | 0.005762 | -0.022983 | -0.0057602 | 2.9198e-06 | 1.7814e-06 | 0.034204 | 0.034204 | 0.034204 | 1 | 0 | 0.99986 | -0.0026663 | 9.3966
29 | 0.011042 | 0.0027676 | -0.011041 | -0.0027672 | 6.2549e-07 | 3.1931e-07 | 0.016433 | 0.016433 | 0.016433 | 0.99986 | -0.0026663 | 0.9998 | -0.0038554 | 4.5146

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30669 | 0.07737

## res_load
| p_mw | q_mvar
0 | 0.0023305 | 0.00058408
1 | 0.0015029 | 0.00037666
2 | 0.020324 | 0.0050937
3 | 0.017368 | 0.0043528
4 | 0.0021953 | 0.00055021
5 | 0.019424 | 0.0048682
6 | 0.00066133 | 0.00016575
7 | 0.010566 | 0.0026481
8 | 0.029308 | 0.0073453
9 | 0.02936 | 0.0073583
10 | 0.010544 | 0.0026425
11 | 0.037832 | 0.0094816
12 | 0.0080048 | 0.0020062
13 | 0.0080751 | 0.0020238
14 | 0.0080303 | 0.0020126
15 | 0.012314 | 0.0030861
16 | 0.011886 | 0.0029788
17 | 0.011941 | 0.0029927
18 | 0.011041 | 0.0027672
19 | 0.037726 | 0.0094549
20 | 0.012227 | 0.0030643

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1