## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-157_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-157_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-157_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-157_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-157_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-157_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1630-157_0_3_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_1630-157_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1630-157_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1630-157_0_3_node_36 | 0.4 | n |  | TRUE
10 | bus_LV_1630-157_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1630-157_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1630-157_0_3_node_44 | 0.4 | n |  | TRUE
13 | bus_LV_1630-157_0_3_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1630-157_0_3_node_39 | 0.4 | n |  | TRUE
15 | bus_LV_1630-157_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1630-157_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1630-157_0_3_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1630-157_0_3_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1630-157_0_3_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_1630-157_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1630-157_0_3_node_38 | 0.4 | n |  | TRUE
22 | bus_LV_1630-157_0_3_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1630-157_0_3_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_1630-157_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1630-157_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1630-157_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1630-157_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1630-157_0_3_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1630-157_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1630-157_0_3_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1630-157_0_3_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1630-157_0_3_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1630-157_0_3_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1630-157_0_3_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_1630-157_0_3_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1630-157_0_3_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_1630-157_0_3_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_1630-157_0_3_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1630-157_0_3_node_46 | 0.4 | n |  | TRUE
40 | bus_LV_1630-157_0_3_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_1630-157_0_3_node_47 | 0.4 | n |  | TRUE
42 | bus_LV_1630-157_0_3_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_1630-157_0_3_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_1630-157_0_3_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_1630-157_0_3_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_1630-157_0_3_node_43 | 0.4 | n |  | TRUE
47 | bus_MV_152_0_node_135 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-157_0_3_load_0 | 0 | 0.0059553 | 0.0014925 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-157_0_3_load_1 | 1 | 0.0048172 | 0.0012073 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-157_0_3_load_3 | 3 | 0.0006683 | 0.00016749 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-157_0_3_load_4 | 4 | 0.0014289 | 0.00035813 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-157_0_3_load_37 | 6 | 0.0012893 | 0.00032312 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-157_0_3_load_5 | 8 | 0.00076135 | 0.00019081 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-157_0_3_load_36 | 9 | 0.01027 | 0.0025738 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-157_0_3_load_11 | 11 | 0.0012378 | 0.00031023 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-157_0_3_load_44 | 12 | 0.0019429 | 0.00048693 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-157_0_3_load_19 | 17 | 0.0014592 | 0.00036571 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-157_0_3_load_35 | 19 | 0.0024561 | 0.00061555 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-157_0_3_load_16 | 20 | 0.0011618 | 0.00029118 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-157_0_3_load_38 | 21 | 0.0012151 | 0.00030453 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-157_0_3_load_30 | 22 | 0.0013688 | 0.00034307 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-157_0_3_load_27 | 23 | 0.0027218 | 0.00068216 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-157_0_3_load_12 | 24 | 0.0129 | 0.003233 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-157_0_3_load_14 | 26 | 0.022136 | 0.0055477 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-157_0_3_load_20 | 29 | 0.00079755 | 0.00019988 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-157_0_3_load_21 | 30 | 0.00071622 | 0.0001795 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-157_0_3_load_23 | 31 | 0.0095021 | 0.0023814 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-157_0_3_load_29 | 35 | 0.00092804 | 0.00023259 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-157_0_3_load_32 | 36 | 0.0058237 | 0.0014596 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-157_0_3_load_31 | 37 | 0.001323 | 0.00033156 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-157_0_3_load_33 | 38 | 0.0031343 | 0.00078553 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-157_0_3_load_47 | 41 | 0.0012383 | 0.00031035 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-157_0_3_load_45 | 43 | 0.0018958 | 0.00047514 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-157_0_3_load_40 | 44 | 0.00067206 | 0.00016843 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-157_0_3_load_43 | 46 | 0.0017345 | 0.0004347 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-157_0_3_line_0 |  | 0 | 1 | 0.050548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-157_0_3_line_1 |  | 0 | 2 | 0.017942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-157_0_3_line_2 |  | 2 | 3 | 0.020919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-157_0_3_line_3 |  | 2 | 4 | 0.042012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-157_0_3_line_4 |  | 3 | 5 | 0.02203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-157_0_3_line_5 |  | 4 | 6 | 0.019537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-157_0_3_line_6 |  | 5 | 7 | 0.012906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-157_0_3_line_7 |  | 5 | 8 | 0.018286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-157_0_3_line_8 |  | 6 | 9 | 0.018995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-157_0_3_line_9 |  | 7 | 12 | 0.010217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-157_0_3_line_10 |  | 7 | 13 | 0.019645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-157_0_3_line_11 |  | 7 | 14 | 0.016407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-157_0_3_line_12 |  | 8 | 10 | 0.0047269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-157_0_3_line_13 |  | 9 | 27 | 0.024052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-157_0_3_line_14 |  | 10 | 11 | 0.0072705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-157_0_3_line_15 |  | 13 | 17 | 0.011112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-157_0_3_line_16 |  | 13 | 20 | 0.022232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-157_0_3_line_17 |  | 14 | 21 | 0.01188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-157_0_3_line_18 |  | 15 | 16 | 0.02054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-157_0_3_line_19 |  | 15 | 17 | 0.0073199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-157_0_3_line_20 |  | 15 | 18 | 0.014172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-157_0_3_line_21 |  | 16 | 19 | 0.12709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-157_0_3_line_22 |  | 18 | 22 | 0.012502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-157_0_3_line_23 |  | 18 | 23 | 0.014334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-157_0_3_line_24 |  | 20 | 28 | 0.010508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-157_0_3_line_25 |  | 21 | 44 | 0.0092776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-157_0_3_line_26 |  | 23 | 33 | 0.012743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-157_0_3_line_27 |  | 24 | 25 | 0.028753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-157_0_3_line_28 |  | 24 | 26 | 0.0066493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-157_0_3_line_29 |  | 25 | 27 | 0.003231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-157_0_3_line_30 |  | 28 | 29 | 0.011922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-157_0_3_line_31 |  | 28 | 30 | 0.037058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-157_0_3_line_32 |  | 30 | 31 | 0.0032365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-157_0_3_line_33 |  | 32 | 33 | 0.019883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-157_0_3_line_34 |  | 32 | 34 | 0.006729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1630-157_0_3_line_35 |  | 33 | 35 | 0.022333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-157_0_3_line_36 |  | 34 | 36 | 0.046338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-157_0_3_line_37 |  | 34 | 37 | 0.026245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-157_0_3_line_38 |  | 36 | 38 | 0.023217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-157_0_3_line_39 |  | 36 | 39 | 0.13055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-157_0_3_line_40 |  | 38 | 40 | 0.074569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-157_0_3_line_41 |  | 39 | 41 | 0.074761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-157_0_3_line_42 |  | 40 | 42 | 0.10286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-157_0_3_line_43 |  | 41 | 45 | 0.13636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-157_0_3_line_44 |  | 42 | 43 | 0.068997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1630-157_0_3_line_45 |  | 45 | 46 | 0.07251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-157_0_3_trafo_2 | 0.63 MVA 20/0.4 kV | 47 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2732649.4781 | 1219762.3268 | 2732667.4206 | 1219770.7757 | 2732664.7929 | 1219776.2772 | 2732657.3274 | 1219791.757 | 2732654.5623 | 1219798.6566
1 | 2732643.4211 | 1219749.1458 | 2732642.1116 | 1219758.8579 | 2732649.4781 | 1219762.3268
2 | 2732643.4211 | 1219749.1458 | 2732639.2959 | 1219745.8846 | 2732634.661 | 1219742.6677 | 2732626.0532 | 1219738.8952 | 2732625.4632 | 1219738.7033
3 | 2732643.4211 | 1219749.1458 | 2732675.4056 | 1219762.3021 | 2732680.5511 | 1219765.764 | 2732681.665 | 1219766.2759
4 | 2732604.5137 | 1219731.8877 | 2732625.4632 | 1219738.7033
5 | 2732681.665 | 1219766.2759 | 2732696.9546 | 1219773.3022 | 2732699.4802 | 1219774.2861
6 | 2732604.5137 | 1219731.8877 | 2732605.0421 | 1219728.9527 | 2732606.6624 | 1219724.0291 | 2732608.8888 | 1219719.8419
7 | 2732604.5137 | 1219731.8877 | 2732606.7038 | 1219741.2553 | 2732612.0241 | 1219747.779 | 2732611.9101 | 1219747.9995
8 | 2732717.1798 | 1219781.1811 | 2732699.4802 | 1219774.2861
9 | 2732608.8888 | 1219719.8419 | 2732616.7106 | 1219713.244
10 | 2732590.9416 | 1219711.7358 | 2732608.8888 | 1219719.8419
11 | 2732608.8888 | 1219719.8419 | 2732624.1148 | 1219726.0638
12 | 2732609.7394 | 1219752.1984 | 2732611.9101 | 1219747.9995
13 | 2732740.8072 | 1219785.6226 | 2732717.7258 | 1219781.3938 | 2732717.1798 | 1219781.1811
14 | 2732609.7394 | 1219752.1984 | 2732614.9555 | 1219757.2631
15 | 2732590.9416 | 1219711.7358 | 2732580.6945 | 1219707.4383
16 | 2732590.9416 | 1219711.7358 | 2732602.363 | 1219700.3029 | 2732607.0715 | 1219696.4699
17 | 2732624.1148 | 1219726.0638 | 2732632.5615 | 1219717.7103
18 | 2732567.8838 | 1219723.132 | 2732569.9906 | 1219722.2671 | 2732569.7164 | 1219721.6271 | 2732569.7009 | 1219720.9596 | 2732569.9943 | 1219719.3759 | 2732571.2999 | 1219714.2674 | 2732573.9442 | 1219704.6073
19 | 2732573.9442 | 1219704.6073 | 2732580.6945 | 1219707.4383
20 | 2732573.9442 | 1219704.6073 | 2732564.4179 | 1219699.8025 | 2732561.2555 | 1219698.2975
21 | 2732567.8838 | 1219723.132 | 2732566.398 | 1219723.3769 | 2732539.0628 | 1219720.2773 | 2732522.9712 | 1219719.1739 | 2732493.0619 | 1219718.8306 | 2732473.388 | 1219720.083 | 2732452.7236 | 1219723.2039 | 2732441.3739 | 1219724.48
22 | 2732561.2555 | 1219698.2975 | 2732565.9093 | 1219686.6916
23 | 2732561.2555 | 1219698.2975 | 2732548.1981 | 1219692.3849
24 | 2732615.2204 | 1219689.8361 | 2732607.0715 | 1219696.4699
25 | 2732639.1581 | 1219711.1865 | 2732632.5615 | 1219717.7103
26 | 2732536.5898 | 1219687.1285 | 2732548.1981 | 1219692.3849
27 | 2732741.2444 | 1219788.8239 | 2732746.4805 | 1219790.6087 | 2732747.3265 | 1219796.9216 | 2732747.2911 | 1219798.511 | 2732746.7276 | 1219800.2887 | 2732744.7722 | 1219802.5359 | 2732736.8411 | 1219806.885 | 2732736.0419 | 1219808.0014
28 | 2732735.8947 | 1219814.6035 | 2732735.6504 | 1219811.262 | 2732735.7322 | 1219809.2956 | 2732736.0419 | 1219808.0014
29 | 2732741.2444 | 1219788.8239 | 2732740.8072 | 1219785.6226
30 | 2732615.2204 | 1219689.8361 | 2732621.8108 | 1219682.9661 | 2732623.3405 | 1219681.1147
31 | 2732615.2204 | 1219689.8361 | 2732592.8606 | 1219669.8888 | 2732586.3599 | 1219667.0505
32 | 2732586.3599 | 1219667.0505 | 2732583.3938 | 1219665.7554
33 | 2732518.4323 | 1219678.9067 | 2732536.5898 | 1219687.1285
34 | 2732518.4323 | 1219678.9067 | 2732512.2925 | 1219676.1123
35 | 2732536.5898 | 1219687.1285 | 2732543.936 | 1219669.155 | 2732546.7086 | 1219670.0953
36 | 2732512.2925 | 1219676.1123 | 2732487.605 | 1219664.8874 | 2732481.5868 | 1219664.1307 | 2732476.1425 | 1219664.5322 | 2732470.7499 | 1219666.0246 | 2732468.9243 | 1219667.0599
37 | 2732512.2925 | 1219676.1123 | 2732510.5818 | 1219662.2518 | 2732510.2015 | 1219658.8739 | 2732510.586 | 1219655.9245 | 2732510.3544 | 1219655.0742 | 2732505.338 | 1219655.3518
38 | 2732468.9243 | 1219667.0599 | 2732463.3537 | 1219670.2191 | 2732450.5504 | 1219681.1166
39 | 2732468.9243 | 1219667.0599 | 2732406.3815 | 1219552.4676
40 | 2732407.7453 | 1219737.2154 | 2732408.3119 | 1219731.5345 | 2732408.8323 | 1219721.4489 | 2732409.6223 | 1219718.6976 | 2732410.9365 | 1219715.9245 | 2732412.9344 | 1219713.1333 | 2732450.5504 | 1219681.1166
41 | 2732406.3815 | 1219552.4676 | 2732397.0788 | 1219554.3179 | 2732389.1628 | 1219556.9664 | 2732340.9532 | 1219587.5424
42 | 2732335.0076 | 1219793.1671 | 2732340.5099 | 1219794.5905 | 2732347.3846 | 1219795.3995 | 2732353.6354 | 1219795.2493 | 2732359.6534 | 1219794.3045 | 2732366.9709 | 1219791.9318 | 2732374.3942 | 1219787.8712 | 2732379.6428 | 1219783.9735 | 2732384.4743 | 1219779.3771 | 2732388.5234 | 1219774.4631 | 2732393.2468 | 1219768.5855 | 2732397.1139 | 1219762.978 | 2732402.301 | 1219753.3187 | 2732404.4908 | 1219748.0408 | 2732407.7453 | 1219737.2154
43 | 2732379.1875 | 1219718.4321 | 2732340.9532 | 1219587.5424
44 | 2732335.0076 | 1219793.1671 | 2732333.2245 | 1219794.84 | 2732321.8344 | 1219792.2627 | 2732312.982 | 1219790.2644 | 2732312.8742 | 1219793.409 | 2732327.7817 | 1219797.9105 | 2732330.6159 | 1219799.497 | 2732345.2827 | 1219806.6286 | 2732352.295 | 1219809.787
45 | 2732332.9664 | 1219751.1319 | 2732343.988 | 1219751.1656 | 2732351.0085 | 1219749.5203 | 2732376.2956 | 1219737.8726 | 2732378.4702 | 1219736.0083 | 2732380.3279 | 1219733.7144 | 2732382.6122 | 1219729.306 | 2732383.8741 | 1219725.1306 | 2732384.2358 | 1219718.7668 | 2732379.1875 | 1219718.4321

## bus_geodata
| x | y | coords
0 | 2732649.4781 | 1219762.3268
1 | 2732654.5623 | 1219798.6566
2 | 2732643.4211 | 1219749.1458
3 | 2732625.4632 | 1219738.7033
4 | 2732681.665 | 1219766.2759
5 | 2732604.5137 | 1219731.8877
6 | 2732699.4802 | 1219774.2861
7 | 2732608.8888 | 1219719.8419
8 | 2732611.9101 | 1219747.9995
9 | 2732717.1798 | 1219781.1811
10 | 2732609.7394 | 1219752.1984
11 | 2732614.9555 | 1219757.2631
12 | 2732616.7106 | 1219713.244
13 | 2732590.9416 | 1219711.7358
14 | 2732624.1148 | 1219726.0638
15 | 2732573.9442 | 1219704.6073
16 | 2732567.8838 | 1219723.132
17 | 2732580.6945 | 1219707.4383
18 | 2732561.2555 | 1219698.2975
19 | 2732441.3739 | 1219724.48
20 | 2732607.0715 | 1219696.4699
21 | 2732632.5615 | 1219717.7103
22 | 2732565.9093 | 1219686.6916
23 | 2732548.1981 | 1219692.3849
24 | 2732736.0419 | 1219808.0014
25 | 2732741.2444 | 1219788.8239
26 | 2732735.8947 | 1219814.6035
27 | 2732740.8072 | 1219785.6226
28 | 2732615.2204 | 1219689.8361
29 | 2732623.3405 | 1219681.1147
30 | 2732586.3599 | 1219667.0505
31 | 2732583.3938 | 1219665.7554
32 | 2732518.4323 | 1219678.9067
33 | 2732536.5898 | 1219687.1285
34 | 2732512.2925 | 1219676.1123
35 | 2732546.7086 | 1219670.0953
36 | 2732468.9243 | 1219667.0599
37 | 2732505.338 | 1219655.3518
38 | 2732450.5504 | 1219681.1166
39 | 2732406.3815 | 1219552.4676
40 | 2732407.7453 | 1219737.2154
41 | 2732340.9532 | 1219587.5424
42 | 2732335.0076 | 1219793.1671
43 | 2732352.295 | 1219809.787
44 | 2732639.1581 | 1219711.1865
45 | 2732379.1875 | 1219718.4321
46 | 2732332.9664 | 1219751.1319
47 | 2732604.5137 | 1219731.8877

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99982 | -0.0033701 | 0.0059553 | 0.0014925
1 | 0.9996 | -0.0076173 | 0.0048172 | 0.0012073
2 | 1 | 0 | -0.10357 | -0.025664
3 | 0.99919 | -0.015618 | 0.0006683 | 0.00016749
4 | 0.99816 | -0.035233 | 0.0014289 | 0.00035813
5 | 0.99834 | -0.031836 | 0 | 0
6 | 0.99733 | -0.051172 | 0.0012893 | 0.00032312
7 | 0.99787 | -0.040897 | 0 | 0
8 | 0.99831 | -0.032475 | 0.00076135 | 0.00019081
9 | 0.99655 | -0.066264 | 0.01027 | 0.0025738
10 | 0.9983 | -0.032578 | 0 | 0
11 | 0.9983 | -0.032735 | 0.0012378 | 0.00031023
12 | 0.99785 | -0.041245 | 0.0019429 | 0.00048693
13 | 0.99722 | -0.053387 | 0 | 0
14 | 0.99784 | -0.041439 | 0 | 0
15 | 0.99683 | -0.060994 | 0 | 0
16 | 0.99678 | -0.06188 | 0 | 0
17 | 0.99698 | -0.058085 | 0.0014592 | 0.00036571
18 | 0.99657 | -0.066016 | 0 | 0
19 | 0.9965 | -0.067362 | 0.0024561 | 0.00061555
20 | 0.99698 | -0.058134 | 0.0011618 | 0.00029118
21 | 0.99782 | -0.041832 | 0.0012151 | 0.00030453
22 | 0.99655 | -0.066316 | 0.0013688 | 0.00034307
23 | 0.99632 | -0.070753 | 0.0027218 | 0.00068216
24 | 0.99476 | -0.10078 | 0.0129 | 0.003233
25 | 0.99568 | -0.083055 | 0 | 0
26 | 0.99462 | -0.10338 | 0.022136 | 0.0055477
27 | 0.99578 | -0.081065 | 0 | 0
28 | 0.99687 | -0.060164 | 0 | 0
29 | 0.99686 | -0.060331 | 0.00079755 | 0.00019988
30 | 0.99653 | -0.066809 | 0.00071622 | 0.0001795
31 | 0.9965 | -0.067348 | 0.0095021 | 0.0023814
32 | 0.99586 | -0.079658 | 0 | 0
33 | 0.99614 | -0.074357 | 0 | 0
34 | 0.99577 | -0.081453 | 0 | 0
35 | 0.99612 | -0.074721 | 0.00092804 | 0.00023259
36 | 0.99519 | -0.092741 | 0.0058237 | 0.0014596
37 | 0.99574 | -0.082063 | 0.001323 | 0.00033156
38 | 0.99508 | -0.0948 | 0.0031343 | 0.00078553
39 | 0.99483 | -0.0996 | 0 | 0
40 | 0.99495 | -0.097298 | 0 | 0
41 | 0.99463 | -0.10353 | 0.0012383 | 0.00031035
42 | 0.99477 | -0.10074 | 0 | 0
43 | 0.99465 | -0.10304 | 0.0018958 | 0.00047514
44 | 0.99782 | -0.041941 | 0.00067206 | 0.00016843
45 | 0.99441 | -0.1077 | 0 | 0
46 | 0.9943 | -0.10992 | 0.0017345 | 0.0004347
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0048182 | 0.0012073 | -0.0048172 | -0.0012073 | 9.7469e-07 | -3.8973e-08 | 0.0071707 | 0.0071709 | 0.0071709 | 0.99982 | -0.0033701 | 0.9996 | -0.0076173 | 1.97
1 | -0.010774 | -0.0026998 | 0.010775 | 0.0027007 | 1.7298e-06 | 8.717e-07 | 0.016034 | 0.016034 | 0.016034 | 0.99982 | -0.0033701 | 1 | 0 | 4.4049
2 | 0.042907 | 0.010795 | -0.042875 | -0.010775 | 3.1992e-05 | 2.0201e-05 | 0.063861 | 0.063861 | 0.063861 | 1 | 0 | 0.99919 | -0.015618 | 17.5442
3 | 0.048233 | 0.012168 | -0.048152 | -0.012117 | 8.1219e-05 | 5.143e-05 | 0.0718 | 0.0718 | 0.0718 | 1 | 0 | 0.99816 | -0.035233 | 19.7253
4 | 0.042207 | 0.010607 | -0.042174 | -0.010586 | 3.265e-05 | 2.0607e-05 | 0.062865 | 0.062866 | 0.062866 | 0.99919 | -0.015618 | 0.99834 | -0.031836 | 17.2708
5 | 0.046723 | 0.011759 | -0.046688 | -0.011736 | 3.5562e-05 | 2.2504e-05 | 0.06967 | 0.06967 | 0.06967 | 0.99816 | -0.035233 | 0.99733 | -0.051172 | 19.1401
6 | 0.040175 | 0.010086 | -0.040157 | -0.010075 | 1.7357e-05 | 1.094e-05 | 0.059886 | 0.059886 | 0.059886 | 0.99834 | -0.031836 | 0.99787 | -0.040897 | 16.4522
7 | 0.0019992 | 0.00050069 | -0.0019992 | -0.00050089 | 6.0887e-08 | -2.0013e-07 | 0.0029797 | 0.0029798 | 0.0029798 | 0.99834 | -0.031836 | 0.99831 | -0.032475 | 0.81863
8 | 0.045398 | 0.011413 | -0.045366 | -0.011392 | 3.2693e-05 | 2.0676e-05 | 0.067746 | 0.067747 | 0.067747 | 0.99733 | -0.051172 | 0.99655 | -0.066264 | 18.6117
9 | 0.0019429 | 0.00048682 | -0.0019429 | -0.00048693 | 3.216e-08 | -1.1288e-07 | 0.0028972 | 0.0028972 | 0.0028972 | 0.99787 | -0.040897 | 0.99785 | -0.041245 | 0.79595
10 | 0.036327 | 0.0091154 | -0.036306 | -0.0091019 | 2.1621e-05 | 1.3581e-05 | 0.054175 | 0.054175 | 0.054175 | 0.99787 | -0.040897 | 0.99722 | -0.053387 | 14.8832
11 | 0.0018872 | 0.00047253 | -0.0018872 | -0.00047271 | 4.8724e-08 | -1.8314e-07 | 0.0028141 | 0.0028142 | 0.0028142 | 0.99787 | -0.040897 | 0.99784 | -0.041439 | 0.77312
12 | 0.0012378 | 0.00031008 | -0.0012378 | -0.00031014 | 6.0338e-09 | -5.7942e-08 | 0.001845 | 0.001845 | 0.001845 | 0.99831 | -0.032475 | 0.9983 | -0.032578 | 0.50687
13 | 0.035096 | 0.0088186 | -0.035071 | -0.0088031 | 2.4777e-05 | 1.5544e-05 | 0.052412 | 0.052412 | 0.052412 | 0.99655 | -0.066264 | 0.99578 | -0.081065 | 14.399
14 | 0.0012378 | 0.00031014 | -0.0012378 | -0.00031023 | 9.281e-09 | -8.9119e-08 | 0.001845 | 0.001845 | 0.001845 | 0.9983 | -0.032578 | 0.9983 | -0.032735 | 0.50688
15 | 0.024121 | 0.0060463 | -0.024115 | -0.006043 | 5.398e-06 | 3.3098e-06 | 0.035992 | 0.035992 | 0.035992 | 0.99722 | -0.053387 | 0.99698 | -0.058085 | 9.888
16 | 0.012185 | 0.0030556 | -0.012182 | -0.0030541 | 2.7563e-06 | 1.474e-06 | 0.018183 | 0.018183 | 0.018183 | 0.99722 | -0.053387 | 0.99698 | -0.058134 | 4.9952
17 | 0.0018872 | 0.00047271 | -0.0018872 | -0.00047285 | 3.5281e-08 | -1.326e-07 | 0.0028142 | 0.0028142 | 0.0028142 | 0.99784 | -0.041439 | 0.99782 | -0.041832 | 0.77313
18 | 0.0024568 | 0.0006141 | -0.0024567 | -0.0006143 | 1.0357e-07 | -2.0147e-07 | 0.0036668 | 0.0036669 | 0.0036669 | 0.99683 | -0.060994 | 0.99678 | -0.06188 | 1.0074
19 | -0.022653 | -0.0056754 | 0.022656 | 0.0056773 | 3.1386e-06 | 1.9133e-06 | 0.033814 | 0.033814 | 0.033814 | 0.99683 | -0.060994 | 0.99698 | -0.058085 | 9.2897
20 | 0.020196 | 0.0050613 | -0.020191 | -0.0050583 | 4.8301e-06 | 2.9066e-06 | 0.030148 | 0.030148 | 0.030148 | 0.99683 | -0.060994 | 0.99657 | -0.066016 | 8.2823
21 | 0.0024567 | 0.0006143 | -0.0024561 | -0.00061555 | 6.4094e-07 | -1.2459e-06 | 0.0036669 | 0.0036675 | 0.0036675 | 0.99678 | -0.06188 | 0.9965 | -0.067362 | 1.0076
22 | 0.0013689 | 0.00034291 | -0.0013688 | -0.00034306 | 1.9585e-08 | -1.5036e-07 | 0.0020439 | 0.0020439 | 0.0020439 | 0.99657 | -0.066016 | 0.99655 | -0.066316 | 0.56151
23 | 0.018822 | 0.0047154 | -0.018818 | -0.0047129 | 4.2454e-06 | 2.5303e-06 | 0.028104 | 0.028104 | 0.028104 | 0.99657 | -0.066016 | 0.99632 | -0.070753 | 7.7208
24 | 0.01102 | 0.0027629 | -0.011019 | -0.0027624 | 1.0661e-06 | 5.4529e-07 | 0.016449 | 0.016449 | 0.016449 | 0.99698 | -0.058134 | 0.99687 | -0.060164 | 4.5189
25 | 0.00067206 | 0.00016831 | -0.00067206 | -0.00016843 | 3.4944e-09 | -1.1895e-07 | 0.0010022 | 0.0010022 | 0.0010022 | 0.99782 | -0.041832 | 0.99782 | -0.041941 | 0.27534
26 | 0.016096 | 0.0040307 | -0.016094 | -0.0040291 | 2.7614e-06 | 1.6014e-06 | 0.024039 | 0.024039 | 0.024039 | 0.99632 | -0.070753 | 0.99614 | -0.074357 | 6.6041
27 | -0.035038 | -0.0087824 | 0.035068 | 0.008801 | 2.962e-05 | 1.8583e-05 | 0.052413 | 0.052412 | 0.052413 | 0.99476 | -0.10078 | 0.99568 | -0.083055 | 14.3991
28 | 0.022138 | 0.0055494 | -0.022136 | -0.0055477 | 2.7346e-06 | 1.6638e-06 | 0.033116 | 0.033116 | 0.033116 | 0.99476 | -0.10078 | 0.99462 | -0.10338 | 9.0979
29 | -0.035068 | -0.008801 | 0.035071 | 0.0088031 | 3.3284e-06 | 2.0882e-06 | 0.052412 | 0.052412 | 0.052412 | 0.99568 | -0.083055 | 0.99578 | -0.081065 | 14.399
30 | 0.00079755 | 0.00019973 | -0.00079755 | -0.00019988 | 6.3358e-09 | -1.5137e-07 | 0.0011904 | 0.0011905 | 0.0011905 | 0.99687 | -0.060164 | 0.99686 | -0.060331 | 0.32706
31 | 0.010222 | 0.0025626 | -0.010219 | -0.0025611 | 3.2353e-06 | 1.5876e-06 | 0.015258 | 0.015258 | 0.015258 | 0.99687 | -0.060164 | 0.99653 | -0.066809 | 4.1919
32 | 0.0095023 | 0.0023816 | -0.0095021 | -0.0023814 | 2.4435e-07 | 1.1422e-07 | 0.014189 | 0.014189 | 0.014189 | 0.99653 | -0.066809 | 0.9965 | -0.067348 | 3.8981
33 | -0.015162 | -0.0037946 | 0.015165 | 0.0037968 | 3.826e-06 | 2.1899e-06 | 0.022653 | 0.022653 | 0.022653 | 0.99586 | -0.079658 | 0.99614 | -0.074357 | 6.2233
34 | 0.015162 | 0.0037946 | -0.01516 | -0.0037939 | 1.2949e-06 | 7.4116e-07 | 0.022653 | 0.022653 | 0.022653 | 0.99586 | -0.079658 | 0.99577 | -0.081453 | 6.2233
35 | 0.00092805 | 0.00023231 | -0.00092804 | -0.00023259 | 1.6094e-08 | -2.8043e-07 | 0.0013862 | 0.0013863 | 0.0013863 | 0.99614 | -0.074357 | 0.99612 | -0.074721 | 0.38086
36 | 0.013837 | 0.0034627 | -0.01383 | -0.0034585 | 7.4285e-06 | 4.1518e-06 | 0.020676 | 0.020676 | 0.020676 | 0.99577 | -0.081453 | 0.99519 | -0.092741 | 5.6802
37 | 0.001323 | 0.00033125 | -0.001323 | -0.00033156 | 3.8465e-08 | -3.1677e-07 | 0.0019769 | 0.001977 | 0.001977 | 0.99577 | -0.081453 | 0.99574 | -0.082063 | 0.54313
38 | 0.0050313 | 0.001258 | -0.0050309 | -0.0012579 | 4.9261e-07 | 1.3633e-08 | 0.0075219 | 0.007522 | 0.007522 | 0.99519 | -0.092741 | 0.99508 | -0.0948 | 2.0665
39 | 0.0029748 | 0.00074099 | -0.0029739 | -0.00074206 | 9.6802e-07 | -1.0761e-06 | 0.0044464 | 0.004447 | 0.004447 | 0.99519 | -0.092741 | 0.99483 | -0.0996 | 1.2217
40 | 0.0018966 | 0.00047241 | -0.0018963 | -0.00047324 | 2.2478e-07 | -8.247e-07 | 0.0028351 | 0.0028354 | 0.0028354 | 0.99508 | -0.0948 | 0.99495 | -0.097298 | 0.77896
41 | 0.0029739 | 0.00074206 | -0.0029733 | -0.00074268 | 5.5447e-07 | -6.1564e-07 | 0.004447 | 0.0044474 | 0.0044474 | 0.99483 | -0.0996 | 0.99463 | -0.10353 | 1.2218
42 | 0.0018963 | 0.00047324 | -0.001896 | -0.00047438 | 3.1014e-07 | -1.1371e-06 | 0.0028354 | 0.0028359 | 0.0028359 | 0.99495 | -0.097298 | 0.99477 | -0.10074 | 0.77908
43 | 0.001735 | 0.00043233 | -0.0017347 | -0.00043388 | 3.4437e-07 | -1.549e-06 | 0.0025948 | 0.0025954 | 0.0025954 | 0.99463 | -0.10353 | 0.99441 | -0.1077 | 0.71302
44 | 0.001896 | 0.00047438 | -0.0018958 | -0.00047514 | 2.081e-07 | -7.6246e-07 | 0.0028359 | 0.0028362 | 0.0028362 | 0.99477 | -0.10074 | 0.99465 | -0.10304 | 0.77917
45 | 0.0017347 | 0.00043388 | -0.0017345 | -0.0004347 | 1.8319e-07 | -8.2333e-07 | 0.0025954 | 0.0025957 | 0.0025957 | 0.99441 | -0.1077 | 0.9943 | -0.10992 | 0.71311

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.10357 | 0.025664

## res_load
| p_mw | q_mvar
0 | 0.0059553 | 0.0014925
1 | 0.0048172 | 0.0012073
2 | 0.0006683 | 0.00016749
3 | 0.0014289 | 0.00035813
4 | 0.0012893 | 0.00032312
5 | 0.00076135 | 0.00019081
6 | 0.01027 | 0.0025738
7 | 0.0012378 | 0.00031023
8 | 0.0019429 | 0.00048693
9 | 0.0014592 | 0.00036571
10 | 0.0024561 | 0.00061555
11 | 0.0011618 | 0.00029118
12 | 0.0012151 | 0.00030453
13 | 0.0013688 | 0.00034307
14 | 0.0027218 | 0.00068216
15 | 0.0129 | 0.003233
16 | 0.022136 | 0.0055477
17 | 0.00079755 | 0.00019988
18 | 0.00071622 | 0.0001795
19 | 0.0095021 | 0.0023814
20 | 0.00092804 | 0.00023259
21 | 0.0058237 | 0.0014596
22 | 0.001323 | 0.00033156
23 | 0.0031343 | 0.00078553
24 | 0.0012383 | 0.00031035
25 | 0.0018958 | 0.00047514
26 | 0.00067206 | 0.00016843
27 | 0.0017345 | 0.0004347

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1