## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-26_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-26_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-26_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-26_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-26_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-26_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1630-26_0_5_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_1630-26_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1630-26_0_5_node_34 | 0.4 | n |  | TRUE
9 | bus_LV_1630-26_0_5_node_37 | 0.4 | n |  | TRUE
10 | bus_LV_1630-26_0_5_node_59 | 0.4 | n |  | TRUE
11 | bus_LV_1630-26_0_5_node_49 | 0.4 | n |  | TRUE
12 | bus_LV_1630-26_0_5_node_46 | 0.4 | n |  | TRUE
13 | bus_LV_1630-26_0_5_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1630-26_0_5_node_129 | 0.4 | n |  | TRUE
15 | bus_LV_1630-26_0_5_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_1630-26_0_5_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1630-26_0_5_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_1630-26_0_5_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_1630-26_0_5_node_39 | 0.4 | n |  | TRUE
20 | bus_LV_1630-26_0_5_node_128 | 0.4 | n |  | TRUE
21 | bus_LV_1630-26_0_5_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_1630-26_0_5_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_1630-26_0_5_node_40 | 0.4 | n |  | TRUE
24 | bus_LV_1630-26_0_5_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_1630-26_0_5_node_50 | 0.4 | n |  | TRUE
26 | bus_LV_1630-26_0_5_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_1630-26_0_5_node_7 | 0.4 | n |  | TRUE
28 | bus_LV_1630-26_0_5_node_8 | 0.4 | n |  | TRUE
29 | bus_LV_1630-26_0_5_node_9 | 0.4 | n |  | TRUE
30 | bus_LV_1630-26_0_5_node_10 | 0.4 | n |  | TRUE
31 | bus_LV_1630-26_0_5_node_11 | 0.4 | n |  | TRUE
32 | bus_LV_1630-26_0_5_node_12 | 0.4 | n |  | TRUE
33 | bus_LV_1630-26_0_5_node_58 | 0.4 | n |  | TRUE
34 | bus_LV_1630-26_0_5_node_13 | 0.4 | n |  | TRUE
35 | bus_LV_1630-26_0_5_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_1630-26_0_5_node_139 | 0.4 | n |  | TRUE
37 | bus_LV_1630-26_0_5_node_138 | 0.4 | n |  | TRUE
38 | bus_LV_1630-26_0_5_node_14 | 0.4 | n |  | TRUE
39 | bus_LV_1630-26_0_5_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_1630-26_0_5_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_1630-26_0_5_node_16 | 0.4 | n |  | TRUE
42 | bus_LV_1630-26_0_5_node_17 | 0.4 | n |  | TRUE
43 | bus_LV_1630-26_0_5_node_18 | 0.4 | n |  | TRUE
44 | bus_LV_1630-26_0_5_node_19 | 0.4 | n |  | TRUE
45 | bus_LV_1630-26_0_5_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_1630-26_0_5_node_20 | 0.4 | n |  | TRUE
47 | bus_LV_1630-26_0_5_node_132 | 0.4 | n |  | TRUE
48 | bus_LV_1630-26_0_5_node_120 | 0.4 | n |  | TRUE
49 | bus_LV_1630-26_0_5_node_136 | 0.4 | n |  | TRUE
50 | bus_LV_1630-26_0_5_node_23 | 0.4 | n |  | TRUE
51 | bus_LV_1630-26_0_5_node_74 | 0.4 | n |  | TRUE
52 | bus_LV_1630-26_0_5_node_134 | 0.4 | n |  | TRUE
53 | bus_LV_1630-26_0_5_node_75 | 0.4 | n |  | TRUE
54 | bus_LV_1630-26_0_5_node_26 | 0.4 | n |  | TRUE
55 | bus_LV_1630-26_0_5_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_1630-26_0_5_node_100 | 0.4 | n |  | TRUE
57 | bus_LV_1630-26_0_5_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_1630-26_0_5_node_121 | 0.4 | n |  | TRUE
59 | bus_LV_1630-26_0_5_node_119 | 0.4 | n |  | TRUE
60 | bus_LV_1630-26_0_5_node_90 | 0.4 | n |  | TRUE
61 | bus_LV_1630-26_0_5_node_88 | 0.4 | n |  | TRUE
62 | bus_LV_1630-26_0_5_node_102 | 0.4 | n |  | TRUE
63 | bus_LV_1630-26_0_5_node_135 | 0.4 | n |  | TRUE
64 | bus_LV_1630-26_0_5_node_89 | 0.4 | n |  | TRUE
65 | bus_LV_1630-26_0_5_node_87 | 0.4 | n |  | TRUE
66 | bus_LV_1630-26_0_5_node_105 | 0.4 | n |  | TRUE
67 | bus_LV_1630-26_0_5_node_117 | 0.4 | n |  | TRUE
68 | bus_LV_1630-26_0_5_node_118 | 0.4 | n |  | TRUE
69 | bus_LV_1630-26_0_5_node_99 | 0.4 | n |  | TRUE
70 | bus_LV_1630-26_0_5_node_30 | 0.4 | n |  | TRUE
71 | bus_LV_1630-26_0_5_node_31 | 0.4 | n |  | TRUE
72 | bus_LV_1630-26_0_5_node_33 | 0.4 | n |  | TRUE
73 | bus_LV_1630-26_0_5_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_1630-26_0_5_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_1630-26_0_5_node_130 | 0.4 | n |  | TRUE
76 | bus_LV_1630-26_0_5_node_41 | 0.4 | n |  | TRUE
77 | bus_LV_1630-26_0_5_node_43 | 0.4 | n |  | TRUE
78 | bus_LV_1630-26_0_5_node_45 | 0.4 | n |  | TRUE
79 | bus_LV_1630-26_0_5_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_1630-26_0_5_node_126 | 0.4 | n |  | TRUE
81 | bus_LV_1630-26_0_5_node_92 | 0.4 | n |  | TRUE
82 | bus_LV_1630-26_0_5_node_54 | 0.4 | n |  | TRUE
83 | bus_LV_1630-26_0_5_node_125 | 0.4 | n |  | TRUE
84 | bus_LV_1630-26_0_5_node_48 | 0.4 | n |  | TRUE
85 | bus_LV_1630-26_0_5_node_131 | 0.4 | n |  | TRUE
86 | bus_LV_1630-26_0_5_node_107 | 0.4 | n |  | TRUE
87 | bus_LV_1630-26_0_5_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_1630-26_0_5_node_106 | 0.4 | n |  | TRUE
89 | bus_LV_1630-26_0_5_node_66 | 0.4 | n |  | TRUE
90 | bus_LV_1630-26_0_5_node_108 | 0.4 | n |  | TRUE
91 | bus_LV_1630-26_0_5_node_51 | 0.4 | n |  | TRUE
92 | bus_LV_1630-26_0_5_node_52 | 0.4 | n |  | TRUE
93 | bus_LV_1630-26_0_5_node_53 | 0.4 | n |  | TRUE
94 | bus_LV_1630-26_0_5_node_61 | 0.4 | n |  | TRUE
95 | bus_LV_1630-26_0_5_node_97 | 0.4 | n |  | TRUE
96 | bus_LV_1630-26_0_5_node_104 | 0.4 | n |  | TRUE
97 | bus_LV_1630-26_0_5_node_91 | 0.4 | n |  | TRUE
98 | bus_LV_1630-26_0_5_node_96 | 0.4 | n |  | TRUE
99 | bus_LV_1630-26_0_5_node_62 | 0.4 | n |  | TRUE
100 | bus_LV_1630-26_0_5_node_63 | 0.4 | n |  | TRUE
101 | bus_LV_1630-26_0_5_node_64 | 0.4 | n |  | TRUE
102 | bus_LV_1630-26_0_5_node_65 | 0.4 | n |  | TRUE
103 | bus_LV_1630-26_0_5_node_67 | 0.4 | n |  | TRUE
104 | bus_LV_1630-26_0_5_node_80 | 0.4 | n |  | TRUE
105 | bus_LV_1630-26_0_5_node_76 | 0.4 | n |  | TRUE
106 | bus_LV_1630-26_0_5_node_70 | 0.4 | n |  | TRUE
107 | bus_LV_1630-26_0_5_node_124 | 0.4 | n |  | TRUE
108 | bus_LV_1630-26_0_5_node_77 | 0.4 | n |  | TRUE
109 | bus_LV_1630-26_0_5_node_73 | 0.4 | n |  | TRUE
110 | bus_LV_1630-26_0_5_node_68 | 0.4 | n |  | TRUE
111 | bus_LV_1630-26_0_5_node_69 | 0.4 | n |  | TRUE
112 | bus_LV_1630-26_0_5_node_71 | 0.4 | n |  | TRUE
113 | bus_LV_1630-26_0_5_node_72 | 0.4 | n |  | TRUE
114 | bus_LV_1630-26_0_5_node_94 | 0.4 | n |  | TRUE
115 | bus_LV_1630-26_0_5_node_123 | 0.4 | n |  | TRUE
116 | bus_LV_1630-26_0_5_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_1630-26_0_5_node_122 | 0.4 | n |  | TRUE
118 | bus_LV_1630-26_0_5_node_103 | 0.4 | n |  | TRUE
119 | bus_LV_1630-26_0_5_node_78 | 0.4 | n |  | TRUE
120 | bus_LV_1630-26_0_5_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_1630-26_0_5_node_137 | 0.4 | n |  | TRUE
122 | bus_LV_1630-26_0_5_node_127 | 0.4 | n |  | TRUE
123 | bus_LV_1630-26_0_5_node_81 | 0.4 | n |  | TRUE
124 | bus_LV_1630-26_0_5_node_82 | 0.4 | n |  | TRUE
125 | bus_LV_1630-26_0_5_node_83 | 0.4 | n |  | TRUE
126 | bus_LV_1630-26_0_5_node_84 | 0.4 | n |  | TRUE
127 | bus_LV_1630-26_0_5_node_85 | 0.4 | n |  | TRUE
128 | bus_LV_1630-26_0_5_node_86 | 0.4 | n |  | TRUE
129 | bus_LV_1630-26_0_5_node_101 | 0.4 | n |  | TRUE
130 | bus_LV_1630-26_0_5_node_114 | 0.4 | n |  | TRUE
131 | bus_LV_1630-26_0_5_node_115 | 0.4 | n |  | TRUE
132 | bus_LV_1630-26_0_5_node_113 | 0.4 | n |  | TRUE
133 | bus_LV_1630-26_0_5_node_116 | 0.4 | n |  | TRUE
134 | bus_LV_1630-26_0_5_node_109 | 0.4 | n |  | TRUE
135 | bus_LV_1630-26_0_5_node_110 | 0.4 | n |  | TRUE
136 | bus_LV_1630-26_0_5_node_111 | 0.4 | n |  | TRUE
137 | bus_LV_1630-26_0_5_node_112 | 0.4 | n |  | TRUE
138 | bus_LV_1630-26_0_5_node_133 | 0.4 | n |  | TRUE
139 | bus_MV_152_0_node_32 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-26_0_5_load_0 | 0 | 0.002777 | 0.00069597 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-26_0_5_load_1 | 1 | 0.0041162 | 0.0010316 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-26_0_5_load_4 | 4 | 0.00409 | 0.0010251 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-26_0_5_load_28 | 6 | 0.0033977 | 0.00085154 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-26_0_5_load_59 | 10 | 0.0074976 | 0.0018791 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-26_0_5_load_49 | 11 | 0.0067851 | 0.0017005 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-26_0_5_load_46 | 12 | 0.0072615 | 0.0018199 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-26_0_5_load_29 | 13 | 0.010477 | 0.0026258 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-26_0_5_load_129 | 14 | 0.008642 | 0.0021659 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-26_0_5_load_128 | 20 | 0.0086721 | 0.0021734 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-26_0_5_load_35 | 24 | 0.0058034 | 0.0014545 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-26_0_5_load_50 | 25 | 0.004881 | 0.0012233 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-26_0_5_load_7 | 27 | 0.0072885 | 0.0018267 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-26_0_5_load_8 | 28 | 0.0090392 | 0.0022654 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-26_0_5_load_11 | 31 | 0.010719 | 0.0026864 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-26_0_5_load_12 | 32 | 0.0060866 | 0.0015254 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-26_0_5_load_44 | 35 | 0.006033 | 0.001512 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-26_0_5_load_139 | 36 | 0.0052688 | 0.0013205 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-26_0_5_load_138 | 37 | 0.0048502 | 0.0012156 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-26_0_5_load_14 | 38 | 0.0048271 | 0.0012098 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-26_0_5_load_15 | 39 | 0.0066052 | 0.0016554 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-26_0_5_load_16 | 41 | 0.0070882 | 0.0017765 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-26_0_5_load_19 | 44 | 0.0071605 | 0.0017946 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-26_0_5_load_132 | 47 | 0.00436 | 0.0010927 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-26_0_5_load_136 | 49 | 0.037525 | 0.0094047 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-26_0_5_load_74 | 51 | 0.0031533 | 0.00079028 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-26_0_5_load_134 | 52 | 0.0013735 | 0.00034424 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-26_0_5_load_100 | 56 | 0.0013419 | 0.00033632 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-26_0_5_load_57 | 57 | 0.0016611 | 0.00041632 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-26_0_5_load_119 | 59 | 0.015469 | 0.0038768 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-26_0_5_load_102 | 62 | 0.00071096 | 0.00017818 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1630-26_0_5_load_135 | 63 | 0.0023672 | 0.00059329 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1630-26_0_5_load_89 | 64 | 0.0018892 | 0.00047347 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1630-26_0_5_load_87 | 65 | 0.00082286 | 0.00020623 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1630-26_0_5_load_117 | 67 | 0.001376 | 0.00034485 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1630-26_0_5_load_118 | 68 | 0.0022801 | 0.00057144 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1630-26_0_5_load_99 | 69 | 0.0014739 | 0.00036939 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1630-26_0_5_load_30 | 70 | 0.0061879 | 0.0015508 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1630-26_0_5_load_31 | 71 | 0.0032514 | 0.00081488 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1630-26_0_5_load_55 | 73 | 0.0106 | 0.0026566 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1630-26_0_5_load_56 | 74 | 0.0048637 | 0.001219 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1630-26_0_5_load_130 | 75 | 0.0020536 | 0.00051467 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1630-26_0_5_load_41 | 76 | 0.010646 | 0.0026681 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1630-26_0_5_load_43 | 77 | 0.0079233 | 0.0019858 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1630-26_0_5_load_126 | 80 | 0.0034355 | 0.00086103 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1630-26_0_5_load_92 | 81 | 0.0063726 | 0.0015971 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1630-26_0_5_load_131 | 85 | 0.0099145 | 0.0024848 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1630-26_0_5_load_106 | 88 | 0.0058585 | 0.0014683 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1630-26_0_5_load_108 | 90 | 0.0071794 | 0.0017993 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1630-26_0_5_load_51 | 91 | 0.0055595 | 0.0013933 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1630-26_0_5_load_52 | 92 | 0.0044399 | 0.0011127 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1630-26_0_5_load_53 | 93 | 0.005886 | 0.0014752 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1630-26_0_5_load_104 | 96 | 0.0057856 | 0.00145 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1630-26_0_5_load_91 | 97 | 0.0039879 | 0.00099947 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1630-26_0_5_load_96 | 98 | 0.003655 | 0.00091604 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1630-26_0_5_load_62 | 99 | 0.0050083 | 0.0012552 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1630-26_0_5_load_63 | 100 | 0.0030322 | 0.00075995 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1630-26_0_5_load_65 | 102 | 0.0026191 | 0.00065641 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1630-26_0_5_load_67 | 103 | 0.0067234 | 0.0016851 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1630-26_0_5_load_76 | 105 | 0.002986 | 0.00074837 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1630-26_0_5_load_124 | 107 | 0.012756 | 0.0031969 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1630-26_0_5_load_77 | 108 | 0.0044266 | 0.0011094 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1630-26_0_5_load_73 | 109 | 0.0055005 | 0.0013785 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1630-26_0_5_load_68 | 110 | 0.0043502 | 0.0010903 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1630-26_0_5_load_71 | 112 | 0.0033457 | 0.00083852 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1630-26_0_5_load_94 | 114 | 0.0058672 | 0.0014705 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1630-26_0_5_load_122 | 117 | 0.013317 | 0.0033376 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1630-26_0_5_load_103 | 118 | 0.0012543 | 0.00031435 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1630-26_0_5_load_137 | 121 | 0.003665 | 0.00091854 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1630-26_0_5_load_127 | 122 | 0.015417 | 0.003864 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1630-26_0_5_load_81 | 123 | 0.0015389 | 0.00038568 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1630-26_0_5_load_85 | 127 | 0.033739 | 0.0084557 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1630-26_0_5_load_86 | 128 | 0.00073721 | 0.00018476 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1630-26_0_5_load_101 | 129 | 0.062427 | 0.015646 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1630-26_0_5_load_115 | 131 | 0.0092655 | 0.0023221 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1630-26_0_5_load_113 | 132 | 0.0023058 | 0.00057789 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1630-26_0_5_load_116 | 133 | 0.0014165 | 0.000355 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1630-26_0_5_load_109 | 134 | 0.001047 | 0.00026241 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1630-26_0_5_load_111 | 136 | 0.00069177 | 0.00017337 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1630-26_0_5_load_133 | 138 | 0.025863 | 0.0064819 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-26_0_5_line_0 |  | 0 | 1 | 0.0087468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_1630-26_0_5_line_1 |  | 0 | 2 | 0.004022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1630-26_0_5_line_2 |  | 1 | 3 | 0.04301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1630-26_0_5_line_3 |  | 2 | 4 | 0.010653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-26_0_5_line_4 |  | 2 | 5 | 0.021282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_1630-26_0_5_line_5 |  | 3 | 6 | 0.010007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1630-26_0_5_line_6 |  | 5 | 11 | 0.019651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1630-26_0_5_line_7 |  | 5 | 12 | 0.014773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1630-26_0_5_line_8 |  | 6 | 13 | 0.0031408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1630-26_0_5_line_9 |  | 7 | 8 | 0.012535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-26_0_5_line_10 |  | 7 | 9 | 0.006371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1630-26_0_5_line_11 |  | 7 | 10 | 0.014277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1630-26_0_5_line_12 |  | 8 | 14 | 0.020599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-26_0_5_line_13 |  | 8 | 15 | 0.008015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-26_0_5_line_14 |  | 9 | 24 | 0.028126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1630-26_0_5_line_15 |  | 10 | 17 | 0.0086484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1630-26_0_5_line_16 |  | 11 | 25 | 0.029572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1630-26_0_5_line_17 |  | 12 | 26 | 0.038845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_1630-26_0_5_line_18 |  | 13 | 55 | 0.095875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-26_0_5_line_19 |  | 15 | 72 | 0.046071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-26_0_5_line_20 |  | 15 | 70 | 0.046178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-26_0_5_line_21 |  | 16 | 17 | 0.010927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1630-26_0_5_line_22 |  | 16 | 18 | 0.048723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1630-26_0_5_line_23 |  | 18 | 49 | 0.017271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-26_0_5_line_24 |  | 18 | 43 | 0.046495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1630-26_0_5_line_25 |  | 19 | 20 | 0.044967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-26_0_5_line_26 |  | 19 | 21 | 0.084576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-26_0_5_line_27 |  | 19 | 22 | 0.12289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-26_0_5_line_28 |  | 21 | 23 | 0.016768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1630-26_0_5_line_29 |  | 21 | 24 | 0.016051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1630-26_0_5_line_30 |  | 22 | 75 | 0.10917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-26_0_5_line_31 |  | 23 | 25 | 0.010136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_1630-26_0_5_line_32 |  | 26 | 30 | 0.023829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1630-26_0_5_line_33 |  | 27 | 28 | 0.017911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1630-26_0_5_line_34 |  | 27 | 29 | 0.015613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_1630-26_0_5_line_35 |  | 28 | 30 | 0.0073827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1630-26_0_5_line_36 |  | 29 | 31 | 0.012191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-26_0_5_line_37 |  | 29 | 32 | 0.0015759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1630-26_0_5_line_38 |  | 30 | 33 | 0.025647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-26_0_5_line_39 |  | 31 | 34 | 0.015582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-26_0_5_line_40 |  | 32 | 35 | 0.010482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1630-26_0_5_line_41 |  | 33 | 36 | 0.001885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-26_0_5_line_42 |  | 33 | 37 | 0.010094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-26_0_5_line_43 |  | 34 | 38 | 0.004963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-26_0_5_line_44 |  | 34 | 39 | 0.005428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1630-26_0_5_line_45 |  | 35 | 40 | 0.018787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_1630-26_0_5_line_46 |  | 40 | 78 | 0.031919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_1630-26_0_5_line_47 |  | 40 | 76 | 0.015411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1630-26_0_5_line_48 |  | 41 | 42 | 0.0077998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1630-26_0_5_line_49 |  | 41 | 43 | 0.0097126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1630-26_0_5_line_50 |  | 42 | 44 | 0.022231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1630-26_0_5_line_51 |  | 43 | 45 | 0.07693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1630-26_0_5_line_52 |  | 45 | 50 | 0.014475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1630-26_0_5_line_53 |  | 45 | 51 | 0.0364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1630-26_0_5_line_54 |  | 45 | 46 | 0.068646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1630-26_0_5_line_55 |  | 46 | 47 | 0.021159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1630-26_0_5_line_56 |  | 46 | 48 | 0.04127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1630-26_0_5_line_57 |  | 48 | 58 | 0.11866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1630-26_0_5_line_58 |  | 48 | 59 | 0.029372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1630-26_0_5_line_59 |  | 50 | 52 | 0.07106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1630-26_0_5_line_60 |  | 50 | 53 | 0.048831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1630-26_0_5_line_61 |  | 53 | 60 | 0.054217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1630-26_0_5_line_62 |  | 53 | 61 | 0.01437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1630-26_0_5_line_63 |  | 53 | 62 | 0.011258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1630-26_0_5_line_64 |  | 54 | 55 | 0.032537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1630-26_0_5_line_65 |  | 54 | 56 | 0.044431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1630-26_0_5_line_66 |  | 55 | 57 | 0.012991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1630-26_0_5_line_67 |  | 56 | 69 | 0.013544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1630-26_0_5_line_68 |  | 57 | 68 | 0.015609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1630-26_0_5_line_69 |  | 58 | 138 | 0.011704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1630-26_0_5_line_70 |  | 60 | 63 | 0.032136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1630-26_0_5_line_71 |  | 61 | 64 | 0.011813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1630-26_0_5_line_72 |  | 61 | 65 | 0.059866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1630-26_0_5_line_73 |  | 62 | 118 | 0.058642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1630-26_0_5_line_74 |  | 66 | 67 | 0.01652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1630-26_0_5_line_75 |  | 66 | 68 | 0.0069093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1630-26_0_5_line_76 |  | 67 | 133 | 0.0058636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1630-26_0_5_line_77 |  | 69 | 126 | 0.004106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1630-26_0_5_line_78 |  | 70 | 71 | 0.0051668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1630-26_0_5_line_79 |  | 72 | 73 | 0.043281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1630-26_0_5_line_80 |  | 73 | 74 | 0.011681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1630-26_0_5_line_81 |  | 76 | 77 | 0.003498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1630-26_0_5_line_82 |  | 78 | 79 | 0.023128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1630-26_0_5_line_83 |  | 78 | 80 | 0.0095624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1630-26_0_5_line_84 |  | 79 | 81 | 0.040903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1630-26_0_5_line_85 |  | 79 | 82 | 0.009984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1630-26_0_5_line_86 |  | 80 | 83 | 0.036273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1630-26_0_5_line_87 |  | 81 | 97 | 0.032045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1630-26_0_5_line_88 |  | 82 | 94 | 0.010434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1630-26_0_5_line_89 |  | 82 | 92 | 0.0080419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1630-26_0_5_line_90 |  | 83 | 122 | 0.008788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1630-26_0_5_line_91 |  | 83 | 104 | 0.023263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1630-26_0_5_line_92 |  | 84 | 85 | 0.021756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1630-26_0_5_line_93 |  | 84 | 86 | 0.006823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1630-26_0_5_line_94 |  | 86 | 90 | 0.009262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1630-26_0_5_line_95 |  | 86 | 88 | 0.022018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1630-26_0_5_line_96 |  | 87 | 88 | 0.018909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1630-26_0_5_line_97 |  | 87 | 89 | 0.02389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1630-26_0_5_line_98 |  | 89 | 105 | 0.025277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1630-26_0_5_line_99 |  | 89 | 101 | 0.002597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1630-26_0_5_line_100 |  | 91 | 92 | 0.012674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1630-26_0_5_line_101 |  | 91 | 93 | 0.014173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1630-26_0_5_line_102 |  | 94 | 95 | 0.090165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1630-26_0_5_line_103 |  | 94 | 96 | 0.045172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1630-26_0_5_line_104 |  | 95 | 98 | 0.022349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1630-26_0_5_line_105 |  | 97 | 116 | 0.011915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1630-26_0_5_line_106 |  | 99 | 100 | 0.031893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1630-26_0_5_line_107 |  | 99 | 101 | 0.010563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1630-26_0_5_line_108 |  | 100 | 102 | 0.01283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1630-26_0_5_line_109 |  | 101 | 103 | 0.033343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1630-26_0_5_line_110 |  | 102 | 104 | 0.0043335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1630-26_0_5_line_111 |  | 103 | 106 | 0.0036424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1630-26_0_5_line_112 |  | 104 | 107 | 0.007731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1630-26_0_5_line_113 |  | 105 | 108 | 0.019758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1630-26_0_5_line_114 |  | 106 | 109 | 0.012269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1630-26_0_5_line_115 |  | 106 | 110 | 0.038634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1630-26_0_5_line_116 |  | 108 | 119 | 0.063754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1630-26_0_5_line_117 |  | 110 | 111 | 0.009739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1630-26_0_5_line_118 |  | 111 | 112 | 0.006112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1630-26_0_5_line_119 |  | 113 | 114 | 0.028581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1630-26_0_5_line_120 |  | 113 | 115 | 0.28987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1630-26_0_5_line_121 |  | 114 | 116 | 0.03673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1630-26_0_5_line_122 |  | 115 | 117 | 0.011449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1630-26_0_5_line_123 |  | 119 | 120 | 0.17542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1630-26_0_5_line_124 |  | 120 | 121 | 0.007875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1630-26_0_5_line_125 |  | 123 | 124 | 0.012486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1630-26_0_5_line_126 |  | 123 | 125 | 0.011327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1630-26_0_5_line_127 |  | 124 | 126 | 0.016356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1630-26_0_5_line_128 |  | 124 | 127 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1630-26_0_5_line_129 |  | 125 | 128 | 0.0032708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1630-26_0_5_line_130 |  | 126 | 129 | 0.040163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1630-26_0_5_line_131 |  | 128 | 130 | 0.0014962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1630-26_0_5_line_132 |  | 130 | 131 | 0.039716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1630-26_0_5_line_133 |  | 130 | 132 | 0.046116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1630-26_0_5_line_134 |  | 132 | 137 | 0.015499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1630-26_0_5_line_135 |  | 134 | 135 | 0.0092819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1630-26_0_5_line_136 |  | 134 | 136 | 0.0025281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1630-26_0_5_line_137 |  | 135 | 137 | 0.005211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-26_0_5_trafo_29 | 0.63 MVA 20/0.4 kV | 139 | 13 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2728284.5126 | 1220280.6514 | 2728283.2424 | 1220287.1681 | 2728283.0373 | 1220289.2656
1 | 2728285.282 | 1220276.7037 | 2728284.5126 | 1220280.6514
2 | 2728273.2303 | 1220330.8654 | 2728275.2369 | 1220326.1604 | 2728280.5083 | 1220309.783 | 2728281.5679 | 1220304.2903 | 2728283.0373 | 1220289.2656
3 | 2728285.282 | 1220276.7037 | 2728274.6941 | 1220275.2745
4 | 2728285.282 | 1220276.7037 | 2728296.2966 | 1220265.3873 | 2728300.7529 | 1220262.1808
5 | 2728273.2303 | 1220330.8654 | 2728267.2363 | 1220337.8086 | 2728266.5871 | 1220338.333
6 | 2728300.7529 | 1220262.1808 | 2728299.5825 | 1220242.5648
7 | 2728300.7529 | 1220262.1808 | 2728315.0116 | 1220266.0432
8 | 2728264.1441 | 1220340.3068 | 2728266.5871 | 1220338.333
9 | 2728236.2393 | 1220227.8307 | 2728234.1207 | 1220224.3489 | 2728230.4211 | 1220216.741
10 | 2728236.2393 | 1220227.8307 | 2728241.707 | 1220224.5346
11 | 2728236.2393 | 1220227.8307 | 2728224.0415 | 1220235.2495
12 | 2728230.4211 | 1220216.741 | 2728246.6801 | 1220204.0363
13 | 2728230.4211 | 1220216.741 | 2728226.0267 | 1220210.0299
14 | 2728241.707 | 1220224.5346 | 2728259.5714 | 1220213.7661 | 2728263.2326 | 1220210.1198 | 2728264.6342 | 1220208.5563
15 | 2728216.6575 | 1220239.752 | 2728223.0491 | 1220235.8532 | 2728224.0415 | 1220235.2495
16 | 2728299.5825 | 1220242.5648 | 2728299.2641 | 1220237.2287 | 2728298.5747 | 1220235.0565 | 2728288.2518 | 1220215.6887
17 | 2728352.6707 | 1220275.5433 | 2728334.1146 | 1220271.2178 | 2728315.0116 | 1220266.0432
18 | 2728185.6025 | 1220392.4952 | 2728189.2362 | 1220390.8276 | 2728218.0215 | 1220377.2696 | 2728220.4138 | 1220375.7977 | 2728223.5138 | 1220373.8851 | 2728229.1831 | 1220369.6815 | 2728231.4582 | 1220367.3064 | 2728235.7709 | 1220360.8941 | 2728240.3724 | 1220354.8216 | 2728242.7135 | 1220352.9038 | 2728245.264 | 1220351.1351 | 2728263.0804 | 1220341.1662 | 2728264.1441 | 1220340.3068
19 | 2728226.0267 | 1220210.0299 | 2728194.2373 | 1220176.5966
20 | 2728226.0267 | 1220210.0299 | 2728230.4706 | 1220205.9889 | 2728234.8483 | 1220200.0896 | 2728236.4033 | 1220196.965 | 2728241.105 | 1220183.7778 | 2728241.3797 | 1220181.9489 | 2728241.5091 | 1220179.1161 | 2728238.2529 | 1220168.9767
21 | 2728216.6575 | 1220239.752 | 2728211.7968 | 1220242.7053 | 2728210.9586 | 1220243.2099 | 2728208.6063 | 1220239.6564
22 | 2728182.0723 | 1220268.4752 | 2728178.6035 | 1220262.8405 | 2728196.8999 | 1220251.7364 | 2728210.9586 | 1220243.2099 | 2728208.6063 | 1220239.6564
23 | 2728182.0723 | 1220268.4752 | 2728186.429 | 1220275.5302 | 2728185.2436 | 1220276.2942 | 2728189.0954 | 1220282.8268
24 | 2728164.5515 | 1220289.0369 | 2728162.9493 | 1220286.2447 | 2728164.1266 | 1220284.0905 | 2728166.8011 | 1220282.5579 | 2728167.4697 | 1220282.172 | 2728169.8138 | 1220280.8213 | 2728164.2141 | 1220271.5712 | 2728178.6035 | 1220262.8405 | 2728182.0723 | 1220268.4752
25 | 2728264.451 | 1220112.7234 | 2728254.4259 | 1220103.1221 | 2728250.8113 | 1220102.4882 | 2728247.7693 | 1220102.7563 | 2728245.2945 | 1220104.1819 | 2728238.4402 | 1220114.7539 | 2728237.4523 | 1220117.6239 | 2728237.2564 | 1220123.5466
26 | 2728264.451 | 1220112.7234 | 2728262.7526 | 1220116.5121 | 2728260.9947 | 1220122.3567 | 2728260.0857 | 1220127.5525 | 2728259.7577 | 1220133.6169 | 2728260.3159 | 1220140.4678 | 2728261.0911 | 1220146.7673 | 2728267.5476 | 1220174.7288 | 2728268.3578 | 1220179.7502 | 2728268.7036 | 1220184.4837 | 2728268.5629 | 1220190.6634 | 2728271.8661 | 1220194.4709
27 | 2728264.451 | 1220112.7234 | 2728265.3441 | 1220110.7299 | 2728268.3864 | 1220105.5135 | 2728269.1681 | 1220104.4628 | 2728257.7595 | 1220094.954 | 2728251.6985 | 1220089.141 | 2728246.9248 | 1220083.1223 | 2728241.1511 | 1220071.7222 | 2728227.8676 | 1220040.3667 | 2728224.4118 | 1220032.0078 | 2728220.6538 | 1220025.3438 | 2728214.7875 | 1220016.4771 | 2728210.4992 | 1220009.4124
28 | 2728271.8661 | 1220194.4709 | 2728280.9906 | 1220204.9981 | 2728282.8882 | 1220207.1073
29 | 2728271.8661 | 1220194.4709 | 2728271.0206 | 1220197.7776 | 2728269.5247 | 1220201.6819 | 2728266.1958 | 1220206.8143 | 2728264.6342 | 1220208.5563
30 | 2728216.0662 | 1220112.515 | 2728209.3493 | 1220084.2922 | 2728209.0886 | 1220078.4263 | 2728209.4391 | 1220072.0176 | 2728212.5191 | 1220052.3681 | 2728213.0411 | 1220044.6954 | 2728213.1314 | 1220035.9237 | 2728212.7662 | 1220031.7347 | 2728211.9008 | 1220028.2132 | 2728210.8261 | 1220024.5427 | 2728206.0024 | 1220016.2545 | 2728204.8333 | 1220014.1498 | 2728204.7639 | 1220013.4923 | 2728204.8987 | 1220012.8724 | 2728209.4068 | 1220010.0895 | 2728210.4992 | 1220009.4124
31 | 2728282.8882 | 1220207.1073 | 2728286.2894 | 1220212.0067 | 2728288.2518 | 1220215.6887
32 | 2728346.6632 | 1220298.5879 | 2728349.0429 | 1220291.0109 | 2728352.6707 | 1220275.5433
33 | 2728339.0981 | 1220322.7242 | 2728344.4552 | 1220305.6327
34 | 2728334.4286 | 1220337.6223 | 2728339.0981 | 1220322.7242
35 | 2728346.6632 | 1220298.5879 | 2728344.4552 | 1220305.6327
36 | 2728334.4286 | 1220337.6223 | 2728322.8428 | 1220333.8289
37 | 2728334.4286 | 1220337.6223 | 2728333.9567 | 1220339.1259
38 | 2728335.3318 | 1220298.199 | 2728335.4714 | 1220307.5651 | 2728342.9244 | 1220300.5534 | 2728343.7224 | 1220297.6905 | 2728346.6632 | 1220298.5879
39 | 2728308.0341 | 1220328.9801 | 2728322.8428 | 1220333.8289
40 | 2728330.8179 | 1220349.127 | 2728333.9567 | 1220339.1259
41 | 2728336.0825 | 1220296.4694 | 2728335.3318 | 1220298.199
42 | 2728325.2475 | 1220298.4042 | 2728333.107 | 1220297.8842 | 2728335.3318 | 1220298.199
43 | 2728307.1831 | 1220324.0912 | 2728308.0341 | 1220328.9801
44 | 2728304.5961 | 1220333.1872 | 2728308.0341 | 1220328.9801
45 | 2728325.6705 | 1220367.1463 | 2728325.8629 | 1220364.9153 | 2728330.8179 | 1220349.127
46 | 2728332.4703 | 1220397.8174 | 2728328.0067 | 1220387.9911 | 2728326.8531 | 1220383.7629 | 2728325.7543 | 1220378.0457 | 2728325.4106 | 1220373.568 | 2728325.4186 | 1220370.032 | 2728325.6705 | 1220367.1463
47 | 2728325.6705 | 1220367.1463 | 2728311.5858 | 1220368.4328 | 2728310.4024 | 1220367.9783
48 | 2728173.2873 | 1220304.2149 | 2728169.3965 | 1220297.4548
49 | 2728164.5515 | 1220289.0369 | 2728169.3965 | 1220297.4548
50 | 2728173.2873 | 1220304.2149 | 2728178.911 | 1220313.4099 | 2728179.9341 | 1220315.2445 | 2728180.6198 | 1220316.1823 | 2728182.0231 | 1220316.5794 | 2728185.0806 | 1220317.3458 | 2728188.5916 | 1220318.1999
51 | 2728109.4658 | 1220295.535 | 2728110.6991 | 1220299.5981 | 2728117.4667 | 1220314.1887 | 2728162.9493 | 1220286.2447 | 2728164.5515 | 1220289.0369
52 | 2728100.2401 | 1220303.1093 | 2728100.1132 | 1220298.425 | 2728109.4658 | 1220295.535
53 | 2728109.4658 | 1220295.535 | 2728121.061 | 1220290.7249 | 2728128.5792 | 1220287.3728 | 2728137.6235 | 1220282.5858 | 2728142.2487 | 1220279.8345
54 | 2728109.4658 | 1220295.535 | 2728110.6991 | 1220299.5981 | 2728117.4667 | 1220314.1887 | 2728122.0436 | 1220325.1181 | 2728123.3554 | 1220329.0606 | 2728125.4572 | 1220331.2075 | 2728124.2664 | 1220342.8023 | 2728122.6033 | 1220348.4822 | 2728120.184 | 1220353.6788 | 2728116.8807 | 1220358.6896
55 | 2728121.6098 | 1220379.1188 | 2728121.1129 | 1220370.8237 | 2728116.8807 | 1220358.6896
56 | 2728087.3273 | 1220387.4882 | 2728093.127 | 1220381.4525 | 2728116.8807 | 1220358.6896
57 | 2728035.9428 | 1220464.7344 | 2728037.8803 | 1220466.7554 | 2728039.6125 | 1220467.3821 | 2728053.081 | 1220468.617 | 2728057.5843 | 1220468.5026 | 2728061.506 | 1220467.5529 | 2728063.8113 | 1220466.5905 | 2728070.3676 | 1220458.1914 | 2728070.7232 | 1220433.2012 | 2728067.9871 | 1220429.495 | 2728067.7759 | 1220411.0868 | 2728073.608 | 1220401.7825 | 2728087.3273 | 1220387.4882
58 | 2728087.3273 | 1220387.4882 | 2728087.2999 | 1220398.2852 | 2728087.2927 | 1220400.0309 | 2728087.259 | 1220402.6545 | 2728101.4649 | 1220402.6181
59 | 2728066.1588 | 1220343.7313 | 2728091.6428 | 1220343.201 | 2728094.6205 | 1220342.3866 | 2728097.3302 | 1220340.9771 | 2728099.501 | 1220339.2113 | 2728101.152 | 1220337.2674 | 2728100.2401 | 1220303.1093
60 | 2728100.2401 | 1220303.1093 | 2728100.1132 | 1220298.425 | 2728090.1491 | 1220301.5132 | 2728072.3581 | 1220305.723 | 2728057.1787 | 1220308.4989
61 | 2728012.2527 | 1220302.8287 | 2728012.6411 | 1220312.3002 | 2728028.7072 | 1220311.7005 | 2728043.0265 | 1220310.4517 | 2728051.332 | 1220309.3071 | 2728057.1787 | 1220308.4989
62 | 2728052.495 | 1220317.6944 | 2728051.9301 | 1220313.6123 | 2728051.332 | 1220309.3071 | 2728057.1787 | 1220308.4989
63 | 2728057.1787 | 1220308.4989 | 2728053.9553 | 1220297.7123
64 | 2728165.5722 | 1220413.292 | 2728168.488 | 1220400.9003 | 2728171.4328 | 1220400.9081 | 2728172.86 | 1220399.838 | 2728177.5855 | 1220395.4028 | 2728179.3467 | 1220394.3287 | 2728181.9335 | 1220393.3391 | 2728185.6025 | 1220392.4952
65 | 2728165.5722 | 1220413.292 | 2728160.2784 | 1220425.0876 | 2728158.9229 | 1220431.2856 | 2728156.2317 | 1220447.3517 | 2728155.3606 | 1220449.7349 | 2728154.4168 | 1220452.3278 | 2728153.4 | 1220454.4298 | 2728152.665 | 1220455.4231
66 | 2728185.6025 | 1220392.4952 | 2728181.6328 | 1220402.0174 | 2728180.8453 | 1220404.5734
67 | 2728144.6086 | 1220466.3107 | 2728152.665 | 1220455.4231
68 | 2728179.2727 | 1220420.0448 | 2728179.5582 | 1220417.6409 | 2728179.6781 | 1220412.0723 | 2728180.2373 | 1220406.5466 | 2728180.8453 | 1220404.5734
69 | 2728038.2466 | 1220453.6083 | 2728036.1355 | 1220457.188 | 2728035.9428 | 1220464.7344
70 | 2728012.2527 | 1220302.8287 | 2728012.0116 | 1220294.9838 | 2728012.7684 | 1220290.8524 | 2728013.7758 | 1220286.7151 | 2728015.3684 | 1220284.6588 | 2728017.849 | 1220282.6105 | 2728027.6635 | 1220280.4753
71 | 2728051.642 | 1220329.4744 | 2728052.495 | 1220317.6944
72 | 2728052.495 | 1220317.6944 | 2728023.0235 | 1220325.7563 | 2728021.5032 | 1220355.029
73 | 2728043.0857 | 1220240.6637 | 2728042.1608 | 1220249.4286 | 2728042.7593 | 1220255.8355 | 2728044.3077 | 1220264.6537 | 2728045.2604 | 1220268.3549 | 2728047.3156 | 1220275.4937 | 2728053.9553 | 1220297.7123
74 | 2728178.7129 | 1220426.9301 | 2728177.4933 | 1220443.4048
75 | 2728178.7129 | 1220426.9301 | 2728179.1038 | 1220421.4675 | 2728179.2727 | 1220420.0448
76 | 2728177.0604 | 1220449.2524 | 2728177.4933 | 1220443.4048
77 | 2728142.1663 | 1220469.6114 | 2728144.6086 | 1220466.3107
78 | 2728236.6731 | 1220164.0574 | 2728238.2529 | 1220168.9767
79 | 2728194.2373 | 1220176.5966 | 2728196.0449 | 1220169.8523 | 2728199.3992 | 1220165.6545 | 2728210.1828 | 1220155.1893 | 2728210.7078 | 1220153.7216 | 2728210.827 | 1220152.7678 | 2728210.4066 | 1220150.7905 | 2728203.7765 | 1220141.57
80 | 2728196.957 | 1220132.0861 | 2728203.7765 | 1220141.57
81 | 2728307.1369 | 1220366.7245 | 2728310.4024 | 1220367.9783
82 | 2728332.4703 | 1220397.8174 | 2728340.5417 | 1220419.4976
83 | 2728332.4703 | 1220397.8174 | 2728336.6716 | 1220395.873 | 2728339.1617 | 1220394.7925 | 2728341.1887 | 1220393.8907
84 | 2728340.5417 | 1220419.4976 | 2728343.85 | 1220427.2863 | 2728350.9179 | 1220451.5025 | 2728353.3277 | 1220458.3019
85 | 2728331.5368 | 1220423.8627 | 2728340.5417 | 1220419.4976
86 | 2728373.115 | 1220376.7207 | 2728361.7192 | 1220382.4909 | 2728344.5493 | 1220392.3955 | 2728341.1887 | 1220393.8907
87 | 2728365.8167 | 1220487.7822 | 2728359.29 | 1220474.0121 | 2728355.5684 | 1220464.6243 | 2728353.3277 | 1220458.3019
88 | 2728331.5368 | 1220423.8627 | 2728330.3448 | 1220426.6948 | 2728329.8492 | 1220430.3204 | 2728330.4079 | 1220433.9798
89 | 2728331.5368 | 1220423.8627 | 2728324.3034 | 1220420.3484 | 2728324.3034 | 1220420.3484
90 | 2728366.1183 | 1220371.3767 | 2728373.115 | 1220376.7207
91 | 2728381.5023 | 1220396.4173 | 2728380.3252 | 1220384.4823 | 2728378.5078 | 1220380.0618 | 2728377.0044 | 1220378.328 | 2728373.115 | 1220376.7207
92 | 2728408.2696 | 1220363.1342 | 2728391.7021 | 1220348.9768
93 | 2728408.2696 | 1220363.1342 | 2728403.0807 | 1220367.5814
94 | 2728397.8254 | 1220375.1075 | 2728400.5831 | 1220370.0629 | 2728403.0807 | 1220367.5814
95 | 2728403.0807 | 1220367.5814 | 2728405.6596 | 1220370.8285 | 2728409.1825 | 1220377.4654 | 2728410.9252 | 1220382.5292 | 2728408.63 | 1220383.3693 | 2728410.0212 | 1220385.5155
96 | 2728425.1349 | 1220395.5016 | 2728415.1365 | 1220392.0833 | 2728411.6711 | 1220388.0609 | 2728410.0212 | 1220385.5155
97 | 2728425.1349 | 1220395.5016 | 2728424.915 | 1220400.7677 | 2728418.9933 | 1220418.4209
98 | 2728418.9933 | 1220418.4209 | 2728430.3158 | 1220423.4357 | 2728440.8567 | 1220430.8606
99 | 2728418.166 | 1220420.8828 | 2728418.9933 | 1220418.4209
100 | 2728317.8726 | 1220409.4268 | 2728324.3034 | 1220420.3484
101 | 2728309.9995 | 1220397.6554 | 2728315.5096 | 1220405.4137 | 2728317.8726 | 1220409.4268
102 | 2728298.2631 | 1220507.2573 | 2728307.6773 | 1220504.6692 | 2728314.5051 | 1220502.003 | 2728319.926 | 1220497.3494 | 2728323.4304 | 1220491.4646 | 2728327.3941 | 1220483.2878 | 2728329.1663 | 1220477.1322 | 2728331.8429 | 1220454.3716 | 2728332.6299 | 1220443.9246 | 2728332.1187 | 1220439.1208 | 2728330.4079 | 1220433.9798
103 | 2728330.4079 | 1220433.9798 | 2728325.5422 | 1220439.6351 | 2728325.8872 | 1220443.3455 | 2728320.9897 | 1220461.3878 | 2728319.8878 | 1220463.21 | 2728318.1044 | 1220464.606 | 2728315.3672 | 1220466.2373 | 2728312.434 | 1220466.7523 | 2728307.7027 | 1220466.7372
104 | 2728298.2631 | 1220507.2573 | 2728297.6005 | 1220484.918
105 | 2728370.92 | 1220498.5491 | 2728365.8167 | 1220487.7822
106 | 2728407.6805 | 1220422.1588 | 2728393.6388 | 1220423.8676 | 2728389.3532 | 1220423.386 | 2728385.9064 | 1220421.6658 | 2728383.4686 | 1220419.2669 | 2728381.7911 | 1220416.106 | 2728381.3431 | 1220413.5613
107 | 2728418.166 | 1220420.8828 | 2728407.6805 | 1220422.1588
108 | 2728381.3431 | 1220413.5613 | 2728381.1623 | 1220412.534 | 2728381.3016 | 1220407.8333 | 2728381.4261 | 1220400.7501
109 | 2728418.166 | 1220420.8828 | 2728412.6557 | 1220432.8403 | 2728407.9184 | 1220452.4534
110 | 2728381.5023 | 1220396.4173 | 2728381.4261 | 1220400.7501
111 | 2728407.0632 | 1220455.9939 | 2728407.9184 | 1220452.4534
112 | 2728381.5023 | 1220396.4173 | 2728373.8301 | 1220395.2955
113 | 2728440.8567 | 1220430.8606 | 2728444.1098 | 1220433.1521 | 2728448.4484 | 1220433.9907 | 2728450.4172 | 1220433.4995 | 2728451.9846 | 1220432.2656 | 2728455.5098 | 1220425.8327
114 | 2728407.0632 | 1220455.9939 | 2728395.1958 | 1220452.8812
115 | 2728407.0632 | 1220455.9939 | 2728402.3159 | 1220479.377 | 2728401.2343 | 1220486.237 | 2728400.6149 | 1220491.7281 | 2728400.6472 | 1220494.0311
116 | 2728502.9123 | 1220383.4804 | 2728486.0206 | 1220396.6599 | 2728466.7834 | 1220413.0137 | 2728455.6824 | 1220425.5177 | 2728455.5098 | 1220425.8327
117 | 2728401.4721 | 1220503.7118 | 2728400.7135 | 1220498.7692 | 2728400.6472 | 1220494.0311
118 | 2728401.4721 | 1220503.7118 | 2728395.4513 | 1220504.8607
119 | 2728401.9417 | 1220549.492 | 2728397.6495 | 1220550.378 | 2728394.3304 | 1220549.7837 | 2728391.5619 | 1220548.2895 | 2728389.4015 | 1220546.0523 | 2728388.0269 | 1220543.276 | 2728386.8945 | 1220534.9004 | 2728385.9099 | 1220532.0451
120 | 2728401.9417 | 1220549.492 | 2728335.9479 | 1220831.7523
121 | 2728370.92 | 1220498.5491 | 2728383.6801 | 1220525.5792 | 2728385.9099 | 1220532.0451
122 | 2728335.9479 | 1220831.7523 | 2728347.0905 | 1220834.3836
123 | 2728502.9123 | 1220383.4804 | 2728505.945 | 1220386.4482 | 2728506.9237 | 1220408.2646 | 2728514.2144 | 1220403.8517 | 2728524.0645 | 1220398.3153 | 2728527.0743 | 1220397.0682 | 2728524.525 | 1220412.4922 | 2728523.6285 | 1220426.9401 | 2728523.7192 | 1220457.1886 | 2728523.2821 | 1220462.3166 | 2728521.7183 | 1220480.9534 | 2728518.7447 | 1220500.5606 | 2728520.001 | 1220521.1153 | 2728520.4378 | 1220522.6816
124 | 2728520.4378 | 1220522.6816 | 2728522.5585 | 1220530.2668
125 | 2728126.1997 | 1220473.3598 | 2728114.4109 | 1220477.4732
126 | 2728103.7162 | 1220481.2048 | 2728114.4109 | 1220477.4732
127 | 2728126.1997 | 1220473.3598 | 2728135.523 | 1220471.1142 | 2728142.1663 | 1220469.6114
128 | 2728126.1997 | 1220473.3598 | 2728121.6809 | 1220485.3001
129 | 2728103.7162 | 1220481.2048 | 2728100.4867 | 1220481.7228
130 | 2728142.1663 | 1220469.6114 | 2728146.5565 | 1220476.5114 | 2728147.6975 | 1220480.2723 | 2728148.4656 | 1220484.0808 | 2728147.915 | 1220508.2439
131 | 2728099.0093 | 1220481.9597 | 2728100.4867 | 1220481.7228
132 | 2728099.0093 | 1220481.9597 | 2728095.7859 | 1220507.244 | 2728093.7046 | 1220511.903 | 2728090.3438 | 1220510.7743 | 2728084.7714 | 1220510.5103
133 | 2728099.0093 | 1220481.9597 | 2728076.6301 | 1220485.6704 | 2728064.3085 | 1220488.9859 | 2728054.0589 | 1220491.9576
134 | 2728039.1731 | 1220496.2736 | 2728054.0589 | 1220491.9576
135 | 2728033.9647 | 1220496.7064 | 2728032.9694 | 1220493.2267 | 2728032.6029 | 1220487.5759
136 | 2728032.4393 | 1220485.0532 | 2728032.6029 | 1220487.5759
137 | 2728033.9647 | 1220496.7064 | 2728039.1731 | 1220496.2736

## bus_geodata
| x | y | coords
0 | 2728284.5126 | 1220280.6514
1 | 2728283.0373 | 1220289.2656
2 | 2728285.282 | 1220276.7037
3 | 2728273.2303 | 1220330.8654
4 | 2728274.6941 | 1220275.2745
5 | 2728300.7529 | 1220262.1808
6 | 2728266.5871 | 1220338.333
7 | 2728236.2393 | 1220227.8307
8 | 2728230.4211 | 1220216.7409
9 | 2728241.707 | 1220224.5346
10 | 2728224.0415 | 1220235.2495
11 | 2728299.5825 | 1220242.5648
12 | 2728315.0116 | 1220266.0432
13 | 2728264.1441 | 1220340.3068
14 | 2728246.6801 | 1220204.0363
15 | 2728226.0267 | 1220210.0299
16 | 2728208.6063 | 1220239.6564
17 | 2728216.6575 | 1220239.752
18 | 2728182.0723 | 1220268.4752
19 | 2728264.451 | 1220112.7234
20 | 2728237.2564 | 1220123.5466
21 | 2728271.8661 | 1220194.4709
22 | 2728210.4992 | 1220009.4124
23 | 2728282.8882 | 1220207.1073
24 | 2728264.6342 | 1220208.5563
25 | 2728288.2518 | 1220215.6887
26 | 2728352.6707 | 1220275.5433
27 | 2728339.0981 | 1220322.7242
28 | 2728344.4552 | 1220305.6327
29 | 2728334.4286 | 1220337.6223
30 | 2728346.6632 | 1220298.5879
31 | 2728322.8428 | 1220333.8289
32 | 2728333.9567 | 1220339.1259
33 | 2728335.3318 | 1220298.199
34 | 2728308.0341 | 1220328.9801
35 | 2728330.8179 | 1220349.127
36 | 2728336.0825 | 1220296.4694
37 | 2728325.2475 | 1220298.4042
38 | 2728307.1831 | 1220324.0912
39 | 2728304.5961 | 1220333.1872
40 | 2728325.6705 | 1220367.1463
41 | 2728169.3965 | 1220297.4548
42 | 2728173.2873 | 1220304.2149
43 | 2728164.5515 | 1220289.0369
44 | 2728188.5916 | 1220318.1999
45 | 2728109.4658 | 1220295.535
46 | 2728116.8807 | 1220358.6896
47 | 2728121.6098 | 1220379.1188
48 | 2728087.3273 | 1220387.4882
49 | 2728189.0954 | 1220282.8268
50 | 2728100.2401 | 1220303.1093
51 | 2728142.2487 | 1220279.8345
52 | 2728066.1588 | 1220343.7313
53 | 2728057.1787 | 1220308.4989
54 | 2728165.5722 | 1220413.292
55 | 2728185.6025 | 1220392.4952
56 | 2728152.665 | 1220455.4231
57 | 2728180.8453 | 1220404.5734
58 | 2728035.9428 | 1220464.7344
59 | 2728101.4649 | 1220402.6182
60 | 2728012.2527 | 1220302.8287
61 | 2728052.495 | 1220317.6944
62 | 2728053.9553 | 1220297.7123
63 | 2728027.6635 | 1220280.4753
64 | 2728051.642 | 1220329.4744
65 | 2728021.5032 | 1220355.029
66 | 2728178.7129 | 1220426.9301
67 | 2728177.4933 | 1220443.4048
68 | 2728179.2727 | 1220420.0448
69 | 2728144.6086 | 1220466.3107
70 | 2728238.2529 | 1220168.9767
71 | 2728236.6731 | 1220164.0574
72 | 2728194.2373 | 1220176.5966
73 | 2728203.7765 | 1220141.57
74 | 2728196.957 | 1220132.0861
75 | 2728216.0662 | 1220112.515
76 | 2728310.4024 | 1220367.9783
77 | 2728307.1369 | 1220366.7245
78 | 2728332.4703 | 1220397.8174
79 | 2728340.5417 | 1220419.4976
80 | 2728341.1887 | 1220393.8907
81 | 2728353.3277 | 1220458.3019
82 | 2728331.5368 | 1220423.8627
83 | 2728373.115 | 1220376.7207
84 | 2728408.2696 | 1220363.1342
85 | 2728391.7021 | 1220348.9768
86 | 2728403.0807 | 1220367.5815
87 | 2728425.1349 | 1220395.5016
88 | 2728410.0212 | 1220385.5155
89 | 2728418.9933 | 1220418.4209
90 | 2728397.8254 | 1220375.1075
91 | 2728317.8726 | 1220409.4268
92 | 2728324.3034 | 1220420.3484
93 | 2728309.9995 | 1220397.6554
94 | 2728330.4079 | 1220433.9798
95 | 2728298.2631 | 1220507.2573
96 | 2728307.7027 | 1220466.7372
97 | 2728365.8167 | 1220487.7822
98 | 2728297.6005 | 1220484.918
99 | 2728407.6805 | 1220422.1588
100 | 2728381.3431 | 1220413.5613
101 | 2728418.166 | 1220420.8828
102 | 2728381.4261 | 1220400.7501
103 | 2728407.9184 | 1220452.4534
104 | 2728381.5023 | 1220396.4173
105 | 2728440.8567 | 1220430.8606
106 | 2728407.0632 | 1220455.9939
107 | 2728373.8301 | 1220395.2955
108 | 2728455.5098 | 1220425.8327
109 | 2728395.1958 | 1220452.8812
110 | 2728400.6472 | 1220494.0311
111 | 2728401.4721 | 1220503.7118
112 | 2728395.4513 | 1220504.8607
113 | 2728401.9417 | 1220549.492
114 | 2728385.9099 | 1220532.0451
115 | 2728335.9479 | 1220831.7523
116 | 2728370.92 | 1220498.5491
117 | 2728347.0905 | 1220834.3836
118 | 2728043.0857 | 1220240.6637
119 | 2728502.9123 | 1220383.4804
120 | 2728520.4378 | 1220522.6816
121 | 2728522.5585 | 1220530.2668
122 | 2728366.1183 | 1220371.3767
123 | 2728114.4109 | 1220477.4732
124 | 2728126.1997 | 1220473.3598
125 | 2728103.7162 | 1220481.2048
126 | 2728142.1663 | 1220469.6114
127 | 2728121.6809 | 1220485.3001
128 | 2728100.4867 | 1220481.7228
129 | 2728147.915 | 1220508.2439
130 | 2728099.0093 | 1220481.9597
131 | 2728084.7714 | 1220510.5103
132 | 2728054.0589 | 1220491.9576
133 | 2728177.0604 | 1220449.2524
134 | 2728032.6029 | 1220487.5759
135 | 2728033.9647 | 1220496.7064
136 | 2728032.4393 | 1220485.0532
137 | 2728039.1731 | 1220496.2736
138 | 2728038.2466 | 1220453.6083
139 | 2728273.2303 | 1220330.8654

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99359 | -0.12144 | 0.002777 | 0.00069597
1 | 0.99445 | -0.10513 | 0.0041162 | 0.0010316
2 | 0.9932 | -0.1289 | 0 | 0
3 | 0.9987 | -0.024544 | 0 | 0
4 | 0.99316 | -0.12967 | 0.00409 | 0.0010251
5 | 0.99115 | -0.1681 | 0 | 0
6 | 0.99969 | -0.0058927 | 0.0033977 | 0.00085154
7 | 0.98636 | -0.26056 | 0 | 0
8 | 0.98597 | -0.2681 | 0 | 0
9 | 0.98658 | -0.25628 | 0 | 0
10 | 0.98597 | -0.26802 | 0.0074976 | 0.0018791
11 | 0.99034 | -0.18366 | 0.0067851 | 0.0017005
12 | 0.99034 | -0.18369 | 0.0072615 | 0.0018199
13 | 1 | 0 | -0.56346 | -0.14472
14 | 0.98581 | -0.27129 | 0.008642 | 0.0021659
15 | 0.98579 | -0.27168 | 0 | 0
16 | 0.98548 | -0.27759 | 0 | 0
17 | 0.98575 | -0.27224 | 0 | 0
18 | 0.98425 | -0.30147 | 0 | 0
19 | 0.9873 | -0.24244 | 0 | 0
20 | 0.98694 | -0.24941 | 0.0086721 | 0.0021734
21 | 0.98813 | -0.22621 | 0 | 0
22 | 0.98707 | -0.24696 | 0 | 0
23 | 0.98878 | -0.21375 | 0 | 0
24 | 0.98755 | -0.23739 | 0.0058034 | 0.0014545
25 | 0.98917 | -0.20622 | 0.004881 | 0.0012233
26 | 0.98826 | -0.22354 | 0 | 0
27 | 0.98574 | -0.2723 | 0.0072885 | 0.0018267
28 | 0.98661 | -0.25535 | 0.0090392 | 0.0022654
29 | 0.985 | -0.28659 | 0 | 0
30 | 0.98699 | -0.24807 | 0 | 0
31 | 0.98475 | -0.29145 | 0.010719 | 0.0026864
32 | 0.98493 | -0.28788 | 0.0060866 | 0.0015254
33 | 0.98675 | -0.25271 | 0 | 0
34 | 0.98458 | -0.29465 | 0 | 0
35 | 0.9845 | -0.29616 | 0.006033 | 0.001512
36 | 0.98674 | -0.25289 | 0.0052688 | 0.0013205
37 | 0.98671 | -0.25359 | 0.0048502 | 0.0012156
38 | 0.98456 | -0.29508 | 0.0048271 | 0.0012098
39 | 0.98455 | -0.29529 | 0.0066052 | 0.0016554
40 | 0.98352 | -0.31529 | 0 | 0
41 | 0.98334 | -0.31893 | 0.0070882 | 0.0017765
42 | 0.98329 | -0.31994 | 0 | 0
43 | 0.98347 | -0.31644 | 0 | 0
44 | 0.98315 | -0.32281 | 0.0071605 | 0.0017946
45 | 0.97937 | -0.39619 | 0 | 0
46 | 0.97645 | -0.45336 | 0 | 0
47 | 0.97636 | -0.45505 | 0.00436 | 0.0010927
48 | 0.97486 | -0.4846 | 0 | 0
49 | 0.98365 | -0.31313 | 0.037525 | 0.0094047
50 | 0.97926 | -0.39841 | 0 | 0
51 | 0.97926 | -0.39827 | 0.0031533 | 0.00079028
52 | 0.97917 | -0.40018 | 0.0013735 | 0.00034424
53 | 0.97894 | -0.40467 | 0 | 0
54 | 0.98574 | -0.27157 | 0 | 0
55 | 0.9892 | -0.20493 | 0 | 0
56 | 0.98101 | -0.36332 | 0.0013419 | 0.00033632
57 | 0.98912 | -0.20649 | 0.0016611 | 0.00041632
58 | 0.97199 | -0.54106 | 0 | 0
59 | 0.97443 | -0.49294 | 0.015469 | 0.0038768
60 | 0.97882 | -0.407 | 0 | 0
61 | 0.9789 | -0.40538 | 0 | 0
62 | 0.97892 | -0.40507 | 0.00071096 | 0.00017818
63 | 0.97875 | -0.40839 | 0.0023672 | 0.00059329
64 | 0.97888 | -0.40578 | 0.0018892 | 0.00047347
65 | 0.97886 | -0.40627 | 0.00082286 | 0.00020623
66 | 0.98903 | -0.20825 | 0 | 0
67 | 0.98899 | -0.20907 | 0.001376 | 0.00034485
68 | 0.98905 | -0.2079 | 0.0022801 | 0.00057144
69 | 0.97959 | -0.39114 | 0.0014739 | 0.00036939
70 | 0.98538 | -0.2795 | 0.0061879 | 0.0015508
71 | 0.98537 | -0.2798 | 0.0032514 | 0.00081488
72 | 0.98513 | -0.28446 | 0 | 0
73 | 0.98451 | -0.29649 | 0.0106 | 0.0026566
74 | 0.98446 | -0.29751 | 0.0048637 | 0.001219
75 | 0.98686 | -0.25098 | 0.0020536 | 0.00051467
76 | 0.98325 | -0.32045 | 0.010646 | 0.0026681
77 | 0.98323 | -0.32095 | 0.0079233 | 0.0019858
78 | 0.98202 | -0.34431 | 0 | 0
79 | 0.98085 | -0.36728 | 0 | 0
80 | 0.98116 | -0.36095 | 0.0034355 | 0.00086103
81 | 0.97972 | -0.38921 | 0.0063726 | 0.0015971
82 | 0.98061 | -0.37186 | 0 | 0
83 | 0.97803 | -0.4221 | 0 | 0
84 | 0.97165 | -0.54758 | 0 | 0
85 | 0.97145 | -0.55156 | 0.0099145 | 0.0024848
86 | 0.97171 | -0.54633 | 0 | 0
87 | 0.97247 | -0.53138 | 0 | 0
88 | 0.97207 | -0.53938 | 0.0058585 | 0.0014683
89 | 0.97298 | -0.52128 | 0 | 0
90 | 0.97165 | -0.54756 | 0.0071794 | 0.0017993
91 | 0.98036 | -0.37681 | 0.0055595 | 0.0013933
92 | 0.98049 | -0.37418 | 0.0044399 | 0.0011127
93 | 0.98028 | -0.37832 | 0.005886 | 0.0014752
94 | 0.98052 | -0.37365 | 0 | 0
95 | 0.98022 | -0.37963 | 0 | 0
96 | 0.98028 | -0.37839 | 0.0057856 | 0.00145
97 | 0.97903 | -0.40271 | 0.0039879 | 0.00099947
98 | 0.98014 | -0.38111 | 0.003655 | 0.00091604
99 | 0.9736 | -0.50916 | 0.0050083 | 0.0012552
100 | 0.97535 | -0.47464 | 0.0030322 | 0.00075995
101 | 0.97306 | -0.51965 | 0 | 0
102 | 0.97609 | -0.46008 | 0.0026191 | 0.00065641
103 | 0.97244 | -0.53189 | 0.0067234 | 0.0016851
104 | 0.97635 | -0.45495 | 0 | 0
105 | 0.97272 | -0.52644 | 0.002986 | 0.00074837
106 | 0.9724 | -0.53277 | 0 | 0
107 | 0.97626 | -0.45676 | 0.012756 | 0.0031969
108 | 0.97257 | -0.52939 | 0.0044266 | 0.0011094
109 | 0.97234 | -0.53402 | 0.0055005 | 0.0013785
110 | 0.97212 | -0.53825 | 0.0043502 | 0.0010903
111 | 0.97209 | -0.53886 | 0 | 0
112 | 0.97207 | -0.53923 | 0.0033457 | 0.00083852
113 | 0.97781 | -0.42664 | 0 | 0
114 | 0.97817 | -0.4197 | 0.0058672 | 0.0014705
115 | 0.97422 | -0.4973 | 0 | 0
116 | 0.97882 | -0.40687 | 0 | 0
117 | 0.97408 | -0.5001 | 0.013317 | 0.0033376
118 | 0.97885 | -0.40641 | 0.0012543 | 0.00031435
119 | 0.97235 | -0.5337 | 0 | 0
120 | 0.97175 | -0.54557 | 0 | 0
121 | 0.97173 | -0.5461 | 0.003665 | 0.00091854
122 | 0.9779 | -0.42456 | 0.015417 | 0.003864
123 | 0.97824 | -0.4177 | 0.0015389 | 0.00038568
124 | 0.97842 | -0.41416 | 0 | 0
125 | 0.97809 | -0.4206 | 0 | 0
126 | 0.97917 | -0.39948 | 0 | 0
127 | 0.97802 | -0.422 | 0.033739 | 0.0084557
128 | 0.97805 | -0.42144 | 0.00073721 | 0.00018476
129 | 0.97684 | -0.44517 | 0.062427 | 0.015646
130 | 0.97803 | -0.4218 | 0 | 0
131 | 0.97769 | -0.42851 | 0.0092655 | 0.0023221
132 | 0.97786 | -0.4252 | 0.0023058 | 0.00057789
133 | 0.98898 | -0.20922 | 0.0014165 | 0.000355
134 | 0.97781 | -0.42615 | 0.001047 | 0.00026241
135 | 0.97782 | -0.42586 | 0 | 0
136 | 0.97781 | -0.42619 | 0.00069177 | 0.00017337
137 | 0.97783 | -0.42569 | 0 | 0
138 | 0.97171 | -0.54664 | 0.025863 | 0.0064819
139 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.42796 | -0.10922 | 0.4283 | 0.10943 | 0.00033758 | 0.00021559 | 0.64161 | 0.64161 | 0.64161 | 0.99359 | -0.12144 | 0.99445 | -0.10513 | 44.067
1 | 0.42518 | 0.10852 | -0.42503 | -0.10842 | 0.00015322 | 9.7852e-05 | 0.63746 | 0.63746 | 0.63746 | 0.99359 | -0.12144 | 0.9932 | -0.1289 | 43.7813
2 | -0.43241 | -0.11046 | 0.4341 | 0.11154 | 0.001692 | 0.0010806 | 0.64777 | 0.64777 | 0.64777 | 0.99445 | -0.10513 | 0.9987 | -0.024544 | 44.49
3 | 0.0040902 | 0.001025 | -0.00409 | -0.0010251 | 1.5001e-07 | -4.1852e-08 | 0.0061279 | 0.0061279 | 0.0061279 | 0.9932 | -0.1289 | 0.99316 | -0.12967 | 1.6835
4 | 0.42094 | 0.1074 | -0.42014 | -0.10689 | 0.00079523 | 0.00050785 | 0.63133 | 0.63133 | 0.63133 | 0.9932 | -0.1289 | 0.99115 | -0.1681 | 43.3605
5 | -0.4341 | -0.11154 | 0.4345 | 0.11179 | 0.00039366 | 0.00025142 | 0.64777 | 0.64777 | 0.64777 | 0.9987 | -0.024544 | 0.99969 | -0.0058927 | 44.4899
6 | 0.17985 | 0.045658 | -0.17972 | -0.045573 | 0.00013452 | 8.5079e-05 | 0.27022 | 0.27022 | 0.27022 | 0.99115 | -0.1681 | 0.99034 | -0.18366 | 18.5589
7 | 0.24029 | 0.061231 | -0.24011 | -0.061116 | 0.0001806 | 0.00011482 | 0.36111 | 0.36111 | 0.36111 | 0.99115 | -0.1681 | 0.99034 | -0.18369 | 24.8017
8 | -0.4379 | -0.11265 | 0.43802 | 0.11273 | 0.00012549 | 8.0148e-05 | 0.65283 | 0.65283 | 0.65283 | 0.99969 | -0.0058927 | 1 | 0 | 44.8372
9 | 0.033585 | 0.0084301 | -0.033573 | -0.0084226 | 1.2069e-05 | 7.5644e-06 | 0.05067 | 0.05067 | 0.05067 | 0.98636 | -0.26056 | 0.98597 | -0.2681 | 13.9205
10 | -0.15091 | -0.038124 | 0.15094 | 0.038144 | 3.0986e-05 | 1.9506e-05 | 0.22777 | 0.22777 | 0.22777 | 0.98636 | -0.26056 | 0.98658 | -0.25628 | 15.6434
11 | 0.11732 | 0.029694 | -0.11728 | -0.029668 | 4.1979e-05 | 2.6138e-05 | 0.1771 | 0.1771 | 0.1771 | 0.98636 | -0.26056 | 0.98597 | -0.26802 | 12.1633
12 | 0.0086433 | 0.0021665 | -0.008642 | -0.0021659 | 1.3144e-06 | 5.7856e-07 | 0.013044 | 0.013045 | 0.013045 | 0.98597 | -0.2681 | 0.98581 | -0.27129 | 3.5837
13 | 0.024929 | 0.0062561 | -0.024925 | -0.0062535 | 4.2551e-06 | 2.6211e-06 | 0.037626 | 0.037626 | 0.037626 | 0.98597 | -0.2681 | 0.98579 | -0.27168 | 10.3368
14 | -0.15094 | -0.038144 | 0.15108 | 0.03823 | 0.00013679 | 8.6109e-05 | 0.22777 | 0.22777 | 0.22777 | 0.98658 | -0.25628 | 0.98755 | -0.23739 | 15.6434
15 | 0.10978 | 0.027789 | -0.10976 | -0.027775 | 2.2284e-05 | 1.3821e-05 | 0.16578 | 0.16578 | 0.16578 | 0.98597 | -0.26802 | 0.98575 | -0.27224 | 11.3862
16 | 0.17293 | 0.043872 | -0.17274 | -0.043754 | 0.00018744 | 0.00011844 | 0.26002 | 0.26002 | 0.26002 | 0.99034 | -0.18366 | 0.98917 | -0.20622 | 17.8587
17 | 0.23285 | 0.059296 | -0.2324 | -0.059012 | 0.00044662 | 0.00028384 | 0.3502 | 0.3502 | 0.3502 | 0.99034 | -0.18369 | 0.98826 | -0.22354 | 24.0524
18 | 0.12379 | 0.03199 | -0.12257 | -0.031207 | 0.0012245 | 0.00078243 | 0.18455 | 0.18455 | 0.18455 | 1 | 0 | 0.9892 | -0.20493 | 50.7003
19 | 0.015482 | 0.0038861 | -0.015473 | -0.0038807 | 9.4374e-06 | 5.453e-06 | 0.023372 | 0.023372 | 0.023372 | 0.98579 | -0.27168 | 0.98513 | -0.28446 | 6.4209
20 | 0.0094429 | 0.0023673 | -0.0094394 | -0.0023657 | 3.5184e-06 | 1.6633e-06 | 0.014254 | 0.014254 | 0.014254 | 0.98579 | -0.27168 | 0.98538 | -0.2795 | 3.916
21 | -0.10973 | -0.027758 | 0.10976 | 0.027775 | 2.8156e-05 | 1.7463e-05 | 0.16578 | 0.16578 | 0.16578 | 0.98548 | -0.27759 | 0.98575 | -0.27224 | 11.3862
22 | 0.10973 | 0.027758 | -0.10961 | -0.02768 | 0.00012554 | 7.7867e-05 | 0.16578 | 0.16578 | 0.16578 | 0.98548 | -0.27759 | 0.98425 | -0.30147 | 11.3863
23 | 0.037546 | 0.0094178 | -0.037525 | -0.0094047 | 2.087e-05 | 1.3138e-05 | 0.056766 | 0.056766 | 0.056766 | 0.98425 | -0.30147 | 0.98365 | -0.31313 | 15.5951
24 | 0.072062 | 0.018262 | -0.07201 | -0.018231 | 5.1806e-05 | 3.0794e-05 | 0.10902 | 0.10902 | 0.10902 | 0.98425 | -0.30147 | 0.98347 | -0.31644 | 7.4876
25 | 0.0086749 | 0.0021747 | -0.0086721 | -0.0021734 | 2.8827e-06 | 1.2701e-06 | 0.013075 | 0.013075 | 0.013075 | 0.9873 | -0.24244 | 0.98694 | -0.24941 | 3.592
26 | -0.010729 | -0.0026869 | 0.010738 | 0.0026912 | 8.2925e-06 | 4.2247e-06 | 0.01617 | 0.01617 | 0.01617 | 0.9873 | -0.24244 | 0.98813 | -0.22621 | 4.4423
27 | 0.0020544 | 0.00051224 | -0.0020539 | -0.00051352 | 4.4161e-07 | -1.2885e-06 | 0.0030953 | 0.0030959 | 0.0030959 | 0.9873 | -0.24244 | 0.98707 | -0.24696 | 0.85052
28 | -0.1677 | -0.042429 | 0.1678 | 0.042492 | 0.00010037 | 6.3378e-05 | 0.25268 | 0.25268 | 0.25268 | 0.98813 | -0.22621 | 0.98878 | -0.21375 | 17.3545
29 | 0.15696 | 0.039737 | -0.15688 | -0.039684 | 8.4174e-05 | 5.3049e-05 | 0.23651 | 0.23651 | 0.23651 | 0.98813 | -0.22621 | 0.98755 | -0.23739 | 16.2439
30 | 0.0020539 | 0.00051352 | -0.0020536 | -0.00051467 | 3.9245e-07 | -1.144e-06 | 0.0030959 | 0.0030964 | 0.0030964 | 0.98707 | -0.24696 | 0.98686 | -0.25098 | 0.85066
31 | -0.1678 | -0.042492 | 0.16786 | 0.04253 | 6.0674e-05 | 3.8311e-05 | 0.25268 | 0.25268 | 0.25268 | 0.98878 | -0.21375 | 0.98917 | -0.20622 | 17.3545
32 | 0.2324 | 0.059012 | -0.23213 | -0.058838 | 0.00027398 | 0.00017413 | 0.3502 | 0.3502 | 0.3502 | 0.98826 | -0.22354 | 0.98699 | -0.24807 | 24.0524
33 | -0.21272 | -0.053876 | 0.21289 | 0.053986 | 0.00017336 | 0.00011004 | 0.32131 | 0.32131 | 0.32131 | 0.98574 | -0.2723 | 0.98661 | -0.25535 | 22.068
34 | 0.20543 | 0.052049 | -0.20529 | -0.05196 | 0.00014094 | 8.9407e-05 | 0.31031 | 0.31031 | 0.31031 | 0.98574 | -0.2723 | 0.985 | -0.28659 | 21.3124
35 | -0.22193 | -0.056252 | 0.22201 | 0.056301 | 7.7648e-05 | 4.9317e-05 | 0.33494 | 0.33494 | 0.33494 | 0.98661 | -0.25535 | 0.98699 | -0.24807 | 23.0043
36 | 0.022158 | 0.0055557 | -0.022153 | -0.0055526 | 5.1229e-06 | 3.1235e-06 | 0.033475 | 0.033475 | 0.033475 | 0.985 | -0.28659 | 0.98475 | -0.29145 | 9.1964
37 | 0.18313 | 0.046404 | -0.18312 | -0.046397 | 1.1322e-05 | 7.1659e-06 | 0.27683 | 0.27683 | 0.27683 | 0.985 | -0.28659 | 0.98493 | -0.28788 | 19.0133
38 | 0.010122 | 0.0025372 | -0.010119 | -0.0025361 | 2.2395e-06 | 1.1056e-06 | 0.01526 | 0.01526 | 0.01526 | 0.98699 | -0.24807 | 0.98675 | -0.25271 | 4.1923
39 | 0.011434 | 0.0028662 | -0.011433 | -0.0028653 | 1.7445e-06 | 9.1825e-07 | 0.017278 | 0.017278 | 0.017278 | 0.98475 | -0.29145 | 0.98458 | -0.29465 | 4.7468
40 | 0.17703 | 0.044872 | -0.17696 | -0.044827 | 7.0391e-05 | 4.4517e-05 | 0.26764 | 0.26764 | 0.26764 | 0.98493 | -0.28788 | 0.9845 | -0.29616 | 18.3818
41 | 0.0052689 | 0.0013205 | -0.0052688 | -0.0013205 | 4.4625e-08 | 4.4812e-09 | 0.0079454 | 0.0079454 | 0.0079454 | 0.98675 | -0.25271 | 0.98674 | -0.25289 | 2.1828
42 | 0.0048504 | 0.0012156 | -0.0048502 | -0.0012156 | 2.0252e-07 | 6.7496e-10 | 0.0073144 | 0.0073145 | 0.0073145 | 0.98675 | -0.25271 | 0.98671 | -0.25359 | 2.0095
43 | 0.0048272 | 0.0012098 | -0.0048271 | -0.0012098 | 9.9055e-08 | 2.776e-10 | 0.0072954 | 0.0072954 | 0.0072954 | 0.98458 | -0.29465 | 0.98456 | -0.29508 | 2.0042
44 | 0.0066054 | 0.0016555 | -0.0066052 | -0.0016554 | 2.0285e-07 | 6.0794e-08 | 0.0099828 | 0.0099828 | 0.0099828 | 0.98458 | -0.29465 | 0.98455 | -0.29529 | 2.7425
45 | 0.17093 | 0.043315 | -0.17077 | -0.043215 | 0.00015695 | 9.973e-05 | 0.25852 | 0.25852 | 0.25852 | 0.9845 | -0.29616 | 0.98352 | -0.31529 | 23.674
46 | 0.1522 | 0.038559 | -0.15199 | -0.038424 | 0.00021183 | 0.00013436 | 0.23042 | 0.23042 | 0.23042 | 0.98352 | -0.31529 | 0.98202 | -0.34431 | 21.1006
47 | 0.018574 | 0.0046566 | -0.018569 | -0.0046539 | 4.5638e-06 | 2.7253e-06 | 0.028102 | 0.028102 | 0.028102 | 0.98352 | -0.31529 | 0.98325 | -0.32045 | 7.7203
48 | 0.0071618 | 0.0017951 | -0.0071615 | -0.0017949 | 3.4354e-07 | 1.2092e-07 | 0.010837 | 0.010837 | 0.010837 | 0.98334 | -0.31893 | 0.98329 | -0.31994 | 2.9773
49 | -0.01425 | -0.0035715 | 0.014252 | 0.0035725 | 1.6936e-06 | 9.6065e-07 | 0.021563 | 0.021563 | 0.021563 | 0.98334 | -0.31893 | 0.98347 | -0.31644 | 5.924
50 | 0.0071615 | 0.0017949 | -0.0071605 | -0.0017946 | 9.7915e-07 | 3.4471e-07 | 0.010837 | 0.010838 | 0.010838 | 0.98329 | -0.31994 | 0.98315 | -0.32281 | 2.9774
51 | 0.057759 | 0.014659 | -0.057538 | -0.014519 | 0.00022065 | 0.00014024 | 0.087456 | 0.087456 | 0.087456 | 0.98347 | -0.31644 | 0.97937 | -0.39619 | 24.0264
52 | 0.0084219 | 0.0021075 | -0.008421 | -0.0021071 | 8.8861e-07 | 3.8658e-07 | 0.012795 | 0.012795 | 0.012795 | 0.97937 | -0.39619 | 0.97926 | -0.39841 | 3.515
53 | 0.0031536 | 0.00079003 | -0.0031533 | -0.00079028 | 3.1336e-07 | -2.5743e-07 | 0.0047913 | 0.0047915 | 0.0047915 | 0.97937 | -0.39619 | 0.97926 | -0.39827 | 1.3163
54 | 0.045963 | 0.011621 | -0.045837 | -0.011542 | 0.00012567 | 7.9568e-05 | 0.06987 | 0.069871 | 0.069871 | 0.97937 | -0.39619 | 0.97645 | -0.45336 | 19.1952
55 | 0.0043604 | 0.0010927 | -0.00436 | -0.0010927 | 3.5034e-07 | -4.0429e-08 | 0.0066447 | 0.0066448 | 0.0066448 | 0.97645 | -0.45336 | 0.97636 | -0.45505 | 1.8255
56 | 0.041477 | 0.010449 | -0.041415 | -0.01041 | 6.1867e-05 | 3.9079e-05 | 0.063226 | 0.063226 | 0.063226 | 0.97645 | -0.45336 | 0.97486 | -0.4846 | 17.3698
57 | 0.02594 | 0.0065294 | -0.02587 | -0.0064862 | 6.9798e-05 | 4.3196e-05 | 0.039605 | 0.039605 | 0.039605 | 0.97486 | -0.4846 | 0.97199 | -0.54106 | 10.8805
58 | 0.015475 | 0.0038804 | -0.015469 | -0.0038768 | 6.1459e-06 | 3.5673e-06 | 0.023621 | 0.023622 | 0.023622 | 0.97486 | -0.4846 | 0.97443 | -0.49294 | 6.4894
59 | 0.0013736 | 0.00034342 | -0.0013735 | -0.00034424 | 1.1608e-07 | -8.1961e-07 | 0.002087 | 0.0020873 | 0.0020873 | 0.97926 | -0.39841 | 0.97917 | -0.40018 | 0.57344
60 | 0.0070473 | 0.0017637 | -0.0070452 | -0.0017629 | 2.0996e-06 | 7.296e-07 | 0.010708 | 0.010708 | 0.010708 | 0.97926 | -0.39841 | 0.97894 | -0.40467 | 2.9417
61 | 0.0023677 | 0.00059247 | -0.0023674 | -0.00059298 | 2.6331e-07 | -5.1304e-07 | 0.0035986 | 0.0035988 | 0.0035988 | 0.97894 | -0.40467 | 0.97882 | -0.407 | 0.98869
62 | 0.0027122 | 0.00067872 | -0.0027121 | -0.00067884 | 9.1571e-08 | -1.2205e-07 | 0.0041223 | 0.0041223 | 0.0041223 | 0.97894 | -0.40467 | 0.9789 | -0.40538 | 1.1325
63 | 0.0019654 | 0.00049173 | -0.0019653 | -0.00049185 | 3.767e-08 | -1.1743e-07 | 0.0029871 | 0.0029872 | 0.0029872 | 0.97894 | -0.40467 | 0.97892 | -0.40507 | 0.82065
64 | -0.11546 | -0.029282 | 0.11583 | 0.02952 | 0.00037119 | 0.00023714 | 0.17442 | 0.17442 | 0.17442 | 0.98574 | -0.27157 | 0.9892 | -0.20493 | 47.9172
65 | 0.11546 | 0.029282 | -0.11496 | -0.028959 | 0.00050688 | 0.00032384 | 0.17442 | 0.17442 | 0.17442 | 0.98574 | -0.27157 | 0.98101 | -0.36332 | 47.9173
66 | 0.0067347 | 0.0016875 | -0.0067342 | -0.0016874 | 4.9997e-07 | 1.5322e-07 | 0.010131 | 0.010131 | 0.010131 | 0.9892 | -0.20493 | 0.98912 | -0.20649 | 2.7831
67 | 0.11361 | 0.028622 | -0.11346 | -0.028526 | 0.00015093 | 9.6425e-05 | 0.17238 | 0.17238 | 0.17238 | 0.98101 | -0.36332 | 0.97959 | -0.39114 | 47.3581
68 | 0.005073 | 0.001271 | -0.0050727 | -0.001271 | 3.4092e-07 | 1.7852e-08 | 0.0076316 | 0.0076317 | 0.0076317 | 0.98912 | -0.20649 | 0.98905 | -0.2079 | 2.0966
69 | 0.02587 | 0.0064862 | -0.025863 | -0.0064819 | 6.8845e-06 | 4.261e-06 | 0.039605 | 0.039605 | 0.039605 | 0.97199 | -0.54106 | 0.97171 | -0.54664 | 10.8805
70 | 0.0023674 | 0.00059298 | -0.0023672 | -0.00059329 | 1.5609e-07 | -3.0401e-07 | 0.0035988 | 0.003599 | 0.003599 | 0.97882 | -0.407 | 0.97875 | -0.40839 | 0.98873
71 | 0.0018892 | 0.00047335 | -0.0018892 | -0.00047347 | 3.6533e-08 | -1.2512e-07 | 0.0028717 | 0.0028718 | 0.0028718 | 0.9789 | -0.40538 | 0.97888 | -0.40578 | 0.78895
72 | 0.00082289 | 0.0002055 | -0.00082286 | -0.00020623 | 3.512e-08 | -7.301e-07 | 0.0012506 | 0.0012509 | 0.0012509 | 0.9789 | -0.40538 | 0.97886 | -0.40627 | 0.34365
73 | 0.0012544 | 0.00031367 | -0.0012543 | -0.00031435 | 7.9936e-08 | -6.8603e-07 | 0.0019064 | 0.0019067 | 0.0019067 | 0.97892 | -0.40507 | 0.97885 | -0.40641 | 0.52382
74 | 0.0027926 | 0.00069964 | -0.0027925 | -0.00069978 | 1.0935e-07 | -1.42e-07 | 0.0042014 | 0.0042015 | 0.0042015 | 0.98903 | -0.20825 | 0.98899 | -0.20907 | 1.1542
75 | -0.0027926 | -0.00069964 | 0.0027926 | 0.00069958 | 4.5735e-08 | -5.9399e-08 | 0.0042014 | 0.0042014 | 0.0042014 | 0.98903 | -0.20825 | 0.98905 | -0.2079 | 1.1542
76 | 0.0014165 | 0.00035493 | -0.0014165 | -0.000355 | 9.9871e-09 | -6.8848e-08 | 0.0021312 | 0.0021312 | 0.0021312 | 0.98899 | -0.20907 | 0.98898 | -0.20922 | 0.5855
77 | 0.11199 | 0.028157 | -0.11194 | -0.028128 | 4.4575e-05 | 2.8476e-05 | 0.17014 | 0.17014 | 0.17014 | 0.97959 | -0.39114 | 0.97917 | -0.39948 | 46.7431
78 | 0.0032515 | 0.00081484 | -0.0032514 | -0.00081488 | 4.671e-08 | -3.5922e-08 | 0.00491 | 0.00491 | 0.00491 | 0.98538 | -0.2795 | 0.98537 | -0.2798 | 1.3489
79 | 0.015473 | 0.0038807 | -0.015464 | -0.0038755 | 8.866e-06 | 5.1235e-06 | 0.023372 | 0.023372 | 0.023372 | 0.98513 | -0.28446 | 0.98451 | -0.29649 | 6.421
80 | 0.004864 | 0.001219 | -0.0048637 | -0.001219 | 2.3674e-07 | 2.9826e-09 | 0.0073515 | 0.0073515 | 0.0073515 | 0.98451 | -0.29649 | 0.98446 | -0.29751 | 2.0197
81 | 0.0079235 | 0.0019858 | -0.0079233 | -0.0019858 | 1.8861e-07 | 7.6345e-08 | 0.011991 | 0.011991 | 0.011991 | 0.98325 | -0.32045 | 0.98323 | -0.32095 | 3.2943
82 | 0.055057 | 0.013862 | -0.054996 | -0.013824 | 6.0395e-05 | 3.8361e-05 | 0.083448 | 0.083448 | 0.083448 | 0.98202 | -0.34431 | 0.98085 | -0.36728 | 22.9253
83 | 0.09693 | 0.024562 | -0.096853 | -0.024513 | 7.7457e-05 | 4.9452e-05 | 0.14697 | 0.14697 | 0.14697 | 0.98202 | -0.34431 | 0.98116 | -0.36095 | 40.3767
84 | 0.029658 | 0.0074712 | -0.029627 | -0.0074519 | 3.107e-05 | 1.9369e-05 | 0.045007 | 0.045007 | 0.045007 | 0.98085 | -0.36728 | 0.97972 | -0.38921 | 12.3646
85 | 0.025339 | 0.0063526 | -0.025333 | -0.0063492 | 5.5326e-06 | 3.4149e-06 | 0.038441 | 0.038441 | 0.038441 | 0.98085 | -0.36728 | 0.98061 | -0.37186 | 10.5608
86 | 0.093417 | 0.023652 | -0.093144 | -0.023477 | 0.00027336 | 0.00017449 | 0.14176 | 0.14176 | 0.14176 | 0.98116 | -0.36095 | 0.97803 | -0.4221 | 38.9454
87 | 0.023254 | 0.0058548 | -0.023239 | -0.0058456 | 1.4998e-05 | 9.1955e-06 | 0.035328 | 0.035328 | 0.035328 | 0.97972 | -0.38921 | 0.97903 | -0.40271 | 9.7056
88 | 0.009444 | 0.0023661 | -0.0094432 | -0.0023657 | 8.0353e-07 | 3.8264e-07 | 0.01433 | 0.01433 | 0.01433 | 0.98061 | -0.37186 | 0.98052 | -0.37365 | 3.9369
89 | 0.015889 | 0.0039831 | -0.015887 | -0.0039821 | 1.7532e-06 | 1.0206e-06 | 0.024111 | 0.024111 | 0.024111 | 0.98061 | -0.37186 | 0.98049 | -0.37418 | 6.6239
90 | 0.015419 | 0.003865 | -0.015417 | -0.003864 | 1.8137e-06 | 1.0505e-06 | 0.02346 | 0.02346 | 0.02346 | 0.97803 | -0.4221 | 0.9779 | -0.42456 | 6.445
91 | 0.077725 | 0.019612 | -0.077603 | -0.019534 | 0.00012209 | 7.7846e-05 | 0.1183 | 0.1183 | 0.1183 | 0.97803 | -0.4221 | 0.97635 | -0.45495 | 32.5004
92 | 0.0099164 | 0.0024857 | -0.0099145 | -0.0024848 | 1.8816e-06 | 9.348e-07 | 0.015186 | 0.015187 | 0.015187 | 0.97165 | -0.54758 | 0.97145 | -0.55156 | 4.1721
93 | -0.0099164 | -0.0024857 | 0.009917 | 0.002486 | 5.9009e-07 | 2.9314e-07 | 0.015186 | 0.015186 | 0.015186 | 0.97165 | -0.54758 | 0.97171 | -0.54633 | 4.1721
94 | 0.0071798 | 0.0017995 | -0.0071794 | -0.0017993 | 4.1986e-07 | 1.5399e-07 | 0.010995 | 0.010995 | 0.010995 | 0.97171 | -0.54633 | 0.97165 | -0.54756 | 3.0205
95 | -0.017097 | -0.0042855 | 0.017102 | 0.0042889 | 5.6595e-06 | 3.3492e-06 | 0.026181 | 0.026181 | 0.026181 | 0.97171 | -0.54633 | 0.97207 | -0.53938 | 7.1926
96 | 0.02297 | 0.0057625 | -0.022961 | -0.0057572 | 8.7606e-06 | 5.3722e-06 | 0.035149 | 0.035149 | 0.035149 | 0.97247 | -0.53138 | 0.97207 | -0.53938 | 9.6564
97 | -0.02297 | -0.0057625 | 0.022981 | 0.0057693 | 1.1068e-05 | 6.787e-06 | 0.035149 | 0.035149 | 0.035149 | 0.97247 | -0.53138 | 0.97298 | -0.52128 | 9.6563
98 | 0.011084 | 0.002777 | -0.011082 | -0.0027756 | 2.7238e-06 | 1.4294e-06 | 0.016951 | 0.016952 | 0.016952 | 0.97298 | -0.52128 | 0.97272 | -0.52644 | 4.657
99 | -0.034065 | -0.0085464 | 0.034068 | 0.008548 | 2.6435e-06 | 1.6596e-06 | 0.0521 | 0.0521 | 0.0521 | 0.97298 | -0.52128 | 0.97306 | -0.51965 | 14.3133
100 | -0.011446 | -0.0028686 | 0.011447 | 0.0028694 | 1.4345e-06 | 7.5825e-07 | 0.017373 | 0.017373 | 0.017373 | 0.98036 | -0.37681 | 0.98049 | -0.37418 | 4.7728
101 | 0.0058864 | 0.0014753 | -0.005886 | -0.0014752 | 4.2428e-07 | 9.2842e-08 | 0.0089346 | 0.0089347 | 0.0089347 | 0.98036 | -0.37681 | 0.98028 | -0.37832 | 2.4546
102 | 0.0036563 | 0.00091545 | -0.0036553 | -0.00091592 | 1.041e-06 | -4.7068e-07 | 0.0055484 | 0.0055488 | 0.0055488 | 0.98052 | -0.37365 | 0.98022 | -0.37963 | 1.5244
103 | 0.0057869 | 0.0014503 | -0.0057856 | -0.00145 | 1.3065e-06 | 2.6652e-07 | 0.008782 | 0.0087822 | 0.0087822 | 0.98052 | -0.37365 | 0.98028 | -0.37839 | 2.4127
104 | 0.0036553 | 0.00091592 | -0.003655 | -0.00091604 | 2.5805e-07 | -1.1654e-07 | 0.0055488 | 0.0055489 | 0.0055489 | 0.98022 | -0.37963 | 0.98014 | -0.38111 | 1.5244
105 | 0.019251 | 0.0048461 | -0.019247 | -0.0048438 | 3.8273e-06 | 2.2997e-06 | 0.029267 | 0.029267 | 0.029267 | 0.97903 | -0.40271 | 0.97882 | -0.40687 | 8.0405
106 | -0.059038 | -0.014821 | 0.059135 | 0.014883 | 9.7392e-05 | 6.1934e-05 | 0.090241 | 0.09024 | 0.090241 | 0.9736 | -0.50916 | 0.97535 | -0.47464 | 24.7913
107 | 0.054029 | 0.013566 | -0.054002 | -0.013549 | 2.7016e-05 | 1.7159e-05 | 0.082586 | 0.082586 | 0.082586 | 0.9736 | -0.50916 | 0.97306 | -0.51965 | 22.6885
108 | -0.062167 | -0.015643 | 0.062211 | 0.01567 | 4.33e-05 | 2.7552e-05 | 0.094866 | 0.094866 | 0.094866 | 0.97535 | -0.47464 | 0.97609 | -0.46008 | 26.0622
109 | 0.019935 | 0.0050005 | -0.019923 | -0.0049935 | 1.1621e-05 | 7.0233e-06 | 0.030486 | 0.030486 | 0.030486 | 0.97306 | -0.51965 | 0.97244 | -0.53189 | 8.3752
110 | -0.06483 | -0.016327 | 0.064846 | 0.016337 | 1.5882e-05 | 1.011e-05 | 0.098859 | 0.098859 | 0.098859 | 0.97609 | -0.46008 | 0.97635 | -0.45495 | 27.1591
111 | 0.013199 | 0.0033084 | -0.013199 | -0.0033081 | 5.5721e-07 | 3.1143e-07 | 0.020198 | 0.020198 | 0.020198 | 0.97244 | -0.53189 | 0.9724 | -0.53277 | 5.5488
112 | 0.012757 | 0.0031975 | -0.012756 | -0.0031969 | 1.0959e-06 | 6.047e-07 | 0.019443 | 0.019443 | 0.019443 | 0.97635 | -0.45495 | 0.97626 | -0.45676 | 5.3414
113 | 0.0080957 | 0.0020272 | -0.0080946 | -0.0020268 | 1.1362e-06 | 4.8198e-07 | 0.012384 | 0.012384 | 0.012384 | 0.97272 | -0.52644 | 0.97257 | -0.52939 | 3.4021
114 | 0.0055008 | 0.0013786 | -0.0055005 | -0.0013785 | 3.26e-07 | 5.6451e-08 | 0.0084176 | 0.0084176 | 0.0084176 | 0.9724 | -0.53277 | 0.97234 | -0.53402 | 2.3125
115 | 0.0076981 | 0.0019295 | -0.0076961 | -0.0019287 | 2.0105e-06 | 8.076e-07 | 0.01178 | 0.01178 | 0.01178 | 0.9724 | -0.53277 | 0.97212 | -0.53825 | 3.2363
116 | 0.0036679 | 0.00091735 | -0.0036672 | -0.00091765 | 7.5278e-07 | -3.092e-07 | 0.0056112 | 0.0056115 | 0.0056115 | 0.97257 | -0.52939 | 0.97235 | -0.5337 | 1.5416
117 | 0.0033459 | 0.00083842 | -0.0033458 | -0.00083848 | 9.5794e-08 | -5.9433e-08 | 0.0051215 | 0.0051215 | 0.0051215 | 0.97212 | -0.53825 | 0.97209 | -0.53886 | 1.407
118 | 0.0033458 | 0.00083848 | -0.0033457 | -0.00083852 | 6.0119e-08 | -3.7294e-08 | 0.0051215 | 0.0051215 | 0.0051215 | 0.97209 | -0.53886 | 0.97207 | -0.53923 | 1.407
119 | -0.013364 | -0.0033638 | 0.013368 | 0.0033662 | 4.4351e-06 | 2.4798e-06 | 0.020342 | 0.020342 | 0.020342 | 0.97781 | -0.42664 | 0.97817 | -0.4197 | 5.5885
120 | 0.013364 | 0.0033638 | -0.013319 | -0.0033386 | 4.4985e-05 | 2.5167e-05 | 0.020342 | 0.020344 | 0.020344 | 0.97781 | -0.42664 | 0.97422 | -0.4973 | 5.5889
121 | -0.019236 | -0.0048367 | 0.019247 | 0.0048438 | 1.1798e-05 | 7.0896e-06 | 0.029267 | 0.029267 | 0.029267 | 0.97817 | -0.4197 | 0.97882 | -0.40687 | 8.0405
122 | 0.013319 | 0.0033386 | -0.013317 | -0.0033376 | 1.7769e-06 | 9.9466e-07 | 0.020344 | 0.020344 | 0.020344 | 0.97422 | -0.4973 | 0.97408 | -0.5001 | 5.5889
123 | 0.0036672 | 0.00091765 | -0.0036651 | -0.0009185 | 2.0717e-06 | -8.4867e-07 | 0.0056115 | 0.0056123 | 0.0056123 | 0.97235 | -0.5337 | 0.97175 | -0.54557 | 1.5418
124 | 0.0036651 | 0.0009185 | -0.003665 | -0.00091854 | 9.3016e-08 | -3.8027e-08 | 0.0056123 | 0.0056123 | 0.0056123 | 0.97175 | -0.54557 | 0.97173 | -0.5461 | 1.5418
125 | -0.015593 | -0.0039087 | 0.015595 | 0.0039102 | 2.634e-06 | 1.529e-06 | 0.023719 | 0.023718 | 0.023719 | 0.97824 | -0.4177 | 0.97842 | -0.41416 | 6.5161
126 | 0.014054 | 0.003523 | -0.014052 | -0.0035219 | 1.9412e-06 | 1.1002e-06 | 0.021378 | 0.021378 | 0.021378 | 0.97824 | -0.4177 | 0.97809 | -0.4206 | 5.873
127 | -0.049347 | -0.012374 | 0.049381 | 0.012396 | 3.4547e-05 | 2.1905e-05 | 0.07505 | 0.07505 | 0.07505 | 0.97842 | -0.41416 | 0.97917 | -0.39948 | 20.6183
128 | 0.033751 | 0.0084636 | -0.033739 | -0.0084557 | 1.2615e-05 | 7.9134e-06 | 0.051332 | 0.051332 | 0.051332 | 0.97842 | -0.41416 | 0.97802 | -0.422 | 14.1022
129 | 0.014052 | 0.0035219 | -0.014051 | -0.0035216 | 5.6054e-07 | 3.177e-07 | 0.021378 | 0.021378 | 0.021378 | 0.97809 | -0.4206 | 0.97805 | -0.42144 | 5.873
130 | 0.062563 | 0.015732 | -0.062427 | -0.015646 | 0.0001362 | 8.6662e-05 | 0.095094 | 0.095095 | 0.095095 | 0.97917 | -0.39948 | 0.97684 | -0.44517 | 26.1249
131 | 0.013314 | 0.0033368 | -0.013314 | -0.0033367 | 2.3022e-07 | 1.2856e-07 | 0.020256 | 0.020256 | 0.020256 | 0.97805 | -0.42144 | 0.97803 | -0.4218 | 5.5649
132 | 0.0092684 | 0.0023235 | -0.0092655 | -0.0023221 | 2.9617e-06 | 1.3972e-06 | 0.014102 | 0.014102 | 0.014102 | 0.97803 | -0.4218 | 0.97769 | -0.42851 | 3.8741
133 | 0.0040454 | 0.0010132 | -0.0040447 | -0.0010133 | 6.5508e-07 | -1.5937e-07 | 0.0061546 | 0.0061548 | 0.0061548 | 0.97803 | -0.4218 | 0.97786 | -0.4252 | 1.6909
134 | 0.0017389 | 0.00043543 | -0.0017388 | -0.0004356 | 4.0692e-08 | -1.6838e-07 | 0.002646 | 0.002646 | 0.002646 | 0.97786 | -0.4252 | 0.97783 | -0.42569 | 0.72693
135 | -0.0017388 | -0.00043576 | 0.0017388 | 0.00043565 | 2.4371e-08 | -1.0083e-07 | 0.0026461 | 0.002646 | 0.0026461 | 0.97781 | -0.42615 | 0.97782 | -0.42586 | 0.72695
136 | 0.00069177 | 0.00017334 | -0.00069177 | -0.00017337 | 1.0506e-09 | -3.1038e-08 | 0.0010527 | 0.0010527 | 0.0010527 | 0.97781 | -0.42615 | 0.97781 | -0.42619 | 0.28921
137 | -0.0017388 | -0.00043565 | 0.0017388 | 0.0004356 | 1.3682e-08 | -5.661e-08 | 0.002646 | 0.002646 | 0.002646 | 0.97782 | -0.42586 | 0.97783 | -0.42569 | 0.72694

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57394 | 0.14734

## res_load
| p_mw | q_mvar
0 | 0.002777 | 0.00069597
1 | 0.0041162 | 0.0010316
2 | 0.00409 | 0.0010251
3 | 0.0033977 | 0.00085154
4 | 0.0074976 | 0.0018791
5 | 0.0067851 | 0.0017005
6 | 0.0072615 | 0.0018199
7 | 0.010477 | 0.0026258
8 | 0.008642 | 0.0021659
9 | 0.0086721 | 0.0021734
10 | 0.0058034 | 0.0014545
11 | 0.004881 | 0.0012233
12 | 0.0072885 | 0.0018267
13 | 0.0090392 | 0.0022654
14 | 0.010719 | 0.0026864
15 | 0.0060866 | 0.0015254
16 | 0.006033 | 0.001512
17 | 0.0052688 | 0.0013205
18 | 0.0048502 | 0.0012156
19 | 0.0048271 | 0.0012098
20 | 0.0066052 | 0.0016554
21 | 0.0070882 | 0.0017765
22 | 0.0071605 | 0.0017946
23 | 0.00436 | 0.0010927
24 | 0.037525 | 0.0094047
25 | 0.0031533 | 0.00079028
26 | 0.0013735 | 0.00034424
27 | 0.0013419 | 0.00033632
28 | 0.0016611 | 0.00041632
29 | 0.015469 | 0.0038768
30 | 0.00071096 | 0.00017818
31 | 0.0023672 | 0.00059329
32 | 0.0018892 | 0.00047347
33 | 0.00082286 | 0.00020623
34 | 0.001376 | 0.00034485
35 | 0.0022801 | 0.00057144
36 | 0.0014739 | 0.00036939
37 | 0.0061879 | 0.0015508
38 | 0.0032514 | 0.00081488
39 | 0.0106 | 0.0026566
40 | 0.0048637 | 0.001219
41 | 0.0020536 | 0.00051467
42 | 0.010646 | 0.0026681
43 | 0.0079233 | 0.0019858
44 | 0.0034355 | 0.00086103
45 | 0.0063726 | 0.0015971
46 | 0.0099145 | 0.0024848
47 | 0.0058585 | 0.0014683
48 | 0.0071794 | 0.0017993
49 | 0.0055595 | 0.0013933
50 | 0.0044399 | 0.0011127
51 | 0.005886 | 0.0014752
52 | 0.0057856 | 0.00145
53 | 0.0039879 | 0.00099947
54 | 0.003655 | 0.00091604
55 | 0.0050083 | 0.0012552
56 | 0.0030322 | 0.00075995
57 | 0.0026191 | 0.00065641
58 | 0.0067234 | 0.0016851
59 | 0.002986 | 0.00074837
60 | 0.012756 | 0.0031969
61 | 0.0044266 | 0.0011094
62 | 0.0055005 | 0.0013785
63 | 0.0043502 | 0.0010903
64 | 0.0033457 | 0.00083852
65 | 0.0058672 | 0.0014705
66 | 0.013317 | 0.0033376
67 | 0.0012543 | 0.00031435
68 | 0.003665 | 0.00091854
69 | 0.015417 | 0.003864
70 | 0.0015389 | 0.00038568
71 | 0.033739 | 0.0084557
72 | 0.00073721 | 0.00018476
73 | 0.062427 | 0.015646
74 | 0.0092655 | 0.0023221
75 | 0.0023058 | 0.00057789
76 | 0.0014165 | 0.000355
77 | 0.001047 | 0.00026241
78 | 0.00069177 | 0.00017337
79 | 0.025863 | 0.0064819

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1