## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-41_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-41_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-41_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1630-41_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1630-41_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-41_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1630-41_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1630-41_0_4_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_1630-41_0_4_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1630-41_0_4_node_29 | 0.4 | n |  | TRUE
10 | bus_LV_1630-41_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1630-41_0_4_node_67 | 0.4 | n |  | TRUE
12 | bus_LV_1630-41_0_4_node_99 | 0.4 | n |  | TRUE
13 | bus_LV_1630-41_0_4_node_52 | 0.4 | n |  | TRUE
14 | bus_LV_1630-41_0_4_node_49 | 0.4 | n |  | TRUE
15 | bus_LV_1630-41_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_1630-41_0_4_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_1630-41_0_4_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_1630-41_0_4_node_66 | 0.4 | n |  | TRUE
19 | bus_LV_1630-41_0_4_node_101 | 0.4 | n |  | TRUE
20 | bus_LV_1630-41_0_4_node_98 | 0.4 | n |  | TRUE
21 | bus_LV_1630-41_0_4_node_53 | 0.4 | n |  | TRUE
22 | bus_LV_1630-41_0_4_node_50 | 0.4 | n |  | TRUE
23 | bus_LV_1630-41_0_4_node_8 | 0.4 | n |  | TRUE
24 | bus_LV_1630-41_0_4_node_9 | 0.4 | n |  | TRUE
25 | bus_LV_1630-41_0_4_node_10 | 0.4 | n |  | TRUE
26 | bus_LV_1630-41_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_1630-41_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1630-41_0_4_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_1630-41_0_4_node_125 | 0.4 | n |  | TRUE
30 | bus_LV_1630-41_0_4_node_132 | 0.4 | n |  | TRUE
31 | bus_LV_1630-41_0_4_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_1630-41_0_4_node_13 | 0.4 | n |  | TRUE
33 | bus_LV_1630-41_0_4_node_14 | 0.4 | n |  | TRUE
34 | bus_LV_1630-41_0_4_node_150 | 0.4 | n |  | TRUE
35 | bus_LV_1630-41_0_4_node_151 | 0.4 | n |  | TRUE
36 | bus_LV_1630-41_0_4_node_156 | 0.4 | n |  | TRUE
37 | bus_LV_1630-41_0_4_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_1630-41_0_4_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_1630-41_0_4_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_1630-41_0_4_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_1630-41_0_4_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_1630-41_0_4_node_25 | 0.4 | n |  | TRUE
43 | bus_LV_1630-41_0_4_node_152 | 0.4 | n |  | TRUE
44 | bus_LV_1630-41_0_4_node_134 | 0.4 | n |  | TRUE
45 | bus_LV_1630-41_0_4_node_123 | 0.4 | n |  | TRUE
46 | bus_LV_1630-41_0_4_node_133 | 0.4 | n |  | TRUE
47 | bus_LV_1630-41_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_1630-41_0_4_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1630-41_0_4_node_131 | 0.4 | n |  | TRUE
50 | bus_LV_1630-41_0_4_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_1630-41_0_4_node_119 | 0.4 | n |  | TRUE
52 | bus_LV_1630-41_0_4_node_116 | 0.4 | n |  | TRUE
53 | bus_LV_1630-41_0_4_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_1630-41_0_4_node_114 | 0.4 | n |  | TRUE
55 | bus_LV_1630-41_0_4_node_120 | 0.4 | n |  | TRUE
56 | bus_LV_1630-41_0_4_node_108 | 0.4 | n |  | TRUE
57 | bus_LV_1630-41_0_4_node_130 | 0.4 | n |  | TRUE
58 | bus_LV_1630-41_0_4_node_117 | 0.4 | n |  | TRUE
59 | bus_LV_1630-41_0_4_node_112 | 0.4 | n |  | TRUE
60 | bus_LV_1630-41_0_4_node_113 | 0.4 | n |  | TRUE
61 | bus_LV_1630-41_0_4_node_154 | 0.4 | n |  | TRUE
62 | bus_LV_1630-41_0_4_node_155 | 0.4 | n |  | TRUE
63 | bus_LV_1630-41_0_4_node_146 | 0.4 | n |  | TRUE
64 | bus_LV_1630-41_0_4_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_1630-41_0_4_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_1630-41_0_4_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_1630-41_0_4_node_105 | 0.4 | n |  | TRUE
68 | bus_LV_1630-41_0_4_node_35 | 0.4 | n |  | TRUE
69 | bus_LV_1630-41_0_4_node_36 | 0.4 | n |  | TRUE
70 | bus_LV_1630-41_0_4_node_37 | 0.4 | n |  | TRUE
71 | bus_LV_1630-41_0_4_node_38 | 0.4 | n |  | TRUE
72 | bus_LV_1630-41_0_4_node_39 | 0.4 | n |  | TRUE
73 | bus_LV_1630-41_0_4_node_42 | 0.4 | n |  | TRUE
74 | bus_LV_1630-41_0_4_node_40 | 0.4 | n |  | TRUE
75 | bus_LV_1630-41_0_4_node_141 | 0.4 | n |  | TRUE
76 | bus_LV_1630-41_0_4_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_1630-41_0_4_node_41 | 0.4 | n |  | TRUE
78 | bus_LV_1630-41_0_4_node_142 | 0.4 | n |  | TRUE
79 | bus_LV_1630-41_0_4_node_144 | 0.4 | n |  | TRUE
80 | bus_LV_1630-41_0_4_node_143 | 0.4 | n |  | TRUE
81 | bus_LV_1630-41_0_4_node_153 | 0.4 | n |  | TRUE
82 | bus_LV_1630-41_0_4_node_48 | 0.4 | n |  | TRUE
83 | bus_LV_1630-41_0_4_node_43 | 0.4 | n |  | TRUE
84 | bus_LV_1630-41_0_4_node_91 | 0.4 | n |  | TRUE
85 | bus_LV_1630-41_0_4_node_89 | 0.4 | n |  | TRUE
86 | bus_LV_1630-41_0_4_node_44 | 0.4 | n |  | TRUE
87 | bus_LV_1630-41_0_4_node_45 | 0.4 | n |  | TRUE
88 | bus_LV_1630-41_0_4_node_46 | 0.4 | n |  | TRUE
89 | bus_LV_1630-41_0_4_node_47 | 0.4 | n |  | TRUE
90 | bus_LV_1630-41_0_4_node_84 | 0.4 | n |  | TRUE
91 | bus_LV_1630-41_0_4_node_57 | 0.4 | n |  | TRUE
92 | bus_LV_1630-41_0_4_node_83 | 0.4 | n |  | TRUE
93 | bus_LV_1630-41_0_4_node_59 | 0.4 | n |  | TRUE
94 | bus_LV_1630-41_0_4_node_51 | 0.4 | n |  | TRUE
95 | bus_LV_1630-41_0_4_node_72 | 0.4 | n |  | TRUE
96 | bus_LV_1630-41_0_4_node_71 | 0.4 | n |  | TRUE
97 | bus_LV_1630-41_0_4_node_54 | 0.4 | n |  | TRUE
98 | bus_LV_1630-41_0_4_node_82 | 0.4 | n |  | TRUE
99 | bus_LV_1630-41_0_4_node_75 | 0.4 | n |  | TRUE
100 | bus_LV_1630-41_0_4_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_1630-41_0_4_node_76 | 0.4 | n |  | TRUE
102 | bus_LV_1630-41_0_4_node_60 | 0.4 | n |  | TRUE
103 | bus_LV_1630-41_0_4_node_61 | 0.4 | n |  | TRUE
104 | bus_LV_1630-41_0_4_node_62 | 0.4 | n |  | TRUE
105 | bus_LV_1630-41_0_4_node_64 | 0.4 | n |  | TRUE
106 | bus_LV_1630-41_0_4_node_77 | 0.4 | n |  | TRUE
107 | bus_LV_1630-41_0_4_node_73 | 0.4 | n |  | TRUE
108 | bus_LV_1630-41_0_4_node_90 | 0.4 | n |  | TRUE
109 | bus_LV_1630-41_0_4_node_149 | 0.4 | n |  | TRUE
110 | bus_LV_1630-41_0_4_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_1630-41_0_4_node_74 | 0.4 | n |  | TRUE
112 | bus_LV_1630-41_0_4_node_138 | 0.4 | n |  | TRUE
113 | bus_LV_1630-41_0_4_node_139 | 0.4 | n |  | TRUE
114 | bus_LV_1630-41_0_4_node_158 | 0.4 | n |  | TRUE
115 | bus_LV_1630-41_0_4_node_68 | 0.4 | n |  | TRUE
116 | bus_LV_1630-41_0_4_node_69 | 0.4 | n |  | TRUE
117 | bus_LV_1630-41_0_4_node_70 | 0.4 | n |  | TRUE
118 | bus_LV_1630-41_0_4_node_88 | 0.4 | n |  | TRUE
119 | bus_LV_1630-41_0_4_node_92 | 0.4 | n |  | TRUE
120 | bus_LV_1630-41_0_4_node_87 | 0.4 | n |  | TRUE
121 | bus_LV_1630-41_0_4_node_81 | 0.4 | n |  | TRUE
122 | bus_LV_1630-41_0_4_node_78 | 0.4 | n |  | TRUE
123 | bus_LV_1630-41_0_4_node_160 | 0.4 | n |  | TRUE
124 | bus_LV_1630-41_0_4_node_161 | 0.4 | n |  | TRUE
125 | bus_LV_1630-41_0_4_node_79 | 0.4 | n |  | TRUE
126 | bus_LV_1630-41_0_4_node_80 | 0.4 | n |  | TRUE
127 | bus_LV_1630-41_0_4_node_94 | 0.4 | n |  | TRUE
128 | bus_LV_1630-41_0_4_node_93 | 0.4 | n |  | TRUE
129 | bus_LV_1630-41_0_4_node_162 | 0.4 | n |  | TRUE
130 | bus_LV_1630-41_0_4_node_86 | 0.4 | n |  | TRUE
131 | bus_LV_1630-41_0_4_node_102 | 0.4 | n |  | TRUE
132 | bus_LV_1630-41_0_4_node_95 | 0.4 | n |  | TRUE
133 | bus_LV_1630-41_0_4_node_96 | 0.4 | n |  | TRUE
134 | bus_LV_1630-41_0_4_node_97 | 0.4 | n |  | TRUE
135 | bus_LV_1630-41_0_4_node_100 | 0.4 | n |  | TRUE
136 | bus_LV_1630-41_0_4_node_104 | 0.4 | n |  | TRUE
137 | bus_LV_1630-41_0_4_node_106 | 0.4 | n |  | TRUE
138 | bus_LV_1630-41_0_4_node_107 | 0.4 | n |  | TRUE
139 | bus_LV_1630-41_0_4_node_109 | 0.4 | n |  | TRUE
140 | bus_LV_1630-41_0_4_node_110 | 0.4 | n |  | TRUE
141 | bus_LV_1630-41_0_4_node_129 | 0.4 | n |  | TRUE
142 | bus_LV_1630-41_0_4_node_126 | 0.4 | n |  | TRUE
143 | bus_LV_1630-41_0_4_node_157 | 0.4 | n |  | TRUE
144 | bus_LV_1630-41_0_4_node_122 | 0.4 | n |  | TRUE
145 | bus_LV_1630-41_0_4_node_127 | 0.4 | n |  | TRUE
146 | bus_LV_1630-41_0_4_node_124 | 0.4 | n |  | TRUE
147 | bus_LV_1630-41_0_4_node_121 | 0.4 | n |  | TRUE
148 | bus_LV_1630-41_0_4_node_111 | 0.4 | n |  | TRUE
149 | bus_LV_1630-41_0_4_node_115 | 0.4 | n |  | TRUE
150 | bus_LV_1630-41_0_4_node_118 | 0.4 | n |  | TRUE
151 | bus_LV_1630-41_0_4_node_137 | 0.4 | n |  | TRUE
152 | bus_LV_1630-41_0_4_node_136 | 0.4 | n |  | TRUE
153 | bus_LV_1630-41_0_4_node_135 | 0.4 | n |  | TRUE
154 | bus_LV_1630-41_0_4_node_145 | 0.4 | n |  | TRUE
155 | bus_LV_1630-41_0_4_node_128 | 0.4 | n |  | TRUE
156 | bus_LV_1630-41_0_4_node_140 | 0.4 | n |  | TRUE
157 | bus_LV_1630-41_0_4_node_159 | 0.4 | n |  | TRUE
158 | bus_MV_152_0_node_63 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-41_0_4_load_0 | 0 | 0.030205 | 0.0075701 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-41_0_4_load_1 | 1 | 0.0053902 | 0.0013509 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-41_0_4_load_4 | 4 | 0.01114 | 0.0027918 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-41_0_4_load_5 | 5 | 0.0053448 | 0.0013395 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-41_0_4_load_18 | 7 | 0.0003046 | 7.6341e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-41_0_4_load_29 | 9 | 0.0043024 | 0.0010783 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-41_0_4_load_67 | 11 | 0.0027501 | 0.00068923 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-41_0_4_load_52 | 13 | 0.0062614 | 0.0015693 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-41_0_4_load_49 | 14 | 0.0056313 | 0.0014113 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-41_0_4_load_16 | 15 | 0.010398 | 0.0026059 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-41_0_4_load_28 | 17 | 0.0038281 | 0.00095942 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-41_0_4_load_66 | 18 | 0.003213 | 0.00080525 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-41_0_4_load_101 | 19 | 0.0040389 | 0.0010122 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-41_0_4_load_98 | 20 | 0.0043325 | 0.0010858 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-41_0_4_load_8 | 23 | 0.0013396 | 0.00033574 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-41_0_4_load_9 | 24 | 0.00077983 | 0.00019544 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-41_0_4_load_10 | 25 | 0.0016099 | 0.00040347 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-41_0_4_load_12 | 26 | 0.0011319 | 0.00028368 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-41_0_4_load_132 | 30 | 0.00076313 | 0.00019126 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-41_0_4_load_17 | 31 | 0.00055988 | 0.00014032 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-41_0_4_load_13 | 32 | 0.0011148 | 0.00027939 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-41_0_4_load_14 | 33 | 0.0010445 | 0.00026179 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-41_0_4_load_150 | 34 | 0.0062181 | 0.0015584 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-41_0_4_load_156 | 36 | 0.0076048 | 0.0019059 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-41_0_4_load_21 | 38 | 0.0039589 | 0.00099219 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-41_0_4_load_22 | 39 | 0.0046487 | 0.0011651 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-41_0_4_load_23 | 40 | 0.0039338 | 0.0009859 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-41_0_4_load_24 | 41 | 0.0040059 | 0.001004 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-41_0_4_load_152 | 43 | 0.0040626 | 0.0010182 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-41_0_4_load_134 | 44 | 0.00083724 | 0.00020983 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-41_0_4_load_133 | 46 | 0.0006066 | 0.00015203 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1630-41_0_4_load_31 | 48 | 0.004788 | 0.0012 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1630-41_0_4_load_131 | 49 | 0.0048583 | 0.0012176 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1630-41_0_4_load_119 | 51 | 0.0045891 | 0.0011501 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1630-41_0_4_load_116 | 52 | 0.0005997 | 0.0001503 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1630-41_0_4_load_108 | 56 | 0.0022651 | 0.00056769 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1630-41_0_4_load_130 | 57 | 0.00056766 | 0.00014227 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1630-41_0_4_load_117 | 58 | 0.0035705 | 0.00089486 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1630-41_0_4_load_112 | 59 | 0.00044461 | 0.00011143 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1630-41_0_4_load_154 | 61 | 0.0033572 | 0.00084139 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1630-41_0_4_load_155 | 62 | 0.0024013 | 0.00060182 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1630-41_0_4_load_58 | 65 | 0.0052139 | 0.0013067 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1630-41_0_4_load_55 | 66 | 0.0071775 | 0.0017989 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1630-41_0_4_load_35 | 68 | 0.0086088 | 0.0021576 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1630-41_0_4_load_37 | 70 | 0.0091842 | 0.0023018 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1630-41_0_4_load_42 | 73 | 0.0056614 | 0.0014189 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1630-41_0_4_load_40 | 74 | 0.0053405 | 0.0013385 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1630-41_0_4_load_141 | 75 | 0.0057759 | 0.0014476 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1630-41_0_4_load_144 | 79 | 0.024376 | 0.0061091 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1630-41_0_4_load_153 | 81 | 0.0049479 | 0.0012401 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1630-41_0_4_load_43 | 83 | 0.0080574 | 0.0020194 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1630-41_0_4_load_91 | 84 | 0.0063318 | 0.0015869 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1630-41_0_4_load_89 | 85 | 0.01122 | 0.002812 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1630-41_0_4_load_44 | 86 | 0.0076039 | 0.0019057 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1630-41_0_4_load_45 | 87 | 0.0086208 | 0.0021606 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1630-41_0_4_load_46 | 88 | 0.0030994 | 0.00077679 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1630-41_0_4_load_47 | 89 | 0.0065932 | 0.0016524 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1630-41_0_4_load_84 | 90 | 0.0086453 | 0.0021667 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1630-41_0_4_load_83 | 92 | 0.0074974 | 0.001879 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1630-41_0_4_load_59 | 93 | 0.015093 | 0.0037827 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1630-41_0_4_load_72 | 95 | 0.0044403 | 0.0011129 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1630-41_0_4_load_71 | 96 | 0.0084358 | 0.0021142 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1630-41_0_4_load_54 | 97 | 0.0065911 | 0.0016519 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1630-41_0_4_load_82 | 98 | 0.0058794 | 0.0014735 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1630-41_0_4_load_85 | 100 | 0.011728 | 0.0029393 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1630-41_0_4_load_60 | 102 | 0.0078696 | 0.0019723 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1630-41_0_4_load_61 | 103 | 0.013469 | 0.0033758 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1630-41_0_4_load_77 | 106 | 0.013653 | 0.0034218 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1630-41_0_4_load_73 | 107 | 0.0078652 | 0.0019712 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1630-41_0_4_load_149 | 109 | 0.0098288 | 0.0024633 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1630-41_0_4_load_138 | 112 | 0.0016905 | 0.00042369 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1630-41_0_4_load_69 | 116 | 0.0062975 | 0.0015783 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1630-41_0_4_load_70 | 117 | 0.0031716 | 0.00079488 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1630-41_0_4_load_92 | 119 | 0.0090588 | 0.0022704 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1630-41_0_4_load_78 | 122 | 0.006174 | 0.0015474 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1630-41_0_4_load_160 | 123 | 0.0047386 | 0.0011876 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1630-41_0_4_load_79 | 125 | 0.0062794 | 0.0015738 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1630-41_0_4_load_80 | 126 | 0.010674 | 0.0026752 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1630-41_0_4_load_94 | 127 | 0.002334 | 0.00058495 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1630-41_0_4_load_93 | 128 | 0.0095417 | 0.0023914 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1630-41_0_4_load_162 | 129 | 0.0036034 | 0.00090309 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1630-41_0_4_load_86 | 130 | 0.008417 | 0.0021095 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1630-41_0_4_load_102 | 131 | 0.002989 | 0.00074912 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1630-41_0_4_load_96 | 133 | 0.004326 | 0.0010842 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1630-41_0_4_load_97 | 134 | 0.0058648 | 0.0014699 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1630-41_0_4_load_100 | 135 | 0.0046352 | 0.0011617 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1630-41_0_4_load_104 | 136 | 0.0013499 | 0.00033831 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1630-41_0_4_load_109 | 139 | 0.00054243 | 0.00013595 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1630-41_0_4_load_129 | 141 | 0.00076673 | 0.00019216 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1630-41_0_4_load_126 | 142 | 0.00058816 | 0.00014741 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1630-41_0_4_load_157 | 143 | 0.00052259 | 0.00013097 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1630-41_0_4_load_124 | 146 | 0.0005221 | 0.00013085 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1630-41_0_4_load_121 | 147 | 0.001437 | 0.00036016 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1630-41_0_4_load_111 | 148 | 0.00052316 | 0.00013112 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1630-41_0_4_load_115 | 149 | 0.0013598 | 0.00034081 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1630-41_0_4_load_137 | 151 | 0.00085712 | 0.00021481 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1630-41_0_4_load_136 | 152 | 0.003669 | 0.00091954 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1630-41_0_4_load_135 | 153 | 0.00088152 | 0.00022093 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1630-41_0_4_load_145 | 154 | 0.0030041 | 0.0007529 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1630-41_0_4_load_128 | 155 | 0.0016741 | 0.00041957 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1630-41_0_4_load_140 | 156 | 0.0052327 | 0.0013114 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1630-41_0_4_load_159 | 157 | 0.015977 | 0.0040043 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 89 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-41_0_4_line_0 |  | 0 | 1 | 0.0085437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-41_0_4_line_1 |  | 1 | 2 | 0.014093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-41_0_4_line_2 |  | 2 | 7 | 0.0024612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-41_0_4_line_3 |  | 2 | 8 | 0.037378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-41_0_4_line_4 |  | 3 | 4 | 0.025877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-41_0_4_line_5 |  | 3 | 5 | 0.016642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-41_0_4_line_6 |  | 3 | 6 | 0.049383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1630-41_0_4_line_7 |  | 4 | 8 | 0.021542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-41_0_4_line_8 |  | 5 | 9 | 0.0038474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-41_0_4_line_9 |  | 6 | 10 | 0.021741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1630-41_0_4_line_10 |  | 6 | 11 | 0.0095582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-41_0_4_line_11 |  | 6 | 12 | 0.036045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-41_0_4_line_12 |  | 7 | 15 | 0.014643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-41_0_4_line_13 |  | 8 | 16 | 0.004942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-41_0_4_line_14 |  | 9 | 17 | 0.011644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-41_0_4_line_15 |  | 10 | 13 | 0.0091676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1630-41_0_4_line_16 |  | 10 | 14 | 0.017686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-41_0_4_line_17 |  | 11 | 18 | 0.02083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-41_0_4_line_18 |  | 12 | 19 | 0.010738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-41_0_4_line_19 |  | 12 | 20 | 0.013878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-41_0_4_line_20 |  | 13 | 21 | 0.0091781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1630-41_0_4_line_21 |  | 14 | 22 | 0.0025409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-41_0_4_line_22 |  | 15 | 33 | 0.0098828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-41_0_4_line_23 |  | 16 | 34 | 0.006874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-41_0_4_line_24 |  | 16 | 35 | 0.020429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-41_0_4_line_25 |  | 17 | 47 | 0.0077422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-41_0_4_line_26 |  | 18 | 115 | 0.0098626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-41_0_4_line_27 |  | 19 | 131 | 0.023687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-41_0_4_line_28 |  | 20 | 135 | 0.0026552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-41_0_4_line_29 |  | 21 | 97 | 0.0067411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_1630-41_0_4_line_30 |  | 22 | 94 | 0.014893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-41_0_4_line_31 |  | 23 | 24 | 0.0014534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-41_0_4_line_32 |  | 23 | 25 | 0.028793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-41_0_4_line_33 |  | 25 | 26 | 0.0028708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-41_0_4_line_34 |  | 26 | 27 | 0.015217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1630-41_0_4_line_35 |  | 27 | 31 | 0.010471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-41_0_4_line_36 |  | 27 | 32 | 0.006206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-41_0_4_line_37 |  | 28 | 29 | 0.021589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-41_0_4_line_38 |  | 28 | 30 | 0.012903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-41_0_4_line_39 |  | 29 | 44 | 0.013942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-41_0_4_line_40 |  | 29 | 45 | 0.022608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-41_0_4_line_41 |  | 30 | 46 | 0.0046519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-41_0_4_line_42 |  | 32 | 33 | 0.011381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-41_0_4_line_43 |  | 35 | 36 | 0.007552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-41_0_4_line_44 |  | 35 | 37 | 0.020728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1630-41_0_4_line_45 |  | 37 | 43 | 0.007206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1630-41_0_4_line_46 |  | 37 | 42 | 0.1482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1630-41_0_4_line_47 |  | 38 | 39 | 0.018023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1630-41_0_4_line_48 |  | 38 | 40 | 0.0042606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1630-41_0_4_line_49 |  | 39 | 41 | 0.0071417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1630-41_0_4_line_50 |  | 41 | 42 | 0.016917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1630-41_0_4_line_51 |  | 44 | 153 | 0.017907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1630-41_0_4_line_52 |  | 45 | 147 | 0.013438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1630-41_0_4_line_53 |  | 47 | 48 | 0.038855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1630-41_0_4_line_54 |  | 48 | 49 | 0.010319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1630-41_0_4_line_55 |  | 49 | 57 | 0.0086587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1630-41_0_4_line_56 |  | 50 | 51 | 0.011692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1630-41_0_4_line_57 |  | 50 | 52 | 0.024495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1630-41_0_4_line_58 |  | 51 | 57 | 0.00061481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1630-41_0_4_line_59 |  | 52 | 58 | 0.01123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1630-41_0_4_line_60 |  | 53 | 54 | 0.046593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1630-41_0_4_line_61 |  | 53 | 55 | 0.1398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1630-41_0_4_line_62 |  | 53 | 56 | 0.024364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1630-41_0_4_line_63 |  | 54 | 59 | 0.024987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1630-41_0_4_line_64 |  | 54 | 60 | 0.060607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1630-41_0_4_line_65 |  | 55 | 61 | 0.030589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1630-41_0_4_line_66 |  | 55 | 62 | 0.008401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1630-41_0_4_line_67 |  | 55 | 63 | 0.10362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1630-41_0_4_line_68 |  | 56 | 67 | 0.014387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1630-41_0_4_line_69 |  | 58 | 150 | 0.015377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1630-41_0_4_line_70 |  | 60 | 149 | 0.030703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1630-41_0_4_line_71 |  | 60 | 148 | 0.067021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1630-41_0_4_line_72 |  | 63 | 154 | 0.021528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1630-41_0_4_line_73 |  | 64 | 65 | 0.021773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1630-41_0_4_line_74 |  | 64 | 66 | 0.032882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1630-41_0_4_line_75 |  | 65 | 99 | 0.024098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1630-41_0_4_line_76 |  | 66 | 91 | 0.0035205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_1630-41_0_4_line_77 |  | 67 | 138 | 0.005613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1630-41_0_4_line_78 |  | 67 | 136 | 0.016816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1630-41_0_4_line_79 |  | 68 | 69 | 0.022533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1630-41_0_4_line_80 |  | 68 | 70 | 0.031899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1630-41_0_4_line_81 |  | 69 | 71 | 0.011637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1630-41_0_4_line_82 |  | 69 | 72 | 0.023864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1630-41_0_4_line_83 |  | 71 | 73 | 0.016491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1630-41_0_4_line_84 |  | 71 | 74 | 0.0087058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1630-41_0_4_line_85 |  | 72 | 75 | 0.0066539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1630-41_0_4_line_86 |  | 73 | 76 | 0.010698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1630-41_0_4_line_87 |  | 74 | 77 | 0.017816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1630-41_0_4_line_88 |  | 75 | 78 | 0.015762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1630-41_0_4_line_89 |  | 76 | 85 | 0.008682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1630-41_0_4_line_90 |  | 77 | 83 | 0.010042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1630-41_0_4_line_91 |  | 78 | 79 | 0.013599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1630-41_0_4_line_92 |  | 78 | 80 | 0.041184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1630-41_0_4_line_93 |  | 80 | 81 | 0.01042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1630-41_0_4_line_94 |  | 80 | 82 | 0.01611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1630-41_0_4_line_95 |  | 82 | 91 | 0.008007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_1630-41_0_4_line_96 |  | 82 | 88 | 0.0091816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_1630-41_0_4_line_97 |  | 83 | 84 | 0.0082622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1630-41_0_4_line_98 |  | 86 | 87 | 0.0044601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_1630-41_0_4_line_99 |  | 86 | 88 | 0.012285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_1630-41_0_4_line_100 |  | 87 | 89 | 0.011979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_1630-41_0_4_line_101 |  | 89 | 90 | 0.00067043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_1630-41_0_4_line_102 |  | 90 | 92 | 0.016436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_1630-41_0_4_line_103 |  | 91 | 93 | 0.014618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1630-41_0_4_line_104 |  | 92 | 98 | 0.021354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_1630-41_0_4_line_105 |  | 94 | 95 | 0.00651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1630-41_0_4_line_106 |  | 94 | 96 | 0.0040549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1630-41_0_4_line_107 |  | 97 | 98 | 0.011964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_1630-41_0_4_line_108 |  | 99 | 100 | 0.027479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1630-41_0_4_line_109 |  | 99 | 101 | 0.051136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1630-41_0_4_line_110 |  | 101 | 121 | 0.007865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1630-41_0_4_line_111 |  | 101 | 122 | 0.024559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1630-41_0_4_line_112 |  | 101 | 111 | 0.085499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1630-41_0_4_line_113 |  | 102 | 103 | 0.02118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1630-41_0_4_line_114 |  | 102 | 104 | 0.051165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1630-41_0_4_line_115 |  | 104 | 105 | 0.095651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1630-41_0_4_line_116 |  | 105 | 106 | 0.010259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1630-41_0_4_line_117 |  | 105 | 107 | 0.020707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1630-41_0_4_line_118 |  | 107 | 111 | 0.0089795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1630-41_0_4_line_119 |  | 108 | 109 | 0.005282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1630-41_0_4_line_120 |  | 108 | 110 | 0.003962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1630-41_0_4_line_121 |  | 110 | 131 | 0.02682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1630-41_0_4_line_122 |  | 112 | 113 | 0.034233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1630-41_0_4_line_123 |  | 112 | 114 | 0.073075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1630-41_0_4_line_124 |  | 113 | 156 | 0.01994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1630-41_0_4_line_125 |  | 114 | 157 | 0.042757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1630-41_0_4_line_126 |  | 115 | 116 | 0.002489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1630-41_0_4_line_127 |  | 115 | 117 | 0.0073691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1630-41_0_4_line_128 |  | 116 | 118 | 0.024363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1630-41_0_4_line_129 |  | 117 | 119 | 0.016843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1630-41_0_4_line_130 |  | 118 | 120 | 0.004934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1630-41_0_4_line_131 |  | 120 | 130 | 0.017183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1630-41_0_4_line_132 |  | 121 | 123 | 0.009252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1630-41_0_4_line_133 |  | 121 | 124 | 0.029321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1630-41_0_4_line_134 |  | 122 | 125 | 0.0054927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1630-41_0_4_line_135 |  | 124 | 129 | 0.012326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1630-41_0_4_line_136 |  | 125 | 126 | 0.022609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1630-41_0_4_line_137 |  | 126 | 127 | 0.0021018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1630-41_0_4_line_138 |  | 127 | 128 | 0.0075998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1630-41_0_4_line_139 |  | 128 | 132 | 0.024189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1630-41_0_4_line_140 |  | 129 | 157 | 0.058501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1630-41_0_4_line_141 |  | 132 | 133 | 0.010878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1630-41_0_4_line_142 |  | 132 | 134 | 0.011251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1630-41_0_4_line_143 |  | 136 | 137 | 0.0053253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1630-41_0_4_line_144 |  | 137 | 139 | 0.006367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1630-41_0_4_line_145 |  | 137 | 140 | 0.016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1630-41_0_4_line_146 |  | 138 | 141 | 0.012178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1630-41_0_4_line_147 |  | 138 | 142 | 0.049532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_1630-41_0_4_line_148 |  | 140 | 143 | 0.009182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_1630-41_0_4_line_149 |  | 140 | 144 | 0.011074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_1630-41_0_4_line_150 |  | 142 | 145 | 0.015155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_1630-41_0_4_line_151 |  | 144 | 146 | 0.014646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_1630-41_0_4_line_152 |  | 144 | 147 | 0.017867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_1630-41_0_4_line_153 |  | 145 | 155 | 0.023291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_1630-41_0_4_line_154 |  | 150 | 151 | 0.011782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_1630-41_0_4_line_155 |  | 150 | 152 | 0.02038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_1630-41_0_4_line_156 |  | 152 | 153 | 0.02733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-41_0_4_trafo_47 | 0.63 MVA 20/0.4 kV | 158 | 89 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2724401.291 | 1216537.3552 | 2724401.4742 | 1216528.8134
1 | 2724401.7764 | 1216514.7236 | 2724401.4742 | 1216528.8134
2 | 2724401.7764 | 1216514.7236 | 2724400.9218 | 1216512.4156
3 | 2724401.7764 | 1216514.7236 | 2724383.4845 | 1216514.5306 | 2724380.9747 | 1216516.5132 | 2724379.6243 | 1216519.3539 | 2724378.2649 | 1216532.0799
4 | 2724379.8677 | 1216575.703 | 2724376.1235 | 1216575.7026 | 2724377.2087 | 1216553.5964
5 | 2724379.8677 | 1216575.703 | 2724396.4852 | 1216576.6139
6 | 2724362.3517 | 1216621.6512 | 2724364.1245 | 1216616.4063 | 2724375.7658 | 1216581.9222 | 2724379.8677 | 1216575.703
7 | 2724378.2649 | 1216532.0799 | 2724377.2087 | 1216553.5964
8 | 2724396.4852 | 1216576.6139 | 2724400.3268 | 1216576.8244
9 | 2724362.3517 | 1216621.6512 | 2724364.1245 | 1216616.4063 | 2724380.083 | 1216619.2193
10 | 2724362.3517 | 1216621.6512 | 2724353.0834 | 1216619.3148
11 | 2724350.0856 | 1216655.5106 | 2724353.9261 | 1216645.4384 | 2724354.3381 | 1216644.2572 | 2724358.8255 | 1216633.3979 | 2724362.3517 | 1216621.6512
12 | 2724398.2061 | 1216498.2645 | 2724398.1746 | 1216504.9964 | 2724400.9218 | 1216512.4156
13 | 2724378.2649 | 1216532.0799 | 2724375.6224 | 1216531.6911 | 2724373.3381 | 1216531.61
14 | 2724411.9536 | 1216577.4618 | 2724400.3268 | 1216576.8244
15 | 2724380.083 | 1216619.2193 | 2724381.2106 | 1216619.4096 | 2724389.0816 | 1216620.9693
16 | 2724380.083 | 1216619.2193 | 2724379.1724 | 1216626.8173 | 2724376.9501 | 1216636.6021
17 | 2724332.8857 | 1216614.2234 | 2724353.0834 | 1216619.3148
18 | 2724350.0856 | 1216655.5106 | 2724346.2654 | 1216665.5466
19 | 2724350.0856 | 1216655.5106 | 2724336.7531 | 1216651.6573
20 | 2724398.0846 | 1216622.7533 | 2724389.0816 | 1216620.9693
21 | 2724376.3873 | 1216639.0799 | 2724376.9501 | 1216636.6021
22 | 2724398.2523 | 1216488.3818 | 2724398.2061 | 1216498.2645
23 | 2724373.3381 | 1216531.61 | 2724373.6561 | 1216524.7446
24 | 2724352.8633 | 1216530.8378 | 2724373.3381 | 1216531.61
25 | 2724419.4408 | 1216576.5851 | 2724416.903 | 1216577.7331 | 2724411.9536 | 1216577.4618
26 | 2724323.6224 | 1216610.9237 | 2724329.1175 | 1216613.2735 | 2724332.8857 | 1216614.2234
27 | 2724335.7363 | 1216686.7342 | 2724344.6054 | 1216669.9075 | 2724346.2654 | 1216665.5466
28 | 2724334.2022 | 1216650.9201 | 2724336.7531 | 1216651.6573
29 | 2724398.0846 | 1216622.7533 | 2724397.2192 | 1216629.4385
30 | 2724376.3873 | 1216639.0799 | 2724374.3638 | 1216647.9668 | 2724373.1371 | 1216653.6123
31 | 2724396.7337 | 1216424.1599 | 2724396.6911 | 1216424.0244 | 2724396.0774 | 1216422.8656
32 | 2724396.7337 | 1216424.1599 | 2724398.3005 | 1216429.1509 | 2724398.5012 | 1216433.7253 | 2724398.4158 | 1216452.7079
33 | 2724398.4029 | 1216455.5787 | 2724398.4158 | 1216452.7079
34 | 2724398.3345 | 1216470.7953 | 2724398.4029 | 1216455.5787
35 | 2724398.3345 | 1216470.7953 | 2724408.8358 | 1216470.9145
36 | 2724398.3345 | 1216470.7953 | 2724398.3055 | 1216477.0011
37 | 2724464.1644 | 1216420.4079 | 2724458.342 | 1216415.1823 | 2724450.6574 | 1216408.928 | 2724447.3511 | 1216406.8685
38 | 2724447.3511 | 1216406.8685 | 2724447.1429 | 1216419.7694
39 | 2724464.1644 | 1216420.4079 | 2724464.0009 | 1216434.3488
40 | 2724464.1644 | 1216420.4079 | 2724480.5545 | 1216436.0291
41 | 2724447.0679 | 1216424.4207 | 2724447.1429 | 1216419.7694
42 | 2724398.2523 | 1216488.3818 | 2724398.3055 | 1216477.0011
43 | 2724352.8633 | 1216530.8378 | 2724352.5463 | 1216538.3815
44 | 2724352.8633 | 1216530.8378 | 2724339.9849 | 1216530.3576 | 2724332.0989 | 1216530.8491
45 | 2724332.3555 | 1216523.6488 | 2724332.0989 | 1216530.8491
46 | 2724297.342 | 1216569.5655 | 2724289.4411 | 1216569.3117 | 2724266.4821 | 1216563.8509 | 2724262.506 | 1216562.9562 | 2724260.0383 | 1216561.4703 | 2724257.8762 | 1216559.1678 | 2724256.5838 | 1216556.6834 | 2724254.6293 | 1216531.6898 | 2724262.3085 | 1216531.6499 | 2724281.3829 | 1216536.9295 | 2724284.2963 | 1216537.435 | 2724286.4217 | 1216537.4905 | 2724290.6694 | 1216537.0232 | 2724332.0989 | 1216530.8491
47 | 2724338.1272 | 1216579.9313 | 2724320.668 | 1216575.457
48 | 2724342.2544 | 1216580.989 | 2724338.1272 | 1216579.9313
49 | 2724313.7498 | 1216573.6841 | 2724320.668 | 1216575.457
50 | 2724297.342 | 1216569.5655 | 2724308.6678 | 1216572.3817 | 2724313.7498 | 1216573.6841
51 | 2724464.0009 | 1216434.3488 | 2724463.7908 | 1216452.2547
52 | 2724480.5545 | 1216436.0291 | 2724488.0754 | 1216443.2029 | 2724490.1527 | 1216445.4284
53 | 2724419.4408 | 1216576.5851 | 2724419.8376 | 1216556.8669 | 2724432.4657 | 1216556.9639 | 2724432.5145 | 1216554.6298 | 2724432.5484 | 1216550.4606
54 | 2724432.5484 | 1216550.4606 | 2724432.5484 | 1216550.4606 | 2724442.867 | 1216550.591
55 | 2724451.525 | 1216550.6994 | 2724448.797 | 1216550.6666 | 2724447.362 | 1216550.6478 | 2724442.867 | 1216550.591
56 | 2724463.8309 | 1216550.8474 | 2724452.1397 | 1216550.7068
57 | 2724463.8309 | 1216550.8474 | 2724462.665 | 1216547.765 | 2724462.916 | 1216526.5666
58 | 2724452.1397 | 1216550.7068 | 2724451.525 | 1216550.6994
59 | 2724462.916 | 1216526.5666 | 2724463.049 | 1216515.3375
60 | 2724522.9899 | 1216542.71 | 2724532.7466 | 1216540.6566 | 2724538.8363 | 1216534.9127 | 2724545.7585 | 1216527.8518 | 2724557.753 | 1216513.9472
61 | 2724522.9899 | 1216542.71 | 2724531.8553 | 1216547.688 | 2724546.5233 | 1216549.7516 | 2724551.8468 | 1216550.8637 | 2724566.8104 | 1216554.0456 | 2724600.2263 | 1216559.5483 | 2724609.4295 | 1216562.8989 | 2724632.1835 | 1216569.0684 | 2724637.4332 | 1216570.8017 | 2724641.9812 | 1216573.043 | 2724649.0601 | 1216575.1927 | 2724657.7349 | 1216576.9311
62 | 2724522.9899 | 1216542.71 | 2724523.4366 | 1216536.6034 | 2724523.2218 | 1216525.0788 | 2724522.6715 | 1216518.3865
63 | 2724557.753 | 1216513.9472 | 2724557.2708 | 1216507.5877 | 2724557.2165 | 1216498.9242 | 2724558.1453 | 1216489.0217
64 | 2724557.753 | 1216513.9472 | 2724575.8858 | 1216493.0653 | 2724577.8354 | 1216489.9036 | 2724581.2517 | 1216482.3469 | 2724588.2268 | 1216462.5994
65 | 2724657.7349 | 1216576.9311 | 2724657.8642 | 1216593.6135 | 2724659.6795 | 1216607.3956
66 | 2724657.7349 | 1216576.9311 | 2724658.2142 | 1216568.5456
67 | 2724657.7349 | 1216576.9311 | 2724675.4795 | 1216579.6821 | 2724678.5201 | 1216581.0023 | 2724689.7444 | 1216587.2087 | 2724697.8781 | 1216590.8483 | 2724715.5655 | 1216595.9668 | 2724720.5467 | 1216597.8281 | 2724741.8985 | 1216611.4634 | 2724746.5728 | 1216613.4739 | 2724753.1095 | 1216615.0341
68 | 2724520.7813 | 1216504.1337 | 2724522.259 | 1216513.3717 | 2724522.6715 | 1216518.3865
69 | 2724463.2311 | 1216499.9617 | 2724463.049 | 1216515.3375
70 | 2724588.2268 | 1216462.5994 | 2724582.6227 | 1216432.4143
71 | 2724588.2268 | 1216462.5994 | 2724591.5112 | 1216452.2711 | 2724593.4681 | 1216435.3321 | 2724593.671 | 1216427.8083 | 2724592.8527 | 1216421.9088 | 2724589.3931 | 1216411.9286 | 2724588.803 | 1216405.6447 | 2724588.4315 | 1216396.8779
72 | 2724753.1095 | 1216615.0341 | 2724760.0226 | 1216616.0352 | 2724765.1704 | 1216617.1883 | 2724768.0266 | 1216618.2489 | 2724773.311 | 1216621.5305
73 | 2724502.8749 | 1216624.6427 | 2724503.9473 | 1216637.2861 | 2724505.6757 | 1216645.4286 | 2724505.8736 | 1216646.1623
74 | 2724502.8749 | 1216624.6427 | 2724498.198 | 1216624.2114 | 2724495.0661 | 1216624.713 | 2724492.5205 | 1216626.2277 | 2724490.7665 | 1216628.3927 | 2724479.8841 | 1216644.2892
75 | 2724514.0052 | 1216668.7653 | 2724511.3018 | 1216663.3045 | 2724508.6219 | 1216656.3542 | 2724505.8736 | 1216646.1623
76 | 2724477.8954 | 1216647.1942 | 2724479.8841 | 1216644.2892
77 | 2724520.7813 | 1216504.1337 | 2724526.395 | 1216503.7173
78 | 2724520.7813 | 1216504.1337 | 2724518.5023 | 1216495.079 | 2724516.2513 | 1216487.9472
79 | 2724403.5883 | 1216689.0422 | 2724403.4135 | 1216693.7756 | 2724406.9198 | 1216698.6192 | 2724410.7325 | 1216700.7894 | 2724415.3089 | 1216706.6421
80 | 2724420.2439 | 1216727.1863 | 2724421.4651 | 1216728.713 | 2724428.3669 | 1216723.3418 | 2724415.3089 | 1216706.6421
81 | 2724392.2117 | 1216691.2175 | 2724396.0357 | 1216689.9408 | 2724400.5957 | 1216689.0575 | 2724403.5883 | 1216689.0422
82 | 2724427.4295 | 1216691.1415 | 2724403.5883 | 1216689.0422
83 | 2724392.2117 | 1216691.2175 | 2724389.0831 | 1216692.6534 | 2724383.7943 | 1216696.0679 | 2724378.4214 | 1216700.1601
84 | 2724392.2117 | 1216691.2175 | 2724391.9741 | 1216682.5149
85 | 2724427.4295 | 1216691.1415 | 2724433.0826 | 1216694.6511
86 | 2724369.9107 | 1216706.642 | 2724378.4214 | 1216700.1601
87 | 2724396.6306 | 1216665.4563 | 2724391.9019 | 1216679.8689 | 2724391.9741 | 1216682.5149
88 | 2724448.2998 | 1216698.7609 | 2724433.0826 | 1216694.6511
89 | 2724369.9107 | 1216706.642 | 2724372.8878 | 1216712.0973 | 2724372.9502 | 1216714.5672
90 | 2724396.6306 | 1216665.4563 | 2724406.6276 | 1216666.4109
91 | 2724448.2998 | 1216698.7609 | 2724446.6659 | 1216712.2596
92 | 2724448.2998 | 1216698.7609 | 2724450.77 | 1216696.4885 | 2724452.1281 | 1216685.2859 | 2724448.4621 | 1216681.1839 | 2724455.1958 | 1216675.8648 | 2724458.4534 | 1216672.2522 | 2724463.2323 | 1216666.3474
93 | 2724463.2323 | 1216666.3474 | 2724470.7362 | 1216673.5986
94 | 2724473.3675 | 1216653.8048 | 2724463.2323 | 1216666.3474
95 | 2724473.3675 | 1216653.8048 | 2724477.8954 | 1216647.1942
96 | 2724473.3675 | 1216653.8048 | 2724464.2631 | 1216652.6168
97 | 2724414.8524 | 1216667.1962 | 2724406.6276 | 1216666.4109
98 | 2724452.0817 | 1216651.0274 | 2724447.6591 | 1216650.4504
99 | 2724464.2631 | 1216652.6168 | 2724452.0817 | 1216651.0274
100 | 2724447.6591 | 1216650.4504 | 2724435.7812 | 1216648.9005
101 | 2724435.1164 | 1216648.8138 | 2724435.7812 | 1216648.9005
102 | 2724435.1164 | 1216648.8138 | 2724424.356 | 1216647.4098 | 2724418.9488 | 1216646.0147
103 | 2724477.8954 | 1216647.1942 | 2724484.6904 | 1216660.1365
104 | 2724398.338 | 1216640.4869 | 2724399.5941 | 1216641.0213 | 2724418.9488 | 1216646.0147
105 | 2724373.1371 | 1216653.6123 | 2724379.552 | 1216654.8249
106 | 2724373.1371 | 1216653.6123 | 2724372.2724 | 1216657.5739
107 | 2724398.338 | 1216640.4869 | 2724397.7799 | 1216640.2495 | 2724396.8217 | 1216639.2175 | 2724396.2375 | 1216637.7375 | 2724396.4092 | 1216635.6951 | 2724397.2192 | 1216629.4385
108 | 2724514.0052 | 1216668.7653 | 2724494.4593 | 1216678.8093 | 2724493.3356 | 1216684.2456
109 | 2724514.0052 | 1216668.7653 | 2724515.7248 | 1216672.2484 | 2724521.7616 | 1216683.917 | 2724525.502 | 1216689.5439 | 2724532.6724 | 1216698.2117 | 2724538.8098 | 1216701.7982 | 2724542.9136 | 1216703.1184 | 2724547.5734 | 1216703.6384
110 | 2724555.3711 | 1216704.8245 | 2724547.5734 | 1216703.6384
111 | 2724547.5734 | 1216703.6384 | 2724550.12 | 1216703.5248 | 2724554.3591 | 1216702.735 | 2724557.5785 | 1216700.9565 | 2724560.2784 | 1216697.866 | 2724562.2479 | 1216693.0256 | 2724563.0585 | 1216688.4056 | 2724563.0585 | 1216688.4056
112 | 2724511.5254 | 1216760.4964 | 2724520.1357 | 1216756.2285 | 2724522.5683 | 1216750.308 | 2724529.7073 | 1216728.5067 | 2724532.6724 | 1216698.2117 | 2724538.8098 | 1216701.7982 | 2724542.9136 | 1216703.1184 | 2724547.5734 | 1216703.6384
113 | 2724438.9647 | 1216750.1564 | 2724447.8216 | 1216741.2731 | 2724440.7853 | 1216736.2664
114 | 2724409.5437 | 1216791.1463 | 2724420.3227 | 1216768.8539 | 2724438.9647 | 1216750.1564
115 | 2724409.5437 | 1216791.1463 | 2724437.6639 | 1216802.52 | 2724447.9894 | 1216780.1292 | 2724451.2974 | 1216776.2842 | 2724455.1009 | 1216773.4391 | 2724466.715 | 1216767.1656 | 2724479.4966 | 1216760.2605 | 2724482.3912 | 1216759.1201
116 | 2724482.3912 | 1216759.1201 | 2724482.2182 | 1216748.864
117 | 2724482.3912 | 1216759.1201 | 2724484.2325 | 1216758.5914 | 2724489.3211 | 1216757.8527 | 2724501.895 | 1216757.6151 | 2724502.9227 | 1216757.9226
118 | 2724511.5254 | 1216760.4964 | 2724502.9227 | 1216757.9226
119 | 2724321.5757 | 1216714.0616 | 2724325.9252 | 1216717.0769
120 | 2724321.5757 | 1216714.0616 | 2724323.2306 | 1216710.46
121 | 2724323.2306 | 1216710.46 | 2724335.7363 | 1216686.7342
122 | 2724557.2814 | 1216736.2223 | 2724544.0482 | 1216767.7944
123 | 2724544.0482 | 1216767.7944 | 2724609.0066 | 1216801.2655
124 | 2724557.2814 | 1216736.2223 | 2724552.1455 | 1216734.5025 | 2724550.5725 | 1216734.1805 | 2724549.3103 | 1216734.2542 | 2724547.681 | 1216734.8094 | 2724545.9041 | 1216736.2512 | 2724545.0773 | 1216737.6573 | 2724544.6635 | 1216739.6502 | 2724544.3614 | 1216741.7455 | 2724543.2061 | 1216743.2448
125 | 2724627.4101 | 1216762.6979 | 2724618.4126 | 1216783.6484 | 2724609.0066 | 1216801.2655
126 | 2724323.6224 | 1216610.9237 | 2724321.3334 | 1216609.946
127 | 2724323.6224 | 1216610.9237 | 2724320.9512 | 1216617.7916
128 | 2724297.6138 | 1216605.6661 | 2724309.8237 | 1216606.5102 | 2724314.7548 | 1216607.1358 | 2724321.3334 | 1216609.946
129 | 2724320.9512 | 1216617.7916 | 2724316.6723 | 1216628.7927 | 2724311.8756 | 1216627.2497
130 | 2724297.6138 | 1216605.6661 | 2724292.6767 | 1216605.3295
131 | 2724292.6767 | 1216605.3295 | 2724291.4658 | 1216622.4698
132 | 2724555.3711 | 1216704.8245 | 2724555.0866 | 1216714.0702
133 | 2724555.3711 | 1216704.8245 | 2724584.4419 | 1216709.2466
134 | 2724563.0585 | 1216688.4056 | 2724563.0326 | 1216684.5576 | 2724562.7275 | 1216682.9416
135 | 2724584.4419 | 1216709.2466 | 2724585.7625 | 1216717.6363 | 2724585.9103 | 1216721.4646
136 | 2724551.4195 | 1216663.7313 | 2724560.3861 | 1216675.6509 | 2724562.1917 | 1216680.1032 | 2724562.7275 | 1216682.9416
137 | 2724550.156 | 1216662.0517 | 2724551.4195 | 1216663.7313
138 | 2724550.156 | 1216662.0517 | 2724548.216 | 1216659.4728 | 2724545.9767 | 1216655.7171
139 | 2724538.5572 | 1216632.8835 | 2724539.233 | 1216637.6124 | 2724540.7769 | 1216643.6828 | 2724542.3517 | 1216648.2748 | 2724544.5034 | 1216653.2459 | 2724545.9767 | 1216655.7171
140 | 2724585.9103 | 1216721.4646 | 2724627.4101 | 1216762.6979
141 | 2724538.5572 | 1216632.8835 | 2724549.2225 | 1216630.5935
142 | 2724538.5572 | 1216632.8835 | 2724538.127 | 1216629.8499 | 2724537.9663 | 1216627.3668 | 2724538.1539 | 1216621.671
143 | 2724514.335 | 1216482.9825 | 2724515.8454 | 1216486.6613 | 2724516.2513 | 1216487.9472
144 | 2724514.335 | 1216482.9825 | 2724520.5339 | 1216481.4552
145 | 2724514.335 | 1216482.9825 | 2724512.0076 | 1216477.3294 | 2724508.7151 | 1216470.6109 | 2724507.4287 | 1216468.5714
146 | 2724533.7409 | 1216513.445 | 2724526.395 | 1216503.7173
147 | 2724526.395 | 1216503.7173 | 2724529.7445 | 1216502.9867 | 2724532.1537 | 1216501.0911 | 2724533.6439 | 1216498.1088 | 2724538.5697 | 1216469.9341 | 2724538.5149 | 1216465.6518 | 2724538.1377 | 1216461.1738 | 2724537.6426 | 1216458.9014
148 | 2724507.4287 | 1216468.5714 | 2724516.3684 | 1216466.3675
149 | 2724507.4287 | 1216468.5714 | 2724504.2684 | 1216463.5236 | 2724501.4028 | 1216459.2716
150 | 2724534.4164 | 1216444.0938 | 2724537.6426 | 1216458.9014
151 | 2724501.4028 | 1216459.2716 | 2724507.3346 | 1216451.6339 | 2724512.2177 | 1216450.5684
152 | 2724501.4028 | 1216459.2716 | 2724499.4137 | 1216456.3277 | 2724494.3526 | 1216449.9281 | 2724490.1527 | 1216445.4284
153 | 2724534.4164 | 1216444.0938 | 2724537.2588 | 1216437.8261 | 2724536.6531 | 1216421.4288
154 | 2724463.2311 | 1216499.9617 | 2724475.0365 | 1216499.4523
155 | 2724463.2311 | 1216499.9617 | 2724463.4702 | 1216479.583
156 | 2724463.7908 | 1216452.2547 | 2724463.4702 | 1216479.583

## bus_geodata
| x | y | coords
0 | 2724401.291 | 1216537.3552
1 | 2724401.4742 | 1216528.8134
2 | 2724401.7764 | 1216514.7236
3 | 2724379.8677 | 1216575.703
4 | 2724377.2087 | 1216553.5964
5 | 2724396.4852 | 1216576.6139
6 | 2724362.3517 | 1216621.6512
7 | 2724400.9218 | 1216512.4156
8 | 2724378.2649 | 1216532.0799
9 | 2724400.3268 | 1216576.8244
10 | 2724380.083 | 1216619.2193
11 | 2724353.0834 | 1216619.3148
12 | 2724350.0856 | 1216655.5106
13 | 2724389.0816 | 1216620.9693
14 | 2724376.9501 | 1216636.6021
15 | 2724398.2061 | 1216498.2645
16 | 2724373.3381 | 1216531.61
17 | 2724411.9536 | 1216577.4618
18 | 2724332.8857 | 1216614.2234
19 | 2724346.2654 | 1216665.5466
20 | 2724336.7531 | 1216651.6573
21 | 2724398.0846 | 1216622.7533
22 | 2724376.3873 | 1216639.0799
23 | 2724396.7337 | 1216424.1599
24 | 2724396.0774 | 1216422.8656
25 | 2724398.4158 | 1216452.7079
26 | 2724398.4029 | 1216455.5787
27 | 2724398.3345 | 1216470.7953
28 | 2724447.3511 | 1216406.8685
29 | 2724464.1644 | 1216420.4079
30 | 2724447.1429 | 1216419.7694
31 | 2724408.8358 | 1216470.9145
32 | 2724398.3055 | 1216477.0012
33 | 2724398.2523 | 1216488.3818
34 | 2724373.6561 | 1216524.7446
35 | 2724352.8633 | 1216530.8378
36 | 2724352.5463 | 1216538.3815
37 | 2724332.0989 | 1216530.8491
38 | 2724338.1272 | 1216579.9313
39 | 2724320.668 | 1216575.457
40 | 2724342.2544 | 1216580.989
41 | 2724313.7498 | 1216573.6841
42 | 2724297.342 | 1216569.5655
43 | 2724332.3555 | 1216523.6488
44 | 2724464.0009 | 1216434.3488
45 | 2724480.5545 | 1216436.0291
46 | 2724447.0679 | 1216424.4207
47 | 2724419.4408 | 1216576.5851
48 | 2724432.5484 | 1216550.4606
49 | 2724442.867 | 1216550.591
50 | 2724463.8309 | 1216550.8474
51 | 2724452.1397 | 1216550.7068
52 | 2724462.916 | 1216526.5666
53 | 2724522.9899 | 1216542.71
54 | 2724557.753 | 1216513.9472
55 | 2724657.7349 | 1216576.9311
56 | 2724522.6715 | 1216518.3865
57 | 2724451.525 | 1216550.6994
58 | 2724463.049 | 1216515.3375
59 | 2724558.1453 | 1216489.0217
60 | 2724588.2268 | 1216462.5994
61 | 2724659.6795 | 1216607.3956
62 | 2724658.2142 | 1216568.5456
63 | 2724753.1095 | 1216615.0341
64 | 2724502.8749 | 1216624.6427
65 | 2724505.8736 | 1216646.1623
66 | 2724479.8841 | 1216644.2892
67 | 2724520.7813 | 1216504.1337
68 | 2724415.3089 | 1216706.6421
69 | 2724403.5883 | 1216689.0422
70 | 2724420.2439 | 1216727.1863
71 | 2724392.2117 | 1216691.2175
72 | 2724427.4295 | 1216691.1415
73 | 2724378.4214 | 1216700.1601
74 | 2724391.9741 | 1216682.5149
75 | 2724433.0826 | 1216694.6511
76 | 2724369.9107 | 1216706.642
77 | 2724396.6306 | 1216665.4563
78 | 2724448.2998 | 1216698.7609
79 | 2724446.6659 | 1216712.2596
80 | 2724463.2323 | 1216666.3474
81 | 2724470.7362 | 1216673.5986
82 | 2724473.3675 | 1216653.8048
83 | 2724406.6276 | 1216666.4109
84 | 2724414.8524 | 1216667.1962
85 | 2724372.9502 | 1216714.5672
86 | 2724452.0817 | 1216651.0274
87 | 2724447.6591 | 1216650.4504
88 | 2724464.2631 | 1216652.6168
89 | 2724435.7812 | 1216648.9005
90 | 2724435.1164 | 1216648.8138
91 | 2724477.8954 | 1216647.1942
92 | 2724418.9488 | 1216646.0147
93 | 2724484.6904 | 1216660.1365
94 | 2724373.1371 | 1216653.6123
95 | 2724379.552 | 1216654.8249
96 | 2724372.2724 | 1216657.5739
97 | 2724397.2192 | 1216629.4385
98 | 2724398.338 | 1216640.4869
99 | 2724514.0052 | 1216668.7653
100 | 2724493.3356 | 1216684.2456
101 | 2724547.5734 | 1216703.6384
102 | 2724438.9647 | 1216750.1564
103 | 2724440.7853 | 1216736.2664
104 | 2724409.5437 | 1216791.1463
105 | 2724482.3912 | 1216759.1201
106 | 2724482.2182 | 1216748.864
107 | 2724502.9227 | 1216757.9226
108 | 2724321.5757 | 1216714.0616
109 | 2724325.9252 | 1216717.0769
110 | 2724323.2306 | 1216710.46
111 | 2724511.5254 | 1216760.4964
112 | 2724544.0482 | 1216767.7944
113 | 2724557.2814 | 1216736.2223
114 | 2724609.0066 | 1216801.2655
115 | 2724323.6224 | 1216610.9237
116 | 2724321.3334 | 1216609.946
117 | 2724320.9512 | 1216617.7916
118 | 2724297.6138 | 1216605.6661
119 | 2724311.8756 | 1216627.2497
120 | 2724292.6767 | 1216605.3295
121 | 2724555.3711 | 1216704.8245
122 | 2724563.0585 | 1216688.4056
123 | 2724555.0866 | 1216714.0702
124 | 2724584.4419 | 1216709.2466
125 | 2724562.7275 | 1216682.9416
126 | 2724551.4195 | 1216663.7313
127 | 2724550.156 | 1216662.0517
128 | 2724545.9767 | 1216655.7171
129 | 2724585.9103 | 1216721.4646
130 | 2724291.4658 | 1216622.4698
131 | 2724335.7363 | 1216686.7342
132 | 2724538.5572 | 1216632.8835
133 | 2724549.2225 | 1216630.5935
134 | 2724538.1539 | 1216621.671
135 | 2724334.2022 | 1216650.9201
136 | 2724516.2513 | 1216487.9472
137 | 2724514.335 | 1216482.9825
138 | 2724526.395 | 1216503.7173
139 | 2724520.5339 | 1216481.4552
140 | 2724507.4287 | 1216468.5714
141 | 2724533.7409 | 1216513.445
142 | 2724537.6426 | 1216458.9014
143 | 2724516.3684 | 1216466.3675
144 | 2724501.4028 | 1216459.2716
145 | 2724534.4164 | 1216444.0938
146 | 2724512.2177 | 1216450.5684
147 | 2724490.1527 | 1216445.4284
148 | 2724588.4315 | 1216396.8779
149 | 2724582.6227 | 1216432.4143
150 | 2724463.2311 | 1216499.9617
151 | 2724475.0365 | 1216499.4523
152 | 2724463.4702 | 1216479.583
153 | 2724463.7908 | 1216452.2547
154 | 2724773.311 | 1216621.5305
155 | 2724536.6531 | 1216421.4288
156 | 2724543.2061 | 1216743.2448
157 | 2724627.4101 | 1216762.6979
158 | 2724473.3675 | 1216653.8048

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97862 | -0.41166 | 0.030205 | 0.0075701
1 | 0.97886 | -0.40696 | 0.0053902 | 0.0013509
2 | 0.97933 | -0.39784 | 0 | 0
3 | 0.98534 | -0.28061 | 0 | 0
4 | 0.98296 | -0.32693 | 0.01114 | 0.0027918
5 | 0.9844 | -0.29881 | 0.0053448 | 0.0013395
6 | 0.98901 | -0.20981 | 0 | 0
7 | 0.97929 | -0.39866 | 0.0003046 | 7.6341e-05
8 | 0.98119 | -0.36131 | 0 | 0
9 | 0.9842 | -0.30265 | 0.0043024 | 0.0010783
10 | 0.99121 | -0.16747 | 0 | 0
11 | 0.98872 | -0.21541 | 0.0027501 | 0.00068923
12 | 0.98815 | -0.22641 | 0 | 0
13 | 0.99221 | -0.14817 | 0.0062614 | 0.0015693
14 | 0.99091 | -0.17328 | 0.0056313 | 0.0014113
15 | 0.97904 | -0.40345 | 0.010398 | 0.0026059
16 | 0.98104 | -0.36439 | 0 | 0
17 | 0.98365 | -0.31338 | 0.0038281 | 0.00095942
18 | 0.98814 | -0.22662 | 0.003213 | 0.00080525
19 | 0.98798 | -0.22964 | 0.0040389 | 0.0010122
20 | 0.98804 | -0.22863 | 0.0043325 | 0.0010858
21 | 0.99325 | -0.12838 | 0 | 0
22 | 0.99088 | -0.17386 | 0 | 0
23 | 0.97874 | -0.40943 | 0.0013396 | 0.00033574
24 | 0.97874 | -0.40945 | 0.00077983 | 0.00019544
25 | 0.97879 | -0.40832 | 0.0016099 | 0.00040347
26 | 0.9788 | -0.40812 | 0.0011319 | 0.00028368
27 | 0.97887 | -0.40678 | 0 | 0
28 | 0.97722 | -0.43914 | 0 | 0
29 | 0.97724 | -0.4386 | 0 | 0
30 | 0.9772 | -0.43946 | 0.00076313 | 0.00019126
31 | 0.97887 | -0.40688 | 0.00055988 | 0.00014032
32 | 0.9789 | -0.40616 | 0.0011148 | 0.00027939
33 | 0.97897 | -0.40481 | 0.0010445 | 0.00026179
34 | 0.981 | -0.36517 | 0.0062181 | 0.0015584
35 | 0.9805 | -0.37484 | 0 | 0
36 | 0.98045 | -0.37588 | 0.0076048 | 0.0019059
37 | 0.98011 | -0.38259 | 0 | 0
38 | 0.97736 | -0.43653 | 0.0039589 | 0.00099219
39 | 0.97749 | -0.43394 | 0.0046487 | 0.0011651
40 | 0.97734 | -0.43684 | 0.0039338 | 0.0009859
41 | 0.97757 | -0.43231 | 0.0040059 | 0.001004
42 | 0.97783 | -0.4272 | 0 | 0
43 | 0.98008 | -0.38312 | 0.0040626 | 0.0010182
44 | 0.97753 | -0.43297 | 0.00083724 | 0.00020983
45 | 0.97681 | -0.44718 | 0 | 0
46 | 0.9772 | -0.43952 | 0.0006066 | 0.00015203
47 | 0.98331 | -0.31999 | 0 | 0
48 | 0.9816 | -0.35324 | 0.004788 | 0.0012
49 | 0.9812 | -0.36119 | 0.0048583 | 0.0012176
50 | 0.98052 | -0.37442 | 0 | 0
51 | 0.98087 | -0.36752 | 0.0045891 | 0.0011501
52 | 0.97978 | -0.3889 | 0.0005997 | 0.0001503
53 | 0.97499 | -0.48304 | 0 | 0
54 | 0.97489 | -0.48504 | 0 | 0
55 | 0.97385 | -0.50555 | 0 | 0
56 | 0.97524 | -0.47808 | 0.0022651 | 0.00056769
57 | 0.98089 | -0.36711 | 0.00056766 | 0.00014227
58 | 0.97945 | -0.39542 | 0.0035705 | 0.00089486
59 | 0.97488 | -0.48524 | 0.00044461 | 0.00011143
60 | 0.97478 | -0.48714 | 0 | 0
61 | 0.97375 | -0.50744 | 0.0033572 | 0.00084139
62 | 0.97383 | -0.50592 | 0.0024013 | 0.00060182
63 | 0.97356 | -0.51128 | 0 | 0
64 | 0.99053 | -0.17996 | 0 | 0
65 | 0.98777 | -0.23281 | 0.0052139 | 0.0013067
66 | 0.99469 | -0.1007 | 0.0071775 | 0.0017989
67 | 0.97542 | -0.47456 | 0 | 0
68 | 0.98824 | -0.22566 | 0.0086088 | 0.0021576
69 | 0.9886 | -0.21851 | 0 | 0
70 | 0.98797 | -0.23089 | 0.0091842 | 0.0023018
71 | 0.98821 | -0.22611 | 0 | 0
72 | 0.98979 | -0.19538 | 0 | 0
73 | 0.98796 | -0.23108 | 0.0056614 | 0.0014189
74 | 0.98805 | -0.22918 | 0.0053405 | 0.0013385
75 | 0.99013 | -0.18894 | 0.0057759 | 0.0014476
76 | 0.98785 | -0.23322 | 0 | 0
77 | 0.98782 | -0.23375 | 0 | 0
78 | 0.991 | -0.17209 | 0 | 0
79 | 0.99069 | -0.17798 | 0.024376 | 0.0061091
80 | 0.99419 | -0.11048 | 0 | 0
81 | 0.99414 | -0.11139 | 0.0049479 | 0.0012401
82 | 0.99551 | -0.085085 | 0 | 0
83 | 0.98769 | -0.23634 | 0.0080574 | 0.0020194
84 | 0.98764 | -0.23727 | 0.0063318 | 0.0015869
85 | 0.98776 | -0.23496 | 0.01122 | 0.002812
86 | 0.99799 | -0.038045 | 0.0076039 | 0.0019057
87 | 0.99852 | -0.027952 | 0.0086208 | 0.0021606
88 | 0.99657 | -0.065079 | 0.0030994 | 0.00077679
89 | 1 | 0 | -0.5494 | -0.14037
90 | 0.99992 | -0.001592 | 0.0086453 | 0.0021667
91 | 0.99493 | -0.096254 | 0 | 0
92 | 0.99791 | -0.03946 | 0.0074974 | 0.001879
93 | 0.99472 | -0.10014 | 0.015093 | 0.0037827
94 | 0.9907 | -0.17726 | 0 | 0
95 | 0.99067 | -0.17778 | 0.0044403 | 0.0011129
96 | 0.99067 | -0.17787 | 0.0084358 | 0.0021142
97 | 0.994 | -0.11387 | 0.0065911 | 0.0016519
98 | 0.99539 | -0.087479 | 0.0058794 | 0.0014735
99 | 0.98484 | -0.28939 | 0 | 0
100 | 0.98454 | -0.29519 | 0.011728 | 0.0029393
101 | 0.97916 | -0.39967 | 0 | 0
102 | 0.97179 | -0.54452 | 0.0078696 | 0.0019723
103 | 0.97153 | -0.54979 | 0.013469 | 0.0033758
104 | 0.97281 | -0.52439 | 0 | 0
105 | 0.97472 | -0.48687 | 0 | 0
106 | 0.97459 | -0.48944 | 0.013653 | 0.0034218
107 | 0.97539 | -0.47358 | 0.0078652 | 0.0019712
108 | 0.98743 | -0.24047 | 0 | 0
109 | 0.98738 | -0.2414 | 0.0098288 | 0.0024633
110 | 0.98746 | -0.23978 | 0 | 0
111 | 0.97575 | -0.46653 | 0 | 0
112 | 0.97592 | -0.46337 | 0.0016905 | 0.00042369
113 | 0.97576 | -0.46665 | 0 | 0
114 | 0.97639 | -0.45411 | 0 | 0
115 | 0.9879 | -0.23137 | 0 | 0
116 | 0.98786 | -0.23202 | 0.0062975 | 0.0015783
117 | 0.98781 | -0.23298 | 0.0031716 | 0.00079488
118 | 0.98767 | -0.23568 | 0 | 0
119 | 0.98767 | -0.2357 | 0.0090588 | 0.0022704
120 | 0.98764 | -0.23643 | 0 | 0
121 | 0.97894 | -0.40414 | 0 | 0
122 | 0.97813 | -0.41987 | 0.006174 | 0.0015474
123 | 0.9789 | -0.40494 | 0.0047386 | 0.0011876
124 | 0.97822 | -0.41829 | 0 | 0
125 | 0.97794 | -0.42378 | 0.0062794 | 0.0015738
126 | 0.97725 | -0.43728 | 0.010674 | 0.0026752
127 | 0.97721 | -0.43813 | 0.002334 | 0.00058495
128 | 0.97707 | -0.44086 | 0.0095417 | 0.0023914
129 | 0.97791 | -0.42424 | 0.0036034 | 0.00090309
130 | 0.9875 | -0.23901 | 0.008417 | 0.0021095
131 | 0.98771 | -0.23507 | 0.002989 | 0.00074912
132 | 0.97684 | -0.44537 | 0 | 0
133 | 0.97679 | -0.44623 | 0.004326 | 0.0010842
134 | 0.97678 | -0.44657 | 0.0058648 | 0.0014699
135 | 0.98803 | -0.22885 | 0.0046352 | 0.0011617
136 | 0.97567 | -0.46951 | 0.0013499 | 0.00033831
137 | 0.97576 | -0.46777 | 0 | 0
138 | 0.9754 | -0.47487 | 0 | 0
139 | 0.97576 | -0.46784 | 0.00054243 | 0.00013595
140 | 0.97603 | -0.46242 | 0 | 0
141 | 0.97539 | -0.47504 | 0.00076673 | 0.00019216
142 | 0.9753 | -0.47692 | 0.00058816 | 0.00014741
143 | 0.97603 | -0.4625 | 0.00052259 | 0.00013097
144 | 0.97623 | -0.4586 | 0 | 0
145 | 0.97527 | -0.47739 | 0 | 0
146 | 0.97622 | -0.45874 | 0.0005221 | 0.00013085
147 | 0.97655 | -0.45228 | 0.001437 | 0.00036016
148 | 0.97475 | -0.48778 | 0.00052316 | 0.00013112
149 | 0.97474 | -0.4879 | 0.0013598 | 0.00034081
150 | 0.97904 | -0.40336 | 0 | 0
151 | 0.97903 | -0.40354 | 0.00085712 | 0.00021481
152 | 0.97852 | -0.41357 | 0.003669 | 0.00091954
153 | 0.97791 | -0.42546 | 0.00088152 | 0.00022093
154 | 0.9735 | -0.51247 | 0.0030041 | 0.0007529
155 | 0.97524 | -0.4781 | 0.0016741 | 0.00041957
156 | 0.97566 | -0.46856 | 0.0052327 | 0.0013114
157 | 0.97667 | -0.4487 | 0.015977 | 0.0040043
158 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.030205 | -0.0075701 | 0.030212 | 0.0075744 | 6.7581e-06 | 4.2178e-06 | 0.045928 | 0.045928 | 0.045928 | 0.97862 | -0.41166 | 0.97886 | -0.40696 | 12.6175
1 | -0.035602 | -0.0089253 | 0.035618 | 0.008935 | 1.548e-05 | 9.73e-06 | 0.054121 | 0.054121 | 0.054121 | 0.97886 | -0.40696 | 0.97933 | -0.39784 | 14.8685
2 | 0.018289 | 0.0045848 | -0.018288 | -0.0045844 | 7.1275e-07 | 4.2519e-07 | 0.027789 | 0.027789 | 0.027789 | 0.97933 | -0.39784 | 0.97929 | -0.39866 | 7.6344
3 | -0.053907 | -0.01352 | 0.054001 | 0.01358 | 9.4043e-05 | 5.9716e-05 | 0.081911 | 0.08191 | 0.081911 | 0.97933 | -0.39784 | 0.98119 | -0.36131 | 22.5029
4 | 0.10001 | 0.025276 | -0.099787 | -0.025135 | 0.00022157 | 0.00014147 | 0.1511 | 0.15111 | 0.15111 | 0.98534 | -0.28061 | 0.98296 | -0.32693 | 41.5124
5 | 0.061175 | 0.015456 | -0.061122 | -0.015422 | 5.3316e-05 | 3.391e-05 | 0.092428 | 0.092428 | 0.092428 | 0.98534 | -0.28061 | 0.9844 | -0.29881 | 25.3923
6 | -0.16118 | -0.040732 | 0.16173 | 0.041082 | 0.00054915 | 0.00035019 | 0.24353 | 0.24353 | 0.24353 | 0.98534 | -0.28061 | 0.98901 | -0.20981 | 33.4523
7 | 0.088648 | 0.022343 | -0.088502 | -0.02225 | 0.00014558 | 9.2899e-05 | 0.13424 | 0.13424 | 0.13424 | 0.98296 | -0.32693 | 0.98119 | -0.36131 | 36.8796
8 | 0.055777 | 0.014082 | -0.055766 | -0.014076 | 1.0265e-05 | 6.5206e-06 | 0.084349 | 0.084349 | 0.084349 | 0.9844 | -0.29881 | 0.9842 | -0.30265 | 23.1727
9 | -0.22053 | -0.055841 | 0.22098 | 0.056128 | 0.00044934 | 0.00028702 | 0.33201 | 0.33201 | 0.33201 | 0.98901 | -0.20981 | 0.99121 | -0.16747 | 45.6053
10 | 0.032944 | 0.0082694 | -0.032936 | -0.0082639 | 8.8079e-06 | 5.5144e-06 | 0.049571 | 0.049571 | 0.049571 | 0.98901 | -0.20981 | 0.98872 | -0.21541 | 13.6185
11 | 0.025855 | 0.00649 | -0.025834 | -0.0064774 | 2.0458e-05 | 1.2631e-05 | 0.038904 | 0.038904 | 0.038904 | 0.98901 | -0.20981 | 0.98815 | -0.22641 | 10.6878
12 | 0.017984 | 0.0045081 | -0.01798 | -0.0045056 | 4.1005e-06 | 2.4401e-06 | 0.027326 | 0.027326 | 0.027326 | 0.97929 | -0.39866 | 0.97904 | -0.40345 | 7.5073
13 | 0.034502 | 0.0086704 | -0.034497 | -0.0086672 | 5.0753e-06 | 3.1858e-06 | 0.052331 | 0.052331 | 0.052331 | 0.98119 | -0.36131 | 0.98104 | -0.36439 | 14.3768
14 | 0.051464 | 0.012997 | -0.051438 | -0.012981 | 2.646e-05 | 1.6787e-05 | 0.077844 | 0.077844 | 0.077844 | 0.9842 | -0.30265 | 0.98365 | -0.31338 | 21.3857
15 | -0.2395 | -0.060771 | 0.23972 | 0.060913 | 0.00022253 | 0.00014218 | 0.3598 | 0.3598 | 0.3598 | 0.99121 | -0.16747 | 0.99221 | -0.14817 | 49.4235
16 | 0.018515 | 0.0046429 | -0.01851 | -0.0046398 | 5.1245e-06 | 3.0518e-06 | 0.027796 | 0.027796 | 0.027796 | 0.99121 | -0.16747 | 0.99091 | -0.17328 | 7.6364
17 | 0.030186 | 0.0075746 | -0.030169 | -0.0075646 | 1.6123e-05 | 1.0052e-05 | 0.045433 | 0.045433 | 0.045433 | 0.98872 | -0.21541 | 0.98814 | -0.22662 | 12.4815
18 | 0.016866 | 0.0042295 | -0.016863 | -0.0042279 | 2.5976e-06 | 1.5249e-06 | 0.025398 | 0.025398 | 0.025398 | 0.98815 | -0.22641 | 0.98798 | -0.22964 | 6.9775
19 | 0.0089687 | 0.0022479 | -0.0089677 | -0.0022475 | 9.4928e-07 | 4.2978e-07 | 0.013506 | 0.013506 | 0.013506 | 0.98815 | -0.22641 | 0.98804 | -0.22863 | 3.7103
20 | -0.24598 | -0.062483 | 0.24622 | 0.062633 | 0.00023456 | 0.00014988 | 0.36919 | 0.36919 | 0.36919 | 0.99221 | -0.14817 | 0.99325 | -0.12838 | 50.7133
21 | 0.012879 | 0.0032285 | -0.012879 | -0.0032283 | 3.564e-07 | 1.9537e-07 | 0.01934 | 0.01934 | 0.01934 | 0.99091 | -0.17328 | 0.99088 | -0.17386 | 5.3132
22 | 0.0075819 | 0.0018997 | -0.0075814 | -0.0018995 | 4.9212e-07 | 1.9069e-07 | 0.011523 | 0.011523 | 0.011523 | 0.97904 | -0.40345 | 0.97897 | -0.40481 | 3.1658
23 | 0.0062183 | 0.0015585 | -0.0062181 | -0.0015584 | 2.2932e-07 | 5.9973e-08 | 0.0094319 | 0.0094319 | 0.0094319 | 0.98104 | -0.36439 | 0.981 | -0.36517 | 2.5912
24 | 0.028278 | 0.0071088 | -0.028264 | -0.0071 | 1.4099e-05 | 8.7655e-06 | 0.0429 | 0.0429 | 0.0429 | 0.98104 | -0.36439 | 0.9805 | -0.37484 | 11.7856
25 | 0.047609 | 0.012021 | -0.047594 | -0.012012 | 1.5073e-05 | 9.5485e-06 | 0.072053 | 0.072053 | 0.072053 | 0.98365 | -0.31338 | 0.98331 | -0.31999 | 19.7948
26 | 0.026956 | 0.0067593 | -0.02695 | -0.0067556 | 6.0947e-06 | 3.7743e-06 | 0.040594 | 0.040594 | 0.040594 | 0.98814 | -0.22662 | 0.9879 | -0.23137 | 11.1523
27 | 0.012824 | 0.0032157 | -0.012821 | -0.0032139 | 3.3139e-06 | 1.8177e-06 | 0.019315 | 0.019315 | 0.019315 | 0.98798 | -0.22964 | 0.98771 | -0.23507 | 5.3064
28 | 0.0046353 | 0.0011617 | -0.0046352 | -0.0011617 | 4.8523e-08 | -2.9509e-09 | 0.0069809 | 0.0069809 | 0.0069809 | 0.98804 | -0.22863 | 0.98803 | -0.22885 | 1.9178
29 | -0.24622 | -0.062633 | 0.24639 | 0.062743 | 0.00017228 | 0.00011008 | 0.36919 | 0.36919 | 0.36919 | 0.99325 | -0.12838 | 0.994 | -0.11387 | 50.7133
30 | 0.012879 | 0.0032283 | -0.012876 | -0.0032271 | 2.089e-06 | 1.1451e-06 | 0.01934 | 0.01934 | 0.01934 | 0.99088 | -0.17386 | 0.9907 | -0.17726 | 5.3132
31 | 0.00077983 | 0.00019543 | -0.00077983 | -0.00019544 | 7.6611e-10 | -1.7775e-08 | 0.0011856 | 0.0011856 | 0.0011856 | 0.97874 | -0.40943 | 0.97874 | -0.40945 | 0.32572
32 | -0.0021195 | -0.00053117 | 0.0021196 | 0.00053088 | 1.1211e-07 | -2.9012e-07 | 0.0032223 | 0.0032222 | 0.0032223 | 0.97874 | -0.40943 | 0.97879 | -0.40832 | 0.88524
33 | -0.0037294 | -0.00093435 | 0.0037295 | 0.00093433 | 3.4605e-08 | -1.3936e-08 | 0.0056696 | 0.0056696 | 0.0056696 | 0.97879 | -0.40832 | 0.9788 | -0.40812 | 1.5576
34 | -0.0048614 | -0.001218 | 0.0048617 | 0.001218 | 3.1166e-07 | 8.1863e-09 | 0.0073903 | 0.0073902 | 0.0073903 | 0.9788 | -0.40812 | 0.97887 | -0.40678 | 2.0303
35 | 0.00055988 | 0.00014019 | -0.00055988 | -0.00014032 | 2.8441e-09 | -1.2981e-07 | 0.00085105 | 0.00085109 | 0.00085109 | 0.97887 | -0.40678 | 0.97887 | -0.40688 | 0.23382
36 | -0.0054216 | -0.0013582 | 0.0054217 | 0.0013582 | 1.5806e-07 | 2.3144e-08 | 0.0082413 | 0.0082413 | 0.0082413 | 0.97887 | -0.40678 | 0.9789 | -0.40616 | 2.2641
37 | -0.0013698 | -0.00034308 | 0.0013698 | 0.00034283 | 3.5215e-08 | -2.4794e-07 | 0.0020857 | 0.0020856 | 0.0020857 | 0.97722 | -0.43914 | 0.97724 | -0.4386 | 0.57298
38 | 0.0013698 | 0.00034308 | -0.0013697 | -0.00034323 | 2.1048e-08 | -1.4817e-07 | 0.0020857 | 0.0020857 | 0.0020857 | 0.97722 | -0.43914 | 0.9772 | -0.43946 | 0.573
39 | -0.022177 | -0.0055668 | 0.022183 | 0.0055705 | 5.963e-06 | 3.6416e-06 | 0.033772 | 0.033772 | 0.033772 | 0.97724 | -0.4386 | 0.97753 | -0.43297 | 9.278
40 | 0.020808 | 0.005224 | -0.020799 | -0.0052188 | 8.5122e-06 | 5.1647e-06 | 0.031686 | 0.031687 | 0.031687 | 0.97724 | -0.4386 | 0.97681 | -0.44718 | 8.7051
41 | 0.0006066 | 0.00015197 | -0.0006066 | -0.00015203 | 1.4884e-09 | -5.7326e-08 | 0.00092367 | 0.0009237 | 0.0009237 | 0.9772 | -0.43946 | 0.9772 | -0.43952 | 0.25376
42 | -0.0065365 | -0.0016376 | 0.0065369 | 0.0016377 | 4.2132e-07 | 1.2656e-07 | 0.0099358 | 0.0099358 | 0.0099358 | 0.9789 | -0.40616 | 0.97897 | -0.40481 | 2.7296
43 | 0.0076052 | 0.0019061 | -0.0076048 | -0.0019059 | 3.7726e-07 | 1.462e-07 | 0.011542 | 0.011542 | 0.011542 | 0.9805 | -0.37484 | 0.98045 | -0.37588 | 3.1708
44 | 0.020659 | 0.0051939 | -0.020651 | -0.0051893 | 7.6434e-06 | 4.6304e-06 | 0.031358 | 0.031358 | 0.031358 | 0.9805 | -0.37484 | 0.98011 | -0.38259 | 8.6149
45 | 0.0040627 | 0.0010182 | -0.0040626 | -0.0010182 | 1.0281e-07 | -2.5014e-08 | 0.0061681 | 0.0061681 | 0.0061681 | 0.98011 | -0.38259 | 0.98008 | -0.38312 | 1.6945
46 | 0.016589 | 0.0041711 | -0.016553 | -0.0041504 | 3.5266e-05 | 2.0707e-05 | 0.02519 | 0.025191 | 0.025191 | 0.98011 | -0.38259 | 0.97783 | -0.4272 | 6.9205
47 | -0.0078927 | -0.0019781 | 0.0078937 | 0.0019785 | 9.7595e-07 | 3.9871e-07 | 0.012017 | 0.012017 | 0.012017 | 0.97736 | -0.43653 | 0.97749 | -0.43394 | 3.3013
48 | 0.0039338 | 0.00098588 | -0.0039338 | -0.0009859 | 5.7312e-08 | -1.6713e-08 | 0.0059892 | 0.0059893 | 0.0059893 | 0.97736 | -0.43653 | 0.97734 | -0.43684 | 1.6454
49 | -0.012542 | -0.0031435 | 0.012543 | 0.0031441 | 9.7632e-07 | 5.3531e-07 | 0.019093 | 0.019093 | 0.019093 | 0.97749 | -0.43394 | 0.97757 | -0.43231 | 5.2454
50 | -0.016549 | -0.0041481 | 0.016553 | 0.0041504 | 4.0256e-06 | 2.3643e-06 | 0.025191 | 0.025191 | 0.025191 | 0.97757 | -0.43231 | 0.97783 | -0.4272 | 6.9205
51 | -0.023021 | -0.0057803 | 0.023029 | 0.0057854 | 8.2479e-06 | 5.0541e-06 | 0.035046 | 0.035046 | 0.035046 | 0.97753 | -0.43297 | 0.97791 | -0.42546 | 9.6281
52 | 0.020799 | 0.0052188 | -0.020794 | -0.0052158 | 5.0596e-06 | 3.07e-06 | 0.031687 | 0.031687 | 0.031687 | 0.97681 | -0.44718 | 0.97655 | -0.45228 | 8.7051
53 | 0.047594 | 0.012012 | -0.047519 | -0.011964 | 7.5645e-05 | 4.7921e-05 | 0.072053 | 0.072053 | 0.072053 | 0.98331 | -0.31999 | 0.9816 | -0.35324 | 19.7948
54 | 0.042731 | 0.010764 | -0.042714 | -0.010753 | 1.6247e-05 | 1.0268e-05 | 0.064795 | 0.064795 | 0.064795 | 0.9816 | -0.35324 | 0.9812 | -0.36119 | 17.8009
55 | 0.037856 | 0.0095358 | -0.037845 | -0.0095291 | 1.0708e-05 | 6.744e-06 | 0.057427 | 0.057427 | 0.057427 | 0.9812 | -0.36119 | 0.98089 | -0.36711 | 15.7768
56 | -0.032677 | -0.0082295 | 0.032688 | 0.0082362 | 1.0789e-05 | 6.7572e-06 | 0.049605 | 0.049605 | 0.049605 | 0.98052 | -0.37442 | 0.98087 | -0.36752 | 13.6276
57 | 0.032677 | 0.0082295 | -0.032655 | -0.0082153 | 2.2603e-05 | 1.4157e-05 | 0.049605 | 0.049605 | 0.049605 | 0.98052 | -0.37442 | 0.97978 | -0.3889 | 13.6277
58 | -0.037277 | -0.0093864 | 0.037278 | 0.0093868 | 7.3771e-07 | 4.6437e-07 | 0.056566 | 0.056566 | 0.056566 | 0.98087 | -0.36752 | 0.98089 | -0.36711 | 15.5402
59 | 0.032055 | 0.008065 | -0.032045 | -0.0080588 | 9.9852e-06 | 6.2491e-06 | 0.048694 | 0.048694 | 0.048694 | 0.97978 | -0.3889 | 0.97945 | -0.39542 | 13.3775
60 | 0.0023281 | 0.0005808 | -0.0023279 | -0.00058124 | 2.2048e-07 | -4.399e-07 | 0.0035522 | 0.0035524 | 0.0035524 | 0.97499 | -0.48304 | 0.97489 | -0.48504 | 0.97593
61 | 0.0087733 | 0.0021992 | -0.0087639 | -0.0021949 | 9.3994e-06 | 4.2742e-06 | 0.01339 | 0.013391 | 0.013391 | 0.97499 | -0.48304 | 0.97385 | -0.50555 | 3.6787
62 | -0.011101 | -0.00278 | 0.011104 | 0.0027814 | 2.6225e-06 | 1.3745e-06 | 0.016942 | 0.016942 | 0.016942 | 0.97499 | -0.48304 | 0.97524 | -0.47808 | 4.6544
63 | 0.00044462 | 0.00011112 | -0.00044461 | -0.00011143 | 4.3148e-09 | -3.0879e-07 | 0.00067853 | 0.00067864 | 0.00067864 | 0.97489 | -0.48504 | 0.97488 | -0.48524 | 0.18644
64 | 0.0018833 | 0.00047011 | -0.0018831 | -0.00047075 | 1.8772e-07 | -6.3545e-07 | 0.0028738 | 0.0028741 | 0.0028741 | 0.97489 | -0.48504 | 0.97478 | -0.48714 | 0.78959
65 | 0.0033575 | 0.0008412 | -0.0033572 | -0.00084139 | 3.0189e-07 | -1.8734e-07 | 0.0051301 | 0.0051302 | 0.0051302 | 0.97385 | -0.50555 | 0.97375 | -0.50744 | 1.4094
66 | 0.0024013 | 0.00060174 | -0.0024013 | -0.00060182 | 4.2413e-08 | -7.7379e-08 | 0.0036691 | 0.0036692 | 0.0036692 | 0.97385 | -0.50555 | 0.97383 | -0.50592 | 1.008
67 | 0.0030051 | 0.00075198 | -0.0030043 | -0.00075274 | 8.1924e-07 | -7.6461e-07 | 0.0045913 | 0.0045918 | 0.0045918 | 0.97385 | -0.50555 | 0.97356 | -0.51128 | 1.2615
68 | -0.013369 | -0.0033491 | 0.013371 | 0.0033503 | 2.2448e-06 | 1.2571e-06 | 0.020398 | 0.020398 | 0.020398 | 0.97524 | -0.47808 | 0.97542 | -0.47456 | 5.6039
69 | 0.028474 | 0.0071639 | -0.028464 | -0.0071572 | 1.0796e-05 | 6.716e-06 | 0.043269 | 0.04327 | 0.04327 | 0.97945 | -0.39542 | 0.97904 | -0.40336 | 11.8872
70 | 0.0013599 | 0.00034046 | -0.0013598 | -0.00034081 | 4.9614e-08 | -3.5097e-07 | 0.0020758 | 0.0020759 | 0.0020759 | 0.97478 | -0.48714 | 0.97474 | -0.4879 | 0.57031
71 | 0.00052318 | 0.00013029 | -0.00052316 | -0.00013112 | 1.6024e-08 | -8.2519e-07 | 0.00079834 | 0.00079864 | 0.00079864 | 0.97478 | -0.48714 | 0.97475 | -0.48778 | 0.21941
72 | 0.0030043 | 0.00075274 | -0.0030041 | -0.0007529 | 1.7022e-07 | -1.5873e-07 | 0.0045918 | 0.0045919 | 0.0045919 | 0.97356 | -0.51128 | 0.9735 | -0.51247 | 1.2615
73 | 0.13797 | 0.035242 | -0.13762 | -0.035017 | 0.00035154 | 0.0002247 | 0.2075 | 0.2075 | 0.2075 | 0.99053 | -0.17996 | 0.98777 | -0.23281 | 57.005
74 | -0.13797 | -0.035242 | 0.1385 | 0.035581 | 0.0005309 | 0.00033935 | 0.2075 | 0.2075 | 0.2075 | 0.99053 | -0.17996 | 0.99469 | -0.1007 | 57.005
75 | 0.1324 | 0.03371 | -0.13204 | -0.03348 | 0.00036019 | 0.00023021 | 0.19964 | 0.19964 | 0.19964 | 0.98777 | -0.23281 | 0.98484 | -0.28939 | 54.8472
76 | -0.14568 | -0.03738 | 0.14571 | 0.0374 | 3.1438e-05 | 2.0029e-05 | 0.21824 | 0.21824 | 0.21824 | 0.99469 | -0.1007 | 0.99493 | -0.096254 | 29.9773
77 | 0.0030294 | 0.00075805 | -0.0030293 | -0.00075809 | 4.4945e-08 | -4.1296e-08 | 0.0046209 | 0.0046209 | 0.0046209 | 0.97542 | -0.47456 | 0.9754 | -0.47487 | 1.2695
78 | -0.016401 | -0.0041084 | 0.016405 | 0.0041107 | 3.9471e-06 | 2.3162e-06 | 0.025019 | 0.025019 | 0.025019 | 0.97542 | -0.47456 | 0.97567 | -0.46951 | 6.8733
79 | -0.017795 | -0.0044604 | 0.017801 | 0.004464 | 6.0668e-06 | 3.5939e-06 | 0.026795 | 0.026795 | 0.026795 | 0.98824 | -0.22566 | 0.9886 | -0.21851 | 7.3613
80 | 0.0091865 | 0.0023028 | -0.0091842 | -0.0023018 | 2.2889e-06 | 1.0563e-06 | 0.013833 | 0.013833 | 0.013833 | 0.98824 | -0.22566 | 0.98797 | -0.23089 | 3.8002
81 | 0.036639 | 0.009192 | -0.036625 | -0.0091837 | 1.3273e-05 | 8.3457e-06 | 0.055151 | 0.055151 | 0.055151 | 0.9886 | -0.21851 | 0.98821 | -0.22611 | 15.1513
82 | -0.05444 | -0.013656 | 0.0545 | 0.013694 | 6.0094e-05 | 3.8153e-05 | 0.081946 | 0.081946 | 0.081946 | 0.9886 | -0.21851 | 0.98979 | -0.19538 | 22.5126
83 | 0.016888 | 0.0042343 | -0.016884 | -0.004232 | 3.9991e-06 | 2.3482e-06 | 0.025429 | 0.025429 | 0.025429 | 0.98821 | -0.22611 | 0.98796 | -0.23108 | 6.9861
84 | 0.019738 | 0.0049493 | -0.019735 | -0.0049476 | 2.8839e-06 | 1.7342e-06 | 0.029721 | 0.029721 | 0.029721 | 0.98821 | -0.22611 | 0.98805 | -0.22918 | 8.1652
85 | -0.0545 | -0.013694 | 0.054517 | 0.013705 | 1.6756e-05 | 1.0638e-05 | 0.081946 | 0.081946 | 0.081946 | 0.98979 | -0.19538 | 0.99013 | -0.18894 | 22.5126
86 | 0.011222 | 0.0028131 | -0.011221 | -0.0028125 | 1.1461e-06 | 5.9655e-07 | 0.016903 | 0.016903 | 0.016903 | 0.98796 | -0.23108 | 0.98785 | -0.23322 | 4.6436
87 | 0.014394 | 0.0036091 | -0.014391 | -0.0036073 | 3.1397e-06 | 1.7813e-06 | 0.021679 | 0.021679 | 0.021679 | 0.98805 | -0.22918 | 0.98782 | -0.23375 | 5.9557
88 | -0.060293 | -0.015152 | 0.060341 | 0.015183 | 4.8547e-05 | 3.0867e-05 | 0.090626 | 0.090626 | 0.090626 | 0.99013 | -0.18894 | 0.991 | -0.17209 | 24.8973
89 | 0.011221 | 0.0028125 | -0.01122 | -0.002812 | 9.3016e-07 | 4.8416e-07 | 0.016903 | 0.016903 | 0.016903 | 0.98785 | -0.23322 | 0.98776 | -0.23496 | 4.6436
90 | 0.014391 | 0.0036073 | -0.014389 | -0.0036063 | 1.7699e-06 | 1.0042e-06 | 0.021679 | 0.021679 | 0.021679 | 0.98782 | -0.23375 | 0.98769 | -0.23634 | 5.9557
91 | 0.024382 | 0.0061133 | -0.024376 | -0.0061091 | 6.8357e-06 | 4.1997e-06 | 0.036612 | 0.036612 | 0.036612 | 0.991 | -0.17209 | 0.99069 | -0.17798 | 10.0582
92 | -0.084724 | -0.021297 | 0.084974 | 0.021456 | 0.00025003 | 0.00015949 | 0.12724 | 0.12724 | 0.12724 | 0.991 | -0.17209 | 0.99419 | -0.11048 | 34.9555
93 | 0.0049481 | 0.0012401 | -0.0049479 | -0.0012401 | 2.1432e-07 | 2.051e-09 | 0.0074059 | 0.007406 | 0.007406 | 0.99419 | -0.11048 | 0.99414 | -0.11139 | 2.0346
94 | -0.089922 | -0.022696 | 0.090031 | 0.022766 | 0.00010952 | 6.9884e-05 | 0.13464 | 0.13464 | 0.13464 | 0.99419 | -0.11048 | 0.99551 | -0.085085 | 36.99
95 | 0.16089 | 0.04124 | -0.1608 | -0.041184 | 8.7062e-05 | 5.5512e-05 | 0.24081 | 0.24081 | 0.24081 | 0.99551 | -0.085085 | 0.99493 | -0.096254 | 33.0786
96 | -0.25092 | -0.064006 | 0.25116 | 0.064161 | 0.00024268 | 0.00015508 | 0.37546 | 0.37546 | 0.37546 | 0.99551 | -0.085085 | 0.99657 | -0.065079 | 51.5735
97 | 0.006332 | 0.001587 | -0.0063318 | -0.0015869 | 2.8197e-07 | 7.4721e-08 | 0.0095396 | 0.0095397 | 0.0095397 | 0.98769 | -0.23634 | 0.98764 | -0.23727 | 2.6208
98 | -0.2622 | -0.067056 | 0.26233 | 0.067138 | 0.00012812 | 8.1883e-05 | 0.39142 | 0.39142 | 0.39142 | 0.99799 | -0.038045 | 0.99852 | -0.027952 | 53.7665
99 | 0.2546 | 0.06515 | -0.25426 | -0.064938 | 0.00033275 | 0.00021264 | 0.38008 | 0.38008 | 0.38008 | 0.99799 | -0.038045 | 0.99657 | -0.065079 | 52.2092
100 | -0.27095 | -0.069298 | 0.27132 | 0.069533 | 0.00036707 | 0.00023461 | 0.40427 | 0.40427 | 0.40427 | 0.99852 | -0.027952 | 1 | 0 | 55.5312
101 | 0.27644 | 0.070832 | -0.27642 | -0.070818 | 2.1327e-05 | 1.3632e-05 | 0.41189 | 0.41189 | 0.41189 | 1 | 0 | 0.99992 | -0.001592 | 56.5787
102 | 0.26777 | 0.068652 | -0.26728 | -0.068338 | 0.00049068 | 0.0003136 | 0.39903 | 0.39903 | 0.39903 | 0.99992 | -0.001592 | 0.99791 | -0.03946 | 54.8115
103 | 0.015096 | 0.0037843 | -0.015093 | -0.0037827 | 2.7943e-06 | 1.5985e-06 | 0.022578 | 0.022578 | 0.022578 | 0.99493 | -0.096254 | 0.99472 | -0.10014 | 6.2027
104 | 0.25978 | 0.066459 | -0.25918 | -0.066074 | 0.00060228 | 0.0003849 | 0.38785 | 0.38785 | 0.38785 | 0.99791 | -0.03946 | 0.99539 | -0.087479 | 53.2759
105 | 0.0044405 | 0.0011128 | -0.0044403 | -0.0011129 | 1.0859e-07 | -1.4325e-08 | 0.0066695 | 0.0066695 | 0.0066695 | 0.9907 | -0.17726 | 0.99067 | -0.17778 | 1.8323
106 | 0.008436 | 0.0021143 | -0.0084358 | -0.0021142 | 2.4413e-07 | 1.0403e-07 | 0.012671 | 0.012671 | 0.012671 | 0.9907 | -0.17726 | 0.99067 | -0.17787 | 3.481
107 | -0.25298 | -0.064395 | 0.2533 | 0.064601 | 0.00032233 | 0.00020598 | 0.37906 | 0.37906 | 0.37906 | 0.994 | -0.11387 | 0.99539 | -0.087479 | 52.0686
108 | 0.011731 | 0.002941 | -0.011728 | -0.0029393 | 3.2376e-06 | 1.7225e-06 | 0.017725 | 0.017725 | 0.017725 | 0.98484 | -0.28939 | 0.98454 | -0.29519 | 4.8696
109 | 0.12031 | 0.030539 | -0.11968 | -0.030134 | 0.00063462 | 0.00040551 | 0.18192 | 0.18192 | 0.18192 | 0.98484 | -0.28939 | 0.97916 | -0.39967 | 49.9778
110 | 0.031308 | 0.0078682 | -0.031301 | -0.007864 | 6.6784e-06 | 4.1753e-06 | 0.047585 | 0.047585 | 0.047585 | 0.97916 | -0.39967 | 0.97894 | -0.40414 | 13.0729
111 | 0.045272 | 0.011375 | -0.045229 | -0.011348 | 4.3606e-05 | 2.7599e-05 | 0.06881 | 0.06881 | 0.06881 | 0.97916 | -0.39967 | 0.97813 | -0.41987 | 18.9038
112 | 0.043096 | 0.01089 | -0.042958 | -0.010803 | 0.00013766 | 8.7028e-05 | 0.065524 | 0.065524 | 0.065524 | 0.97916 | -0.39967 | 0.97575 | -0.46653 | 18.0012
113 | 0.013473 | 0.0033777 | -0.013469 | -0.0033758 | 3.3804e-06 | 1.9011e-06 | 0.02063 | 0.02063 | 0.02063 | 0.97179 | -0.54452 | 0.97153 | -0.54979 | 5.6677
114 | -0.021342 | -0.00535 | 0.021363 | 0.0053625 | 2.0491e-05 | 1.248e-05 | 0.03268 | 0.03268 | 0.03268 | 0.97179 | -0.54452 | 0.97281 | -0.52439 | 8.9781
115 | -0.021363 | -0.0053625 | 0.021401 | 0.0053858 | 3.8307e-05 | 2.3327e-05 | 0.03268 | 0.03268 | 0.03268 | 0.97281 | -0.52439 | 0.97472 | -0.48687 | 8.978
116 | 0.013655 | 0.0034228 | -0.013653 | -0.0034218 | 1.6718e-06 | 9.4211e-07 | 0.020846 | 0.020846 | 0.020846 | 0.97472 | -0.48687 | 0.97459 | -0.48944 | 5.727
117 | -0.035056 | -0.0088086 | 0.035079 | 0.0088226 | 2.2246e-05 | 1.3979e-05 | 0.053526 | 0.053526 | 0.053526 | 0.97472 | -0.48687 | 0.97539 | -0.47358 | 14.7048
118 | -0.042944 | -0.010794 | 0.042958 | 0.010803 | 1.4457e-05 | 9.1406e-06 | 0.065524 | 0.065524 | 0.065524 | 0.97539 | -0.47358 | 0.97575 | -0.46653 | 18.0012
119 | 0.0098292 | 0.0024635 | -0.0098288 | -0.0024633 | 4.3459e-07 | 2.1057e-07 | 0.014812 | 0.014812 | 0.014812 | 0.98743 | -0.24047 | 0.98738 | -0.2414 | 4.0693
120 | -0.0098292 | -0.0024635 | 0.0098295 | 0.0024637 | 3.2598e-07 | 1.5794e-07 | 0.014812 | 0.014812 | 0.014812 | 0.98743 | -0.24047 | 0.98746 | -0.23978 | 4.0693
121 | -0.0098295 | -0.0024637 | 0.0098318 | 0.0024648 | 2.2066e-06 | 1.0691e-06 | 0.014812 | 0.014812 | 0.014812 | 0.98746 | -0.23978 | 0.98771 | -0.23507 | 4.0693
122 | 0.005234 | 0.0013116 | -0.0052331 | -0.0013115 | 8.1757e-07 | 9.5568e-08 | 0.0079803 | 0.0079804 | 0.0079804 | 0.97592 | -0.46337 | 0.97576 | -0.46665 | 2.1924
123 | -0.0069245 | -0.0017353 | 0.0069276 | 0.0017363 | 3.0545e-06 | 1.0414e-06 | 0.010558 | 0.010558 | 0.010558 | 0.97592 | -0.46337 | 0.97639 | -0.45411 | 2.9005
124 | 0.0052331 | 0.0013115 | -0.0052327 | -0.0013114 | 4.7623e-07 | 5.5743e-08 | 0.0079804 | 0.0079805 | 0.0079805 | 0.97576 | -0.46665 | 0.97566 | -0.46856 | 2.1925
125 | -0.0069276 | -0.0017363 | 0.0069293 | 0.0017369 | 1.7871e-06 | 6.0885e-07 | 0.010558 | 0.010557 | 0.010558 | 0.97639 | -0.45411 | 0.97667 | -0.4487 | 2.9004
126 | 0.014718 | 0.0036893 | -0.014717 | -0.003689 | 4.5872e-07 | 2.6171e-07 | 0.022169 | 0.022169 | 0.022169 | 0.9879 | -0.23137 | 0.98786 | -0.23202 | 6.0904
127 | 0.012233 | 0.0030663 | -0.012232 | -0.0030658 | 9.3817e-07 | 5.0608e-07 | 0.018425 | 0.018425 | 0.018425 | 0.9879 | -0.23137 | 0.98781 | -0.23298 | 5.0619
128 | 0.0084198 | 0.0021107 | -0.0084184 | -0.0021101 | 1.4696e-06 | 6.2871e-07 | 0.012683 | 0.012683 | 0.012683 | 0.98786 | -0.23202 | 0.98767 | -0.23568 | 3.4844
129 | 0.00906 | 0.0022709 | -0.0090588 | -0.0022704 | 1.1764e-06 | 5.3735e-07 | 0.013648 | 0.013648 | 0.013648 | 0.98781 | -0.23298 | 0.98767 | -0.2357 | 3.7494
130 | 0.0084184 | 0.0021101 | -0.0084181 | -0.0021099 | 2.9763e-07 | 1.2734e-07 | 0.012683 | 0.012683 | 0.012683 | 0.98767 | -0.23568 | 0.98764 | -0.23643 | 3.4844
131 | 0.0084181 | 0.0021099 | -0.008417 | -0.0021095 | 1.0365e-06 | 4.4352e-07 | 0.012683 | 0.012683 | 0.012683 | 0.98764 | -0.23643 | 0.9875 | -0.23901 | 3.4844
132 | 0.0047387 | 0.0011876 | -0.0047386 | -0.0011876 | 1.8001e-07 | -1.1085e-09 | 0.007203 | 0.0072031 | 0.0072031 | 0.97894 | -0.40414 | 0.9789 | -0.40494 | 1.9789
133 | 0.026562 | 0.0066764 | -0.026544 | -0.0066653 | 1.793e-05 | 1.1107e-05 | 0.040382 | 0.040382 | 0.040382 | 0.97894 | -0.40414 | 0.97822 | -0.41829 | 11.0941
134 | 0.039055 | 0.0098004 | -0.039047 | -0.0097958 | 7.2718e-06 | 4.5851e-06 | 0.059418 | 0.059418 | 0.059418 | 0.97813 | -0.41987 | 0.97794 | -0.42378 | 16.3235
135 | 0.026544 | 0.0066653 | -0.026537 | -0.0066606 | 7.5377e-06 | 4.6694e-06 | 0.040382 | 0.040382 | 0.040382 | 0.97822 | -0.41829 | 0.97791 | -0.42424 | 11.0941
136 | 0.032768 | 0.0082221 | -0.032747 | -0.0082089 | 2.108e-05 | 1.3207e-05 | 0.049863 | 0.049863 | 0.049863 | 0.97794 | -0.42378 | 0.97725 | -0.43728 | 13.6986
137 | 0.022073 | 0.0055336 | -0.022072 | -0.0055331 | 8.9033e-07 | 5.4348e-07 | 0.03361 | 0.03361 | 0.03361 | 0.97725 | -0.43728 | 0.97721 | -0.43813 | 9.2334
138 | 0.019738 | 0.0049481 | -0.019735 | -0.0049466 | 2.5745e-06 | 1.5525e-06 | 0.030056 | 0.030056 | 0.030056 | 0.97721 | -0.43813 | 0.97707 | -0.44086 | 8.2571
139 | 0.010194 | 0.0025552 | -0.010191 | -0.0025541 | 2.1861e-06 | 1.0962e-06 | 0.015524 | 0.015524 | 0.015524 | 0.97707 | -0.44086 | 0.97684 | -0.44537 | 4.265
140 | 0.022933 | 0.0057576 | -0.022907 | -0.0057412 | 2.672e-05 | 1.6368e-05 | 0.034899 | 0.0349 | 0.0349 | 0.97791 | -0.42424 | 0.97667 | -0.4487 | 9.5878
141 | 0.0043262 | 0.0010842 | -0.004326 | -0.0010842 | 1.7716e-07 | -2.279e-08 | 0.00659 | 0.0065901 | 0.0065901 | 0.97684 | -0.44537 | 0.97679 | -0.44623 | 1.8105
142 | 0.0058652 | 0.0014699 | -0.0058648 | -0.0014699 | 3.3679e-07 | 7.4707e-08 | 0.0089344 | 0.0089345 | 0.0089345 | 0.97684 | -0.44537 | 0.97678 | -0.44657 | 2.4545
143 | -0.017755 | -0.004449 | 0.017756 | 0.0044499 | 1.4642e-06 | 8.7056e-07 | 0.027078 | 0.027077 | 0.027078 | 0.97567 | -0.46951 | 0.97576 | -0.46777 | 7.4389
144 | 0.00054243 | 0.00013587 | -0.00054243 | -0.00013595 | 1.6337e-09 | -7.8484e-08 | 0.00082717 | 0.0008272 | 0.0008272 | 0.97576 | -0.46777 | 0.97576 | -0.46784 | 0.22725
145 | -0.018298 | -0.0045857 | 0.018303 | 0.0045885 | 4.672e-06 | 2.7902e-06 | 0.027905 | 0.027905 | 0.027905 | 0.97576 | -0.46777 | 0.97603 | -0.46242 | 7.6661
146 | 0.00076674 | 0.00019201 | -0.00076673 | -0.00019216 | 6.2479e-09 | -1.48e-07 | 0.0011696 | 0.0011697 | 0.0011697 | 0.9754 | -0.47487 | 0.97539 | -0.47504 | 0.32135
147 | 0.0022626 | 0.00056608 | -0.0022623 | -0.00056655 | 2.2126e-07 | -4.7657e-07 | 0.0034513 | 0.0034515 | 0.0034515 | 0.9754 | -0.47487 | 0.9753 | -0.47692 | 0.94822
148 | 0.00052259 | 0.00013086 | -0.00052259 | -0.00013097 | 2.1855e-09 | -1.1336e-07 | 0.00079667 | 0.00079671 | 0.00079671 | 0.97603 | -0.46242 | 0.97603 | -0.4625 | 0.21888
149 | -0.018826 | -0.0047194 | 0.018829 | 0.0047214 | 3.4209e-06 | 2.0509e-06 | 0.028701 | 0.028701 | 0.028701 | 0.97603 | -0.46242 | 0.97623 | -0.4586 | 7.885
150 | 0.0016742 | 0.00041915 | -0.0016742 | -0.00041931 | 3.7076e-08 | -1.6539e-07 | 0.0025542 | 0.0025542 | 0.0025542 | 0.9753 | -0.47692 | 0.97527 | -0.47739 | 0.70171
151 | 0.0005221 | 0.00013067 | -0.0005221 | -0.00013085 | 3.4781e-09 | -1.8089e-07 | 0.00079575 | 0.00079582 | 0.00079582 | 0.97623 | -0.4586 | 0.97622 | -0.45874 | 0.21863
152 | -0.019351 | -0.0048521 | 0.019357 | 0.0048556 | 5.8296e-06 | 3.5075e-06 | 0.029497 | 0.029497 | 0.029497 | 0.97623 | -0.4586 | 0.97655 | -0.45228 | 8.1036
153 | 0.0016742 | 0.00041931 | -0.0016741 | -0.00041957 | 5.6984e-08 | -2.5415e-07 | 0.0025542 | 0.0025543 | 0.0025543 | 0.97527 | -0.47739 | 0.97524 | -0.4781 | 0.70174
154 | 0.00085713 | 0.00021467 | -0.00085712 | -0.00021481 | 7.4979e-09 | -1.4336e-07 | 0.0013027 | 0.0013027 | 0.0013027 | 0.97904 | -0.40336 | 0.97903 | -0.40354 | 0.35789
155 | 0.027606 | 0.0069425 | -0.027593 | -0.0069342 | 1.346e-05 | 8.3584e-06 | 0.041967 | 0.041967 | 0.041967 | 0.97904 | -0.40336 | 0.97852 | -0.41357 | 11.5294
156 | 0.023924 | 0.0060146 | -0.02391 | -0.0060063 | 1.357e-05 | 8.3417e-06 | 0.036388 | 0.036388 | 0.036388 | 0.97852 | -0.41357 | 0.97791 | -0.42546 | 9.9966

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.556 | 0.14202

## res_load
| p_mw | q_mvar
0 | 0.030205 | 0.0075701
1 | 0.0053902 | 0.0013509
2 | 0.01114 | 0.0027918
3 | 0.0053448 | 0.0013395
4 | 0.0003046 | 7.6341e-05
5 | 0.0043024 | 0.0010783
6 | 0.0027501 | 0.00068923
7 | 0.0062614 | 0.0015693
8 | 0.0056313 | 0.0014113
9 | 0.010398 | 0.0026059
10 | 0.0038281 | 0.00095942
11 | 0.003213 | 0.00080525
12 | 0.0040389 | 0.0010122
13 | 0.0043325 | 0.0010858
14 | 0.0013396 | 0.00033574
15 | 0.00077983 | 0.00019544
16 | 0.0016099 | 0.00040347
17 | 0.0011319 | 0.00028368
18 | 0.00076313 | 0.00019126
19 | 0.00055988 | 0.00014032
20 | 0.0011148 | 0.00027939
21 | 0.0010445 | 0.00026179
22 | 0.0062181 | 0.0015584
23 | 0.0076048 | 0.0019059
24 | 0.0039589 | 0.00099219
25 | 0.0046487 | 0.0011651
26 | 0.0039338 | 0.0009859
27 | 0.0040059 | 0.001004
28 | 0.0040626 | 0.0010182
29 | 0.00083724 | 0.00020983
30 | 0.0006066 | 0.00015203
31 | 0.004788 | 0.0012
32 | 0.0048583 | 0.0012176
33 | 0.0045891 | 0.0011501
34 | 0.0005997 | 0.0001503
35 | 0.0022651 | 0.00056769
36 | 0.00056766 | 0.00014227
37 | 0.0035705 | 0.00089486
38 | 0.00044461 | 0.00011143
39 | 0.0033572 | 0.00084139
40 | 0.0024013 | 0.00060182
41 | 0.0052139 | 0.0013067
42 | 0.0071775 | 0.0017989
43 | 0.0086088 | 0.0021576
44 | 0.0091842 | 0.0023018
45 | 0.0056614 | 0.0014189
46 | 0.0053405 | 0.0013385
47 | 0.0057759 | 0.0014476
48 | 0.024376 | 0.0061091
49 | 0.0049479 | 0.0012401
50 | 0.0080574 | 0.0020194
51 | 0.0063318 | 0.0015869
52 | 0.01122 | 0.002812
53 | 0.0076039 | 0.0019057
54 | 0.0086208 | 0.0021606
55 | 0.0030994 | 0.00077679
56 | 0.0065932 | 0.0016524
57 | 0.0086453 | 0.0021667
58 | 0.0074974 | 0.001879
59 | 0.015093 | 0.0037827
60 | 0.0044403 | 0.0011129
61 | 0.0084358 | 0.0021142
62 | 0.0065911 | 0.0016519
63 | 0.0058794 | 0.0014735
64 | 0.011728 | 0.0029393
65 | 0.0078696 | 0.0019723
66 | 0.013469 | 0.0033758
67 | 0.013653 | 0.0034218
68 | 0.0078652 | 0.0019712
69 | 0.0098288 | 0.0024633
70 | 0.0016905 | 0.00042369
71 | 0.0062975 | 0.0015783
72 | 0.0031716 | 0.00079488
73 | 0.0090588 | 0.0022704
74 | 0.006174 | 0.0015474
75 | 0.0047386 | 0.0011876
76 | 0.0062794 | 0.0015738
77 | 0.010674 | 0.0026752
78 | 0.002334 | 0.00058495
79 | 0.0095417 | 0.0023914
80 | 0.0036034 | 0.00090309
81 | 0.008417 | 0.0021095
82 | 0.002989 | 0.00074912
83 | 0.004326 | 0.0010842
84 | 0.0058648 | 0.0014699
85 | 0.0046352 | 0.0011617
86 | 0.0013499 | 0.00033831
87 | 0.00054243 | 0.00013595
88 | 0.00076673 | 0.00019216
89 | 0.00058816 | 0.00014741
90 | 0.00052259 | 0.00013097
91 | 0.0005221 | 0.00013085
92 | 0.001437 | 0.00036016
93 | 0.00052316 | 0.00013112
94 | 0.0013598 | 0.00034081
95 | 0.00085712 | 0.00021481
96 | 0.003669 | 0.00091954
97 | 0.00088152 | 0.00022093
98 | 0.0030041 | 0.0007529
99 | 0.0016741 | 0.00041957
100 | 0.0052327 | 0.0013114
101 | 0.015977 | 0.0040043

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1