## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-44_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-44_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1630-44_0_3_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_1630-44_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1630-44_0_3_node_30 | 0.4 | n |  | TRUE
5 | bus_LV_1630-44_0_3_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1630-44_0_3_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1630-44_0_3_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1630-44_0_3_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1630-44_0_3_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1630-44_0_3_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_1630-44_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1630-44_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1630-44_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1630-44_0_3_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_1630-44_0_3_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1630-44_0_3_node_6 | 0.4 | n |  | TRUE
17 | bus_LV_1630-44_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1630-44_0_3_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1630-44_0_3_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_1630-44_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1630-44_0_3_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1630-44_0_3_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_1630-44_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1630-44_0_3_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_1630-44_0_3_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1630-44_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1630-44_0_3_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_1630-44_0_3_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_1630-44_0_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1630-44_0_3_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1630-44_0_3_node_24 | 0.4 | n |  | TRUE
32 | bus_MV_152_0_node_147 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-44_0_3_load_0 | 0 | 0.012138 | 0.0030421 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-44_0_3_load_30 | 4 | 0.0070197 | 0.0017593 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-44_0_3_load_13 | 7 | 0.036628 | 0.0091798 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-44_0_3_load_29 | 10 | 0.030299 | 0.0075937 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-44_0_3_load_21 | 13 | 0.0047124 | 0.001181 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-44_0_3_load_25 | 14 | 0.0075228 | 0.0018854 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-44_0_3_load_20 | 15 | 0.0083383 | 0.0020898 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-44_0_3_load_6 | 16 | 0.036771 | 0.0092156 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-44_0_3_load_14 | 17 | 0.051637 | 0.012942 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-44_0_3_load_31 | 19 | 0.051602 | 0.012933 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-44_0_3_load_22 | 21 | 0.021251 | 0.0053261 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-44_0_3_load_23 | 22 | 0.0088885 | 0.0022277 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-44_0_3_load_32 | 24 | 0.054766 | 0.013726 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-44_0_3_load_35 | 27 | 0.011669 | 0.0029245 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-44_0_3_load_26 | 29 | 0.0089151 | 0.0022343 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-44_0_3_load_34 | 30 | 0.054825 | 0.01374 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-44_0_3_load_24 | 31 | 0.020061 | 0.0050279 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-44_0_3_line_0 |  | 0 | 1 | 0.0031059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-44_0_3_line_1 |  | 1 | 2 | 0.026266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-44_0_3_line_2 |  | 2 | 7 | 0.023398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-44_0_3_line_3 |  | 3 | 4 | 0.005496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-44_0_3_line_4 |  | 3 | 5 | 0.029786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-44_0_3_line_5 |  | 3 | 6 | 0.027338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-44_0_3_line_6 |  | 5 | 7 | 0.0096093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-44_0_3_line_7 |  | 5 | 11 | 0.038189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-44_0_3_line_8 |  | 6 | 15 | 0.0079344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-44_0_3_line_9 |  | 8 | 9 | 0.031229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_1630-44_0_3_line_10 |  | 8 | 10 | 0.056062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-44_0_3_line_11 |  | 8 | 11 | 0.032934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-44_0_3_line_12 |  | 9 | 17 | 0.0040268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1630-44_0_3_line_13 |  | 11 | 16 | 0.001928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-44_0_3_line_14 |  | 12 | 13 | 0.011908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-44_0_3_line_15 |  | 12 | 14 | 0.01775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-44_0_3_line_16 |  | 13 | 15 | 0.010264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-44_0_3_line_17 |  | 17 | 20 | 0.016679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1630-44_0_3_line_18 |  | 18 | 19 | 0.006258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1630-44_0_3_line_19 |  | 18 | 20 | 0.020135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1630-44_0_3_line_20 |  | 20 | 23 | 0.056012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_1630-44_0_3_line_21 |  | 21 | 22 | 0.02075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-44_0_3_line_22 |  | 22 | 31 | 0.0022336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-44_0_3_line_23 |  | 23 | 24 | 0.005303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-44_0_3_line_24 |  | 23 | 25 | 0.022293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-44_0_3_line_25 |  | 25 | 28 | 0.026078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-44_0_3_line_26 |  | 25 | 29 | 0.03298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-44_0_3_line_27 |  | 26 | 27 | 0.007262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-44_0_3_line_28 |  | 26 | 28 | 0.019379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-44_0_3_line_29 |  | 28 | 30 | 0.007594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-44_0_3_line_30 |  | 29 | 31 | 0.0062452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-44_0_3_trafo_31 | 0.63 MVA 20/0.4 kV | 32 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2723975.9141 | 1217028.9854 | 2723974.9274 | 1217026.0403
1 | 2723975.9141 | 1217028.9854 | 2724000.9761 | 1217020.9004
2 | 2724000.9761 | 1217020.9004 | 2724002.5973 | 1217025.4711 | 2724005.3678 | 1217028.4533 | 2724006.9451 | 1217028.5639 | 2724019.2411 | 1217024.6743
3 | 2724030.895 | 1217000.9519 | 2724036.4042 | 1217000.7886
4 | 2724027.6203 | 1217029.1057 | 2724030.5638 | 1217024.8748 | 2724032.4463 | 1217020.5439 | 2724033.0282 | 1217008.2797 | 2724030.895 | 1217000.9519
5 | 2724030.895 | 1217000.9519 | 2724033.0282 | 1217008.2797 | 2724039.9887 | 1217006.6233 | 2724046.0699 | 1217006.3385 | 2724050.1331 | 1217006.6901 | 2724049.0936 | 1217008.8368
6 | 2724027.6203 | 1217029.1057 | 2724019.6426 | 1217024.5472 | 2724019.2411 | 1217024.6743
7 | 2724003.8698 | 1217056.266 | 2724011.0434 | 1217053.8467 | 2724015.9377 | 1217050.3903 | 2724017.3033 | 1217043.8914 | 2724027.6203 | 1217029.1057
8 | 2724049.0936 | 1217008.8368 | 2724057.0276 | 1217008.9112
9 | 2724013.4851 | 1217079.551 | 2724028.8944 | 1217087.1665 | 2724031.5599 | 1217087.1664 | 2724034.4953 | 1217086.6048 | 2724042.7443 | 1217084.6972
10 | 2724013.4851 | 1217079.551 | 2724018.5742 | 1217086.062 | 2724020.5359 | 1217089.5944 | 2724030.5104 | 1217107.2936 | 2724040.1279 | 1217124.6295 | 2724042.1382 | 1217127.6354
11 | 2724003.8698 | 1217056.266 | 2724005.9104 | 1217062.569 | 2724002.8561 | 1217064.8294 | 2724008.1603 | 1217071.9565 | 2724005.6066 | 1217076.429 | 2724013.4851 | 1217079.551
12 | 2724042.7443 | 1217084.6972 | 2724041.8769 | 1217080.765
13 | 2724003.8698 | 1217056.266 | 2724002.0124 | 1217055.7492
14 | 2724079.1987 | 1217009.1192 | 2724067.2913 | 1217009.0075
15 | 2724079.1987 | 1217009.1192 | 2724085.2726 | 1217009.1902 | 2724084.9587 | 1217020.862
16 | 2724057.0276 | 1217008.9112 | 2724067.2913 | 1217009.0075
17 | 2724058.1513 | 1217077.112 | 2724041.8769 | 1217080.765
18 | 2724060.1534 | 1217056.8267 | 2724053.9061 | 1217057.4305
19 | 2724053.9061 | 1217057.4305 | 2724058.1513 | 1217077.112
20 | 2724058.1513 | 1217077.112 | 2724074.3796 | 1217073.4803 | 2724081.8186 | 1217071.8116 | 2724084.3876 | 1217071.3425 | 2724088.4824 | 1217072.7289 | 2724095.3196 | 1217072.9714 | 2724112.5159 | 1217067.7143
21 | 2724097.6168 | 1217034.2116 | 2724110.0222 | 1217034.3251 | 2724114.5745 | 1217034.1643 | 2724118.3369 | 1217033.7137
22 | 2724118.3369 | 1217033.7137 | 2724120.5547 | 1217033.4482
23 | 2724111.2182 | 1217062.5721 | 2724112.5159 | 1217067.7143
24 | 2724134.6467 | 1217064.7284 | 2724118.1842 | 1217066.4758 | 2724112.5159 | 1217067.7143
25 | 2724134.6467 | 1217064.7284 | 2724140.3245 | 1217064.124 | 2724140.4622 | 1217072.8225 | 2724143.0195 | 1217084.2069
26 | 2724126.7556 | 1217032.7057 | 2724134.6467 | 1217064.7284
27 | 2724146.3806 | 1217102.5691 | 2724148.0711 | 1217109.632
28 | 2724143.0195 | 1217084.2069 | 2724144.159 | 1217089.2902 | 2724147.1059 | 1217102.384 | 2724146.3806 | 1217102.5691
29 | 2724143.0195 | 1217084.2069 | 2724135.5536 | 1217085.7081
30 | 2724126.7556 | 1217032.7057 | 2724120.5547 | 1217033.4482

## bus_geodata
| x | y | coords
0 | 2723974.9274 | 1217026.0403
1 | 2723975.9141 | 1217028.9854
2 | 2724000.9761 | 1217020.9004
3 | 2724030.895 | 1217000.9518
4 | 2724036.4042 | 1217000.7886
5 | 2724027.6203 | 1217029.1057
6 | 2724049.0936 | 1217008.8368
7 | 2724019.2411 | 1217024.6743
8 | 2724013.4851 | 1217079.551
9 | 2724042.7443 | 1217084.6972
10 | 2724042.1383 | 1217127.6354
11 | 2724003.8698 | 1217056.266
12 | 2724079.1987 | 1217009.1192
13 | 2724067.2913 | 1217009.0075
14 | 2724084.9587 | 1217020.862
15 | 2724057.0276 | 1217008.9112
16 | 2724002.0124 | 1217055.7492
17 | 2724041.8769 | 1217080.765
18 | 2724053.9061 | 1217057.4305
19 | 2724060.1534 | 1217056.8267
20 | 2724058.1513 | 1217077.112
21 | 2724097.6168 | 1217034.2116
22 | 2724118.3369 | 1217033.7137
23 | 2724112.5159 | 1217067.7143
24 | 2724111.2182 | 1217062.5721
25 | 2724134.6467 | 1217064.7284
26 | 2724146.3806 | 1217102.5691
27 | 2724148.0711 | 1217109.632
28 | 2724143.0195 | 1217084.2069
29 | 2724126.7556 | 1217032.7057
30 | 2724135.5536 | 1217085.7081
31 | 2724120.5547 | 1217033.4482
32 | 2724053.9061 | 1217057.4305

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98663 | -0.25742 | 0.012138 | 0.0030421
1 | 0.98666 | -0.25674 | 0 | 0
2 | 0.98696 | -0.25103 | 0 | 0
3 | 0.98689 | -0.25227 | 0 | 0
4 | 0.98686 | -0.25297 | 0.0070197 | 0.0017593
5 | 0.98765 | -0.23758 | 0 | 0
6 | 0.98638 | -0.26235 | 0 | 0
7 | 0.98722 | -0.24595 | 0.036628 | 0.0091798
8 | 0.99375 | -0.11962 | 0 | 0
9 | 0.9958 | -0.080169 | 0 | 0
10 | 0.9922 | -0.14965 | 0.030299 | 0.0075937
11 | 0.99033 | -0.18561 | 0 | 0
12 | 0.98603 | -0.26913 | 0 | 0
13 | 0.98611 | -0.26752 | 0.0047124 | 0.001181
14 | 0.9859 | -0.27152 | 0.0075228 | 0.0018854
15 | 0.98622 | -0.26527 | 0.0083383 | 0.0020898
16 | 0.99026 | -0.18687 | 0.036771 | 0.0092156
17 | 0.99598 | -0.076786 | 0.051637 | 0.012942
18 | 0.99928 | -0.013661 | 0 | 0
19 | 1 | 0 | -0.3806 | -0.096331
20 | 0.99697 | -0.057748 | 0 | 0
21 | 0.98722 | -0.24588 | 0.021251 | 0.0053261
22 | 0.98763 | -0.23799 | 0.0088885 | 0.0022277
23 | 0.99234 | -0.14675 | 0 | 0
24 | 0.99207 | -0.15189 | 0.054766 | 0.013726
25 | 0.98977 | -0.19644 | 0 | 0
26 | 0.98797 | -0.23138 | 0 | 0
27 | 0.98789 | -0.23289 | 0.011669 | 0.0029245
28 | 0.98818 | -0.22734 | 0 | 0
29 | 0.98798 | -0.23119 | 0.0089151 | 0.0022343
30 | 0.98779 | -0.23477 | 0.054825 | 0.01374
31 | 0.98769 | -0.23679 | 0.020061 | 0.0050279
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012138 | -0.0030421 | 0.012139 | 0.0030423 | 3.9034e-07 | 2.1015e-07 | 0.018307 | 0.018307 | 0.018307 | 0.98663 | -0.25742 | 0.98666 | -0.25674 | 5.0293
1 | -0.012139 | -0.0030423 | 0.012142 | 0.0030441 | 3.3009e-06 | 1.777e-06 | 0.018307 | 0.018306 | 0.018307 | 0.98666 | -0.25674 | 0.98696 | -0.25103 | 5.0293
2 | -0.012142 | -0.0030441 | 0.012145 | 0.0030457 | 2.9405e-06 | 1.5828e-06 | 0.018306 | 0.018306 | 0.018306 | 0.98696 | -0.25103 | 0.98722 | -0.24595 | 5.0292
3 | 0.0070199 | 0.0017594 | -0.0070197 | -0.0017593 | 2.309e-07 | 7.7551e-08 | 0.010584 | 0.010585 | 0.010585 | 0.98689 | -0.25227 | 0.98686 | -0.25297 | 2.9078
4 | -0.027609 | -0.0069245 | 0.027628 | 0.0069366 | 1.9358e-05 | 1.2008e-05 | 0.04163 | 0.04163 | 0.04163 | 0.98689 | -0.25227 | 0.98765 | -0.23758 | 11.4368
5 | 0.020589 | 0.0051652 | -0.020579 | -0.0051592 | 9.8811e-06 | 5.9747e-06 | 0.031046 | 0.031046 | 0.031046 | 0.98689 | -0.25227 | 0.98638 | -0.26235 | 8.529
6 | 0.048792 | 0.012238 | -0.048773 | -0.012226 | 1.9475e-05 | 1.2341e-05 | 0.073515 | 0.073515 | 0.073515 | 0.98765 | -0.23758 | 0.98722 | -0.24595 | 20.1965
7 | -0.076421 | -0.019174 | 0.07661 | 0.019295 | 0.00018987 | 0.00012103 | 0.11514 | 0.11514 | 0.11514 | 0.98765 | -0.23758 | 0.99033 | -0.18561 | 31.6332
8 | 0.020579 | 0.0051592 | -0.020576 | -0.0051575 | 2.8678e-06 | 1.7341e-06 | 0.031046 | 0.031046 | 0.031046 | 0.98638 | -0.26235 | 0.98622 | -0.26527 | 8.529
9 | -0.14408 | -0.036362 | 0.14436 | 0.036536 | 0.00027278 | 0.00017377 | 0.21584 | 0.21584 | 0.21584 | 0.99375 | -0.11962 | 0.9958 | -0.080169 | 29.6481
10 | 0.030343 | 0.0076207 | -0.030299 | -0.0075937 | 4.3409e-05 | 2.7057e-05 | 0.04544 | 0.04544 | 0.04544 | 0.99375 | -0.11962 | 0.9922 | -0.14965 | 12.4836
11 | 0.11374 | 0.028741 | -0.11338 | -0.028512 | 0.00035859 | 0.00022907 | 0.1704 | 0.1704 | 0.1704 | 0.99375 | -0.11962 | 0.99033 | -0.18561 | 46.8126
12 | -0.14436 | -0.036536 | 0.14438 | 0.036551 | 2.3449e-05 | 1.485e-05 | 0.21584 | 0.21584 | 0.21584 | 0.9958 | -0.080169 | 0.99598 | -0.076786 | 19.7653
13 | 0.036773 | 0.009217 | -0.036771 | -0.0092156 | 2.2072e-06 | 1.3878e-06 | 0.055253 | 0.055253 | 0.055253 | 0.99033 | -0.18561 | 0.99026 | -0.18687 | 15.1795
14 | -0.0075237 | -0.0018857 | 0.0075243 | 0.0018859 | 5.7566e-07 | 2.1652e-07 | 0.011354 | 0.011354 | 0.011354 | 0.98603 | -0.26913 | 0.98611 | -0.26752 | 3.1192
15 | 0.0075237 | 0.0018857 | -0.0075228 | -0.0018854 | 8.5811e-07 | 3.2281e-07 | 0.011354 | 0.011354 | 0.011354 | 0.98603 | -0.26913 | 0.9859 | -0.27152 | 3.1193
16 | -0.012237 | -0.003067 | 0.012238 | 0.0030677 | 1.3123e-06 | 7.0893e-07 | 0.018465 | 0.018465 | 0.018465 | 0.98611 | -0.26752 | 0.98622 | -0.26527 | 5.0728
17 | -0.19602 | -0.049492 | 0.1962 | 0.049606 | 0.00017897 | 0.00011389 | 0.29298 | 0.29298 | 0.29298 | 0.99598 | -0.076786 | 0.99697 | -0.057748 | 26.8301
18 | -0.3787 | -0.096172 | 0.37895 | 0.096331 | 0.00024915 | 0.00015921 | 0.56437 | 0.56437 | 0.56437 | 0.99928 | -0.013661 | 1 | 0 | 51.6818
19 | 0.3787 | 0.096172 | -0.3779 | -0.095659 | 0.00080165 | 0.00051226 | 0.56437 | 0.56437 | 0.56437 | 0.99928 | -0.013661 | 0.99697 | -0.057748 | 51.6818
20 | 0.1817 | 0.046053 | -0.18093 | -0.045559 | 0.00077346 | 0.00049356 | 0.27138 | 0.27138 | 0.27138 | 0.99697 | -0.057748 | 0.99234 | -0.14675 | 37.2777
21 | -0.021251 | -0.0053261 | 0.021259 | 0.0053309 | 7.9838e-06 | 4.8442e-06 | 0.032032 | 0.032031 | 0.032032 | 0.98722 | -0.24588 | 0.98763 | -0.23799 | 8.7999
22 | -0.030148 | -0.0075586 | 0.030149 | 0.0075597 | 1.7282e-06 | 1.0775e-06 | 0.045423 | 0.045423 | 0.045423 | 0.98763 | -0.23799 | 0.98769 | -0.23679 | 12.4789
23 | 0.054779 | 0.013734 | -0.054766 | -0.013726 | 1.3418e-05 | 8.5193e-06 | 0.082144 | 0.082144 | 0.082144 | 0.99234 | -0.14675 | 0.99207 | -0.15189 | 22.567
24 | 0.12615 | 0.031825 | -0.12585 | -0.031634 | 0.00029937 | 0.00019131 | 0.18924 | 0.18924 | 0.18924 | 0.99234 | -0.14675 | 0.98977 | -0.19644 | 51.9884
25 | 0.066614 | 0.016741 | -0.066516 | -0.016679 | 9.8111e-05 | 6.2457e-05 | 0.10016 | 0.10016 | 0.10016 | 0.98977 | -0.19644 | 0.98818 | -0.22734 | 27.5175
26 | 0.059238 | 0.014893 | -0.059139 | -0.01483 | 9.8126e-05 | 6.2378e-05 | 0.089074 | 0.089074 | 0.089074 | 0.98977 | -0.19644 | 0.98798 | -0.23119 | 24.471
27 | 0.01167 | 0.0029249 | -0.011669 | -0.0029245 | 8.4126e-07 | 4.4542e-07 | 0.017576 | 0.017576 | 0.017576 | 0.98797 | -0.23138 | 0.98789 | -0.23289 | 4.8286
28 | -0.01167 | -0.0029249 | 0.011672 | 0.0029261 | 2.245e-06 | 1.1886e-06 | 0.017576 | 0.017576 | 0.017576 | 0.98797 | -0.23138 | 0.98818 | -0.22734 | 4.8286
29 | 0.054844 | 0.013753 | -0.054825 | -0.01374 | 1.9424e-05 | 1.2334e-05 | 0.082588 | 0.082588 | 0.082588 | 0.98818 | -0.22734 | 0.98779 | -0.23477 | 22.689
30 | 0.050224 | 0.012596 | -0.050211 | -0.012588 | 1.3402e-05 | 8.4971e-06 | 0.075647 | 0.075647 | 0.075647 | 0.98798 | -0.23119 | 0.98769 | -0.23679 | 20.7822

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4322 | 0.10926

## res_load
| p_mw | q_mvar
0 | 0.012138 | 0.0030421
1 | 0.0070197 | 0.0017593
2 | 0.036628 | 0.0091798
3 | 0.030299 | 0.0075937
4 | 0.0047124 | 0.001181
5 | 0.0075228 | 0.0018854
6 | 0.0083383 | 0.0020898
7 | 0.036771 | 0.0092156
8 | 0.051637 | 0.012942
9 | 0.051602 | 0.012933
10 | 0.021251 | 0.0053261
11 | 0.0088885 | 0.0022277
12 | 0.054766 | 0.013726
13 | 0.011669 | 0.0029245
14 | 0.0089151 | 0.0022343
15 | 0.054825 | 0.01374
16 | 0.020061 | 0.0050279

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1