## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-58_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-58_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-58_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-58_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1630-58_0_5_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1630-58_0_5_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1630-58_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1630-58_0_5_node_29 | 0.4 | n |  | TRUE
8 | bus_LV_1630-58_0_5_node_56 | 0.4 | n |  | TRUE
9 | bus_LV_1630-58_0_5_node_30 | 0.4 | n |  | TRUE
10 | bus_LV_1630-58_0_5_node_36 | 0.4 | n |  | TRUE
11 | bus_LV_1630-58_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1630-58_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1630-58_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1630-58_0_5_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1630-58_0_5_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1630-58_0_5_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1630-58_0_5_node_46 | 0.4 | n |  | TRUE
18 | bus_LV_1630-58_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1630-58_0_5_node_47 | 0.4 | n |  | TRUE
20 | bus_LV_1630-58_0_5_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1630-58_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1630-58_0_5_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1630-58_0_5_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1630-58_0_5_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1630-58_0_5_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_1630-58_0_5_node_122 | 0.4 | n |  | TRUE
27 | bus_LV_1630-58_0_5_node_44 | 0.4 | n |  | TRUE
28 | bus_LV_1630-58_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1630-58_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1630-58_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1630-58_0_5_node_154 | 0.4 | n |  | TRUE
32 | bus_LV_1630-58_0_5_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_1630-58_0_5_node_123 | 0.4 | n |  | TRUE
34 | bus_LV_1630-58_0_5_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_1630-58_0_5_node_131 | 0.4 | n |  | TRUE
36 | bus_LV_1630-58_0_5_node_130 | 0.4 | n |  | TRUE
37 | bus_LV_1630-58_0_5_node_120 | 0.4 | n |  | TRUE
38 | bus_LV_1630-58_0_5_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_1630-58_0_5_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_1630-58_0_5_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_1630-58_0_5_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_1630-58_0_5_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1630-58_0_5_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_1630-58_0_5_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_1630-58_0_5_node_52 | 0.4 | n |  | TRUE
46 | bus_LV_1630-58_0_5_node_48 | 0.4 | n |  | TRUE
47 | bus_LV_1630-58_0_5_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_1630-58_0_5_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_1630-58_0_5_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_1630-58_0_5_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_1630-58_0_5_node_58 | 0.4 | n |  | TRUE
52 | bus_LV_1630-58_0_5_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_1630-58_0_5_node_141 | 0.4 | n |  | TRUE
54 | bus_LV_1630-58_0_5_node_140 | 0.4 | n |  | TRUE
55 | bus_LV_1630-58_0_5_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_1630-58_0_5_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_1630-58_0_5_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_1630-58_0_5_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_1630-58_0_5_node_41 | 0.4 | n |  | TRUE
60 | bus_LV_1630-58_0_5_node_155 | 0.4 | n |  | TRUE
61 | bus_LV_1630-58_0_5_node_121 | 0.4 | n |  | TRUE
62 | bus_LV_1630-58_0_5_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_1630-58_0_5_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_1630-58_0_5_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_1630-58_0_5_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_1630-58_0_5_node_145 | 0.4 | n |  | TRUE
67 | bus_LV_1630-58_0_5_node_144 | 0.4 | n |  | TRUE
68 | bus_LV_1630-58_0_5_node_59 | 0.4 | n |  | TRUE
69 | bus_LV_1630-58_0_5_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_1630-58_0_5_node_61 | 0.4 | n |  | TRUE
71 | bus_LV_1630-58_0_5_node_151 | 0.4 | n |  | TRUE
72 | bus_LV_1630-58_0_5_node_149 | 0.4 | n |  | TRUE
73 | bus_LV_1630-58_0_5_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_1630-58_0_5_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_1630-58_0_5_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_1630-58_0_5_node_78 | 0.4 | n |  | TRUE
77 | bus_LV_1630-58_0_5_node_71 | 0.4 | n |  | TRUE
78 | bus_LV_1630-58_0_5_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_1630-58_0_5_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_1630-58_0_5_node_65 | 0.4 | n |  | TRUE
81 | bus_LV_1630-58_0_5_node_81 | 0.4 | n |  | TRUE
82 | bus_LV_1630-58_0_5_node_79 | 0.4 | n |  | TRUE
83 | bus_LV_1630-58_0_5_node_80 | 0.4 | n |  | TRUE
84 | bus_LV_1630-58_0_5_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_1630-58_0_5_node_118 | 0.4 | n |  | TRUE
86 | bus_LV_1630-58_0_5_node_89 | 0.4 | n |  | TRUE
87 | bus_LV_1630-58_0_5_node_90 | 0.4 | n |  | TRUE
88 | bus_LV_1630-58_0_5_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_1630-58_0_5_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_1630-58_0_5_node_76 | 0.4 | n |  | TRUE
91 | bus_LV_1630-58_0_5_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_1630-58_0_5_node_146 | 0.4 | n |  | TRUE
93 | bus_LV_1630-58_0_5_node_119 | 0.4 | n |  | TRUE
94 | bus_LV_1630-58_0_5_node_66 | 0.4 | n |  | TRUE
95 | bus_LV_1630-58_0_5_node_67 | 0.4 | n |  | TRUE
96 | bus_LV_1630-58_0_5_node_68 | 0.4 | n |  | TRUE
97 | bus_LV_1630-58_0_5_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_1630-58_0_5_node_100 | 0.4 | n |  | TRUE
99 | bus_LV_1630-58_0_5_node_102 | 0.4 | n |  | TRUE
100 | bus_LV_1630-58_0_5_node_99 | 0.4 | n |  | TRUE
101 | bus_LV_1630-58_0_5_node_147 | 0.4 | n |  | TRUE
102 | bus_LV_1630-58_0_5_node_152 | 0.4 | n |  | TRUE
103 | bus_LV_1630-58_0_5_node_139 | 0.4 | n |  | TRUE
104 | bus_LV_1630-58_0_5_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_1630-58_0_5_node_83 | 0.4 | n |  | TRUE
106 | bus_LV_1630-58_0_5_node_84 | 0.4 | n |  | TRUE
107 | bus_LV_1630-58_0_5_node_85 | 0.4 | n |  | TRUE
108 | bus_LV_1630-58_0_5_node_86 | 0.4 | n |  | TRUE
109 | bus_LV_1630-58_0_5_node_87 | 0.4 | n |  | TRUE
110 | bus_LV_1630-58_0_5_node_91 | 0.4 | n |  | TRUE
111 | bus_LV_1630-58_0_5_node_88 | 0.4 | n |  | TRUE
112 | bus_LV_1630-58_0_5_node_133 | 0.4 | n |  | TRUE
113 | bus_LV_1630-58_0_5_node_128 | 0.4 | n |  | TRUE
114 | bus_LV_1630-58_0_5_node_92 | 0.4 | n |  | TRUE
115 | bus_LV_1630-58_0_5_node_126 | 0.4 | n |  | TRUE
116 | bus_LV_1630-58_0_5_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_1630-58_0_5_node_94 | 0.4 | n |  | TRUE
118 | bus_LV_1630-58_0_5_node_95 | 0.4 | n |  | TRUE
119 | bus_LV_1630-58_0_5_node_96 | 0.4 | n |  | TRUE
120 | bus_LV_1630-58_0_5_node_97 | 0.4 | n |  | TRUE
121 | bus_LV_1630-58_0_5_node_101 | 0.4 | n |  | TRUE
122 | bus_LV_1630-58_0_5_node_98 | 0.4 | n |  | TRUE
123 | bus_LV_1630-58_0_5_node_103 | 0.4 | n |  | TRUE
124 | bus_LV_1630-58_0_5_node_104 | 0.4 | n |  | TRUE
125 | bus_LV_1630-58_0_5_node_105 | 0.4 | n |  | TRUE
126 | bus_LV_1630-58_0_5_node_108 | 0.4 | n |  | TRUE
127 | bus_LV_1630-58_0_5_node_109 | 0.4 | n |  | TRUE
128 | bus_LV_1630-58_0_5_node_106 | 0.4 | n |  | TRUE
129 | bus_LV_1630-58_0_5_node_112 | 0.4 | n |  | TRUE
130 | bus_LV_1630-58_0_5_node_116 | 0.4 | n |  | TRUE
131 | bus_LV_1630-58_0_5_node_117 | 0.4 | n |  | TRUE
132 | bus_LV_1630-58_0_5_node_107 | 0.4 | n |  | TRUE
133 | bus_LV_1630-58_0_5_node_114 | 0.4 | n |  | TRUE
134 | bus_LV_1630-58_0_5_node_110 | 0.4 | n |  | TRUE
135 | bus_LV_1630-58_0_5_node_115 | 0.4 | n |  | TRUE
136 | bus_LV_1630-58_0_5_node_153 | 0.4 | n |  | TRUE
137 | bus_LV_1630-58_0_5_node_111 | 0.4 | n |  | TRUE
138 | bus_LV_1630-58_0_5_node_137 | 0.4 | n |  | TRUE
139 | bus_LV_1630-58_0_5_node_136 | 0.4 | n |  | TRUE
140 | bus_LV_1630-58_0_5_node_138 | 0.4 | n |  | TRUE
141 | bus_LV_1630-58_0_5_node_132 | 0.4 | n |  | TRUE
142 | bus_LV_1630-58_0_5_node_148 | 0.4 | n |  | TRUE
143 | bus_LV_1630-58_0_5_node_134 | 0.4 | n |  | TRUE
144 | bus_LV_1630-58_0_5_node_129 | 0.4 | n |  | TRUE
145 | bus_LV_1630-58_0_5_node_124 | 0.4 | n |  | TRUE
146 | bus_LV_1630-58_0_5_node_125 | 0.4 | n |  | TRUE
147 | bus_LV_1630-58_0_5_node_127 | 0.4 | n |  | TRUE
148 | bus_LV_1630-58_0_5_node_143 | 0.4 | n |  | TRUE
149 | bus_MV_225_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-58_0_5_load_0 | 0 | 0.0027287 | 0.00068389 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-58_0_5_load_6 | 4 | 0.013145 | 0.0032945 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-58_0_5_load_3 | 5 | 0.0054186 | 0.001358 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-58_0_5_load_29 | 7 | 0.0019125 | 0.00047931 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-58_0_5_load_56 | 8 | 0.019913 | 0.0049906 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-58_0_5_load_30 | 9 | 0.00078611 | 0.00019702 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-58_0_5_load_7 | 11 | 0.0013659 | 0.00034233 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-58_0_5_load_8 | 12 | 0.0024251 | 0.00060779 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-58_0_5_load_11 | 15 | 0.0020341 | 0.00050979 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-58_0_5_load_12 | 18 | 0.002472 | 0.00061953 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-58_0_5_load_47 | 19 | 0.0023297 | 0.00058387 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-58_0_5_load_13 | 20 | 0.01074 | 0.0026916 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-58_0_5_load_15 | 21 | 0.0022395 | 0.00056128 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-58_0_5_load_16 | 22 | 0.0023642 | 0.00059253 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-58_0_5_load_122 | 26 | 0.0014239 | 0.00035687 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-58_0_5_load_44 | 27 | 0.0047633 | 0.0011938 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-58_0_5_load_154 | 31 | 0.0057277 | 0.0014355 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-58_0_5_load_33 | 34 | 0.0074291 | 0.0018619 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-58_0_5_load_130 | 36 | 0.0019229 | 0.00048193 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-58_0_5_load_120 | 37 | 0.0032524 | 0.00081513 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-58_0_5_load_23 | 38 | 0.0074235 | 0.0018605 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-58_0_5_load_24 | 39 | 0.0016964 | 0.00042516 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-58_0_5_load_26 | 41 | 0.00066298 | 0.00016616 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-58_0_5_load_27 | 42 | 0.0018593 | 0.00046598 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-58_0_5_load_28 | 43 | 0.0062191 | 0.0015586 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-58_0_5_load_52 | 45 | 0.00083029 | 0.00020809 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-58_0_5_load_48 | 46 | 0.009919 | 0.0024859 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-58_0_5_load_31 | 50 | 0.0027638 | 0.00069267 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-58_0_5_load_35 | 52 | 0.0022247 | 0.00055755 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-58_0_5_load_141 | 53 | 0.002741 | 0.00068695 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-58_0_5_load_140 | 54 | 0.0060038 | 0.0015047 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1630-58_0_5_load_37 | 55 | 0.0022067 | 0.00055306 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1630-58_0_5_load_38 | 56 | 0.00074019 | 0.00018551 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1630-58_0_5_load_40 | 58 | 0.013476 | 0.0033774 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1630-58_0_5_load_155 | 60 | 0.0037144 | 0.00093091 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1630-58_0_5_load_54 | 62 | 0.0014088 | 0.00035307 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1630-58_0_5_load_55 | 65 | 0.018033 | 0.0045195 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1630-58_0_5_load_145 | 66 | 0.0022774 | 0.00057077 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1630-58_0_5_load_59 | 68 | 0.0012017 | 0.00030117 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1630-58_0_5_load_60 | 69 | 0.00022874 | 5.7327e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1630-58_0_5_load_151 | 71 | 0.00043665 | 0.00010943 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1630-58_0_5_load_149 | 72 | 0.00024722 | 6.1959e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1630-58_0_5_load_62 | 74 | 0.00036858 | 9.2374e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1630-58_0_5_load_71 | 77 | 0.00035346 | 8.8586e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1630-58_0_5_load_65 | 80 | 0.00057433 | 0.00014394 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1630-58_0_5_load_81 | 81 | 0.00014728 | 3.6912e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1630-58_0_5_load_79 | 82 | 0.00015148 | 3.7965e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1630-58_0_5_load_89 | 86 | 0.00040128 | 0.00010057 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1630-58_0_5_load_90 | 87 | 0.000203 | 5.0878e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1630-58_0_5_load_73 | 88 | 0.00036647 | 9.1846e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1630-58_0_5_load_74 | 89 | 0.00015785 | 3.956e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1630-58_0_5_load_77 | 91 | 0.00029117 | 7.2973e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1630-58_0_5_load_146 | 92 | 0.00015721 | 3.9402e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1630-58_0_5_load_66 | 94 | 0.00018501 | 4.6368e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1630-58_0_5_load_70 | 97 | 0.00021253 | 5.3264e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1630-58_0_5_load_100 | 98 | 0.0040722 | 0.0010206 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1630-58_0_5_load_99 | 100 | 0.0054956 | 0.0013773 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1630-58_0_5_load_147 | 101 | 0.0004228 | 0.00010596 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1630-58_0_5_load_82 | 104 | 0.00018951 | 4.7497e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1630-58_0_5_load_83 | 105 | 0.00020492 | 5.1357e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1630-58_0_5_load_85 | 107 | 0.00049311 | 0.00012358 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1630-58_0_5_load_86 | 108 | 0.0004826 | 0.00012095 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1630-58_0_5_load_87 | 109 | 0.00040442 | 0.00010136 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1630-58_0_5_load_91 | 110 | 0.00039738 | 9.9592e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1630-58_0_5_load_133 | 112 | 0.00035889 | 8.9947e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1630-58_0_5_load_128 | 113 | 0.004994 | 0.0012516 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1630-58_0_5_load_92 | 114 | 0.00032217 | 8.0743e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1630-58_0_5_load_93 | 116 | 0.00016941 | 4.2457e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1630-58_0_5_load_95 | 118 | 0.00016703 | 4.1861e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1630-58_0_5_load_97 | 120 | 0.00054809 | 0.00013736 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1630-58_0_5_load_101 | 121 | 0.00016257 | 4.0744e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1630-58_0_5_load_98 | 122 | 0.00038428 | 9.631e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1630-58_0_5_load_103 | 123 | 0.0038699 | 0.00096988 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1630-58_0_5_load_109 | 127 | 0.0037366 | 0.00093648 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1630-58_0_5_load_106 | 128 | 0.0070999 | 0.0017794 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1630-58_0_5_load_116 | 130 | 0.0020426 | 0.00051193 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1630-58_0_5_load_117 | 131 | 0.0054405 | 0.0013635 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1630-58_0_5_load_107 | 132 | 0.0056683 | 0.0014206 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1630-58_0_5_load_114 | 133 | 0.00346 | 0.00086715 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1630-58_0_5_load_110 | 134 | 0.0027686 | 0.00069387 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1630-58_0_5_load_115 | 135 | 0.0035024 | 0.00087778 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1630-58_0_5_load_153 | 136 | 0.0019349 | 0.00048494 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1630-58_0_5_load_111 | 137 | 0.0028312 | 0.00070957 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1630-58_0_5_load_137 | 138 | 0.0013304 | 0.00033342 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1630-58_0_5_load_138 | 140 | 0.002089 | 0.00052355 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1630-58_0_5_load_148 | 142 | 0.0019154 | 0.00048005 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1630-58_0_5_load_134 | 143 | 0.0017267 | 0.00043276 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1630-58_0_5_load_129 | 144 | 0.0027711 | 0.00069452 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1630-58_0_5_load_124 | 145 | 0.0066129 | 0.0016573 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1630-58_0_5_load_125 | 146 | 0.0041021 | 0.0010281 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1630-58_0_5_load_127 | 147 | 0.003917 | 0.00098171 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1630-58_0_5_load_143 | 148 | 0.0022331 | 0.00055966 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-58_0_5_line_0 |  | 0 | 1 | 0.0024243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-58_0_5_line_1 |  | 0 | 2 | 0.012271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-58_0_5_line_2 |  | 1 | 3 | 0.021625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-58_0_5_line_3 |  | 2 | 4 | 0.008113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-58_0_5_line_4 |  | 2 | 5 | 0.012544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-58_0_5_line_5 |  | 3 | 6 | 0.069969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1630-58_0_5_line_6 |  | 3 | 7 | 0.012882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1630-58_0_5_line_7 |  | 6 | 8 | 0.01472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1630-58_0_5_line_8 |  | 7 | 9 | 0.010355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1630-58_0_5_line_9 |  | 8 | 10 | 0.026956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1630-58_0_5_line_10 |  | 9 | 50 | 0.010998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1630-58_0_5_line_11 |  | 10 | 51 | 0.036004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-58_0_5_line_12 |  | 10 | 32 | 0.038659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_1630-58_0_5_line_13 |  | 11 | 12 | 0.015323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-58_0_5_line_14 |  | 11 | 13 | 0.0062929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-58_0_5_line_15 |  | 12 | 14 | 0.010474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-58_0_5_line_16 |  | 13 | 15 | 0.008589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-58_0_5_line_17 |  | 14 | 16 | 0.07386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-58_0_5_line_18 |  | 15 | 17 | 0.0077687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-58_0_5_line_19 |  | 16 | 18 | 0.05599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-58_0_5_line_20 |  | 17 | 19 | 0.0089268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-58_0_5_line_21 |  | 18 | 20 | 0.001542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-58_0_5_line_22 |  | 19 | 62 | 0.010851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-58_0_5_line_23 |  | 20 | 21 | 0.0088839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-58_0_5_line_24 |  | 22 | 23 | 0.079193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-58_0_5_line_25 |  | 23 | 24 | 0.010308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-58_0_5_line_26 |  | 24 | 27 | 0.048445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-58_0_5_line_27 |  | 24 | 25 | 0.05455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-58_0_5_line_28 |  | 25 | 26 | 0.12543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-58_0_5_line_29 |  | 26 | 30 | 0.06669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1630-58_0_5_line_30 |  | 27 | 37 | 0.10801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-58_0_5_line_31 |  | 28 | 29 | 0.023514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_1630-58_0_5_line_32 |  | 28 | 30 | 0.11215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1630-58_0_5_line_33 |  | 29 | 31 | 0.036285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-58_0_5_line_34 |  | 29 | 32 | 0.14968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_1630-58_0_5_line_35 |  | 30 | 33 | 0.034238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-58_0_5_line_36 |  | 32 | 34 | 0.0046519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-58_0_5_line_37 |  | 33 | 35 | 0.020897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-58_0_5_line_38 |  | 33 | 36 | 0.011535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-58_0_5_line_39 |  | 35 | 133 | 0.096361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-58_0_5_line_40 |  | 36 | 144 | 0.016382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-58_0_5_line_41 |  | 37 | 61 | 0.027635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-58_0_5_line_42 |  | 38 | 39 | 0.015611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-58_0_5_line_43 |  | 38 | 40 | 0.022624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-58_0_5_line_44 |  | 39 | 41 | 0.008013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1630-58_0_5_line_45 |  | 40 | 42 | 0.0071244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1630-58_0_5_line_46 |  | 40 | 43 | 0.011897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1630-58_0_5_line_47 |  | 41 | 44 | 0.018466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1630-58_0_5_line_48 |  | 44 | 45 | 0.020218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1630-58_0_5_line_49 |  | 44 | 46 | 0.020794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1630-58_0_5_line_50 |  | 45 | 59 | 0.015928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_1630-58_0_5_line_51 |  | 46 | 64 | 0.012765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1630-58_0_5_line_52 |  | 47 | 48 | 0.004709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1630-58_0_5_line_53 |  | 47 | 49 | 0.014803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1630-58_0_5_line_54 |  | 48 | 60 | 0.013211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1630-58_0_5_line_55 |  | 48 | 59 | 0.018882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_1630-58_0_5_line_56 |  | 49 | 50 | 0.00077864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_1630-58_0_5_line_57 |  | 51 | 54 | 0.080855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1630-58_0_5_line_58 |  | 52 | 53 | 0.062246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1630-58_0_5_line_59 |  | 53 | 54 | 0.068465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1630-58_0_5_line_60 |  | 55 | 56 | 0.0088943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1630-58_0_5_line_61 |  | 55 | 57 | 0.017105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1630-58_0_5_line_62 |  | 57 | 58 | 0.024293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1630-58_0_5_line_63 |  | 57 | 59 | 0.011924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1630-58_0_5_line_64 |  | 61 | 141 | 0.090501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1630-58_0_5_line_65 |  | 62 | 63 | 0.032486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1630-58_0_5_line_66 |  | 63 | 65 | 0.056861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1630-58_0_5_line_67 |  | 63 | 64 | 0.00768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1630-58_0_5_line_68 |  | 65 | 66 | 0.017697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1630-58_0_5_line_69 |  | 66 | 67 | 0.0036005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1630-58_0_5_line_70 |  | 67 | 148 | 0.015098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1630-58_0_5_line_71 |  | 68 | 69 | 0.02915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1630-58_0_5_line_72 |  | 68 | 70 | 0.016432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1630-58_0_5_line_73 |  | 70 | 71 | 0.16286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1630-58_0_5_line_74 |  | 70 | 72 | 0.18749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1630-58_0_5_line_75 |  | 72 | 73 | 0.015012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1630-58_0_5_line_76 |  | 73 | 78 | 0.030178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1630-58_0_5_line_77 |  | 73 | 83 | 0.034054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1630-58_0_5_line_78 |  | 74 | 75 | 0.0073191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1630-58_0_5_line_79 |  | 74 | 76 | 0.10405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1630-58_0_5_line_80 |  | 75 | 79 | 0.033999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1630-58_0_5_line_81 |  | 75 | 80 | 0.10159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1630-58_0_5_line_82 |  | 76 | 81 | 0.014969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1630-58_0_5_line_83 |  | 76 | 82 | 0.016246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1630-58_0_5_line_84 |  | 77 | 78 | 0.018696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1630-58_0_5_line_85 |  | 78 | 95 | 0.087167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1630-58_0_5_line_86 |  | 79 | 84 | 0.071996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1630-58_0_5_line_87 |  | 80 | 85 | 0.011505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1630-58_0_5_line_88 |  | 82 | 83 | 0.013923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1630-58_0_5_line_89 |  | 84 | 91 | 0.026691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1630-58_0_5_line_90 |  | 84 | 88 | 0.021065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1630-58_0_5_line_91 |  | 85 | 93 | 0.016774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1630-58_0_5_line_92 |  | 86 | 87 | 0.025312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1630-58_0_5_line_93 |  | 87 | 108 | 0.0057455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1630-58_0_5_line_94 |  | 88 | 89 | 0.011384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1630-58_0_5_line_95 |  | 89 | 90 | 0.0076078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1630-58_0_5_line_96 |  | 90 | 92 | 0.007291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1630-58_0_5_line_97 |  | 93 | 101 | 0.020673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1630-58_0_5_line_98 |  | 94 | 95 | 0.0095585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1630-58_0_5_line_99 |  | 94 | 96 | 0.01284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1630-58_0_5_line_100 |  | 96 | 97 | 0.022097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1630-58_0_5_line_101 |  | 97 | 102 | 0.019635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1630-58_0_5_line_102 |  | 98 | 99 | 0.01204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1630-58_0_5_line_103 |  | 98 | 100 | 0.029827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1630-58_0_5_line_104 |  | 99 | 123 | 0.014946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1630-58_0_5_line_105 |  | 100 | 121 | 0.0076076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1630-58_0_5_line_106 |  | 102 | 103 | 0.067671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1630-58_0_5_line_107 |  | 103 | 138 | 0.07869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1630-58_0_5_line_108 |  | 104 | 105 | 0.037006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1630-58_0_5_line_109 |  | 105 | 106 | 0.057059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1630-58_0_5_line_110 |  | 106 | 107 | 0.051457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1630-58_0_5_line_111 |  | 106 | 108 | 0.016182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1630-58_0_5_line_112 |  | 106 | 109 | 0.016487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1630-58_0_5_line_113 |  | 109 | 110 | 4.5514e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1630-58_0_5_line_114 |  | 110 | 114 | 0.01575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1630-58_0_5_line_115 |  | 111 | 112 | 0.076209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1630-58_0_5_line_116 |  | 111 | 113 | 0.009856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1630-58_0_5_line_117 |  | 113 | 115 | 0.076976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1630-58_0_5_line_118 |  | 114 | 116 | 0.011316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1630-58_0_5_line_119 |  | 115 | 145 | 0.016076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1630-58_0_5_line_120 |  | 116 | 117 | 0.015204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1630-58_0_5_line_121 |  | 117 | 118 | 0.017816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1630-58_0_5_line_122 |  | 117 | 119 | 0.057026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1630-58_0_5_line_123 |  | 118 | 120 | 0.0083834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1630-58_0_5_line_124 |  | 119 | 121 | 0.0086205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1630-58_0_5_line_125 |  | 120 | 122 | 0.024694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1630-58_0_5_line_126 |  | 123 | 124 | 0.030185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1630-58_0_5_line_127 |  | 124 | 125 | 0.024973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1630-58_0_5_line_128 |  | 125 | 126 | 0.02041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1630-58_0_5_line_129 |  | 125 | 127 | 0.019278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1630-58_0_5_line_130 |  | 125 | 128 | 0.011494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1630-58_0_5_line_131 |  | 126 | 129 | 0.004049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1630-58_0_5_line_132 |  | 126 | 130 | 0.026696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1630-58_0_5_line_133 |  | 127 | 131 | 0.014021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1630-58_0_5_line_134 |  | 128 | 132 | 0.013648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1630-58_0_5_line_135 |  | 129 | 133 | 0.035631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1630-58_0_5_line_136 |  | 129 | 134 | 0.013406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1630-58_0_5_line_137 |  | 130 | 135 | 0.0068682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1630-58_0_5_line_138 |  | 131 | 136 | 0.14533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1630-58_0_5_line_139 |  | 134 | 137 | 0.018255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1630-58_0_5_line_140 |  | 136 | 140 | 0.081095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1630-58_0_5_line_141 |  | 138 | 139 | 0.036126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1630-58_0_5_line_142 |  | 139 | 140 | 0.037896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1630-58_0_5_line_143 |  | 139 | 143 | 0.036841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1630-58_0_5_line_144 |  | 141 | 142 | 0.031582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1630-58_0_5_line_145 |  | 144 | 147 | 0.041344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1630-58_0_5_line_146 |  | 145 | 146 | 0.0040249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1630-58_0_5_line_147 |  | 146 | 147 | 0.0014831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-58_0_5_trafo_122 | 0.63 MVA 20/0.4 kV | 149 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22
0 | 2724027.1983 | 1217966.2967 | 2724029.3993 | 1217967.3129
1 | 2724040.5399 | 1217972.457 | 2724029.3993 | 1217967.3129
2 | 2724020.9427 | 1217952.0331 | 2724016.9405 | 1217961.5461 | 2724027.1983 | 1217966.2967
3 | 2724040.5399 | 1217972.457 | 2724044.0764 | 1217965.1553
4 | 2724040.5399 | 1217972.457 | 2724033.8119 | 1217983.0442
5 | 2723993.2878 | 1218016.2634 | 2723995.0166 | 1218013.4639 | 2723996.2741 | 1218010.6879 | 2724016.9405 | 1217961.5461 | 2724020.9427 | 1217952.0331
6 | 2724020.9427 | 1217952.0331 | 2724025.9361 | 1217940.1587
7 | 2723993.2878 | 1218016.2634 | 2723993.8776 | 1218030.9713
8 | 2724025.9361 | 1217940.1587 | 2724029.9504 | 1217930.6129
9 | 2723998.1385 | 1218057.5189 | 2723995.9823 | 1218049.49 | 2723993.9425 | 1218032.5898 | 2723993.8776 | 1218030.9713
10 | 2724029.9504 | 1217930.6129 | 2724034.2137 | 1217920.4747
11 | 2724005.5534 | 1218092.6785 | 2724003.4171 | 1218077.133 | 2723998.1385 | 1218057.5189
12 | 2723998.1385 | 1218057.5189 | 2724007.0954 | 1218056.1931 | 2724012.834 | 1218054.8115 | 2724018.5869 | 1218054.9313 | 2724022.1133 | 1218056.2279 | 2724023.0285 | 1218052.3884 | 2724024.8738 | 1218054.9288 | 2724026.8714 | 1218061.8202
13 | 2724145.7273 | 1217767.7387 | 2724148.2744 | 1217752.6287
14 | 2724144.3455 | 1217773.8742 | 2724145.4315 | 1217769.4934 | 2724145.7273 | 1217767.7387
15 | 2724150.0153 | 1217742.3009 | 2724148.2744 | 1217752.6287
16 | 2724144.3455 | 1217773.8742 | 2724142.8746 | 1217777.413 | 2724140.596 | 1217781.5883
17 | 2724150.0153 | 1217742.3009 | 2724150.8505 | 1217737.5702 | 2724153.9287 | 1217719.2199 | 2724158.9356 | 1217700.1426 | 2724149.6592 | 1217697.1025 | 2724140.1952 | 1217715.8089
18 | 2724136.8745 | 1217788.4077 | 2724140.596 | 1217781.5883
19 | 2724140.1952 | 1217715.8089 | 2724133.3826 | 1217728.9884 | 2724106.7613 | 1217734.783 | 2724101.4738 | 1217747.648
20 | 2724136.8745 | 1217788.4077 | 2724131.974 | 1217795.0998 | 2724131.5597 | 1217795.5775
21 | 2724100.8877 | 1217749.0742 | 2724101.4738 | 1217747.648
22 | 2724124.4499 | 1217803.7743 | 2724131.5597 | 1217795.5775
23 | 2724100.8877 | 1217749.0742 | 2724097.5105 | 1217757.2913
24 | 2724249.5059 | 1217804.7234 | 2724246.6733 | 1217806.9216 | 2724244.0235 | 1217809.4572 | 2724232.0276 | 1217822.8621 | 2724227.0439 | 1217827.7175 | 2724222.0268 | 1217831.2602 | 2724217.7849 | 1217833.3178 | 2724198.3429 | 1217839.6731 | 2724186.7968 | 1217844.2583 | 2724183.926 | 1217845.802
25 | 2724249.5059 | 1217804.7234 | 2724251.0491 | 1217803.9104 | 2724252.871 | 1217803.2034 | 2724256.7299 | 1217802.0385 | 2724257.5597 | 1217804.48
26 | 2724257.5597 | 1217804.48 | 2724259.5632 | 1217807.4463 | 2724262.3646 | 1217809.6509 | 2724266.9795 | 1217810.8258 | 2724271.6546 | 1217810.2117 | 2724275.1548 | 1217808.4055 | 2724278.1191 | 1217805.3538 | 2724289.4543 | 1217788.6883 | 2724291.5387 | 1217785.9083
27 | 2724233.0217 | 1217853.0954 | 2724241.6443 | 1217838.3302 | 2724254.0842 | 1217810.2009 | 2724257.5597 | 1217804.48
28 | 2724233.0217 | 1217853.0954 | 2724224.7685 | 1217872.3606 | 2724213.1093 | 1217890.7431 | 2724211.9489 | 1217893.9548 | 2724210.0587 | 1217900.1202 | 2724208.3972 | 1217904.0553 | 2724200.1526 | 1217917.8165 | 2724197.3839 | 1217923.8746 | 2724195.3709 | 1217928.6475 | 2724193.5491 | 1217934.4474 | 2724192.5695 | 1217939.1863 | 2724192.3059 | 1217943.0839 | 2724192.4484 | 1217947.9017 | 2724193.6038 | 1217960.9471 | 2724193.5074 | 1217965.571 | 2724193.1608 | 1217968.8741
29 | 2724184.7282 | 1218034.0973 | 2724184.0082 | 1218027.844 | 2724183.531 | 1218023.0526 | 2724183.0382 | 1218016.1035 | 2724183.4173 | 1218011.0297 | 2724184.7879 | 1218006.4769 | 2724186.5098 | 1218001.0974 | 2724190.2442 | 1217990.9673 | 2724191.402 | 1217986.4212 | 2724192.6355 | 1217973.8815 | 2724193.1608 | 1217968.8741
30 | 2724291.5387 | 1217785.9083 | 2724345.2093 | 1217879.6409
31 | 2724101.3011 | 1218002.5901 | 2724099.9988 | 1218008.968 | 2724098.2417 | 1218025.878
32 | 2724101.3011 | 1218002.5901 | 2724106.9705 | 1218007.8123 | 2724112.5116 | 1218015.1779 | 2724117.3899 | 1218018.2819 | 2724128.123 | 1218014.4358 | 2724132.1335 | 1218012.9071 | 2724136.4202 | 1218013.4301 | 2724139.1851 | 1218015.2002 | 2724140.5909 | 1218024.9816 | 2724141.2148 | 1218031.1105 | 2724142.4313 | 1218034.672 | 2724156.4284 | 1218038.878 | 2724165.4307 | 1218036.8306 | 2724169.6474 | 1218034.8836 | 2724175.2746 | 1218039.2154 | 2724184.7282 | 1218034.0973
33 | 2724088.0062 | 1218060.5031 | 2724089.4215 | 1218054.5279 | 2724095.8325 | 1218038.7379 | 2724096.7072 | 1218035.3868 | 2724097.8525 | 1218029.6172 | 2724098.2417 | 1218025.878
34 | 2724098.2417 | 1218025.878 | 2724086.6876 | 1218025.4037 | 2724080.0176 | 1218029.2122 | 2724079.4527 | 1218023.5293 | 2724076.9426 | 1218023.3769 | 2724075.1098 | 1218024.9734 | 2724072.1323 | 1218030.1265 | 2724069.4094 | 1218035.0848 | 2724065.6337 | 1218036.6408 | 2724063.6514 | 1218035.5764 | 2724061.5674 | 1218032.4639 | 2724060.4484 | 1218026.7695 | 2724061.7668 | 1218021.4372 | 2724059.703 | 1218020.6381 | 2724059.0673 | 1218017.6225 | 2724057.0005 | 1218018.4245 | 2724055.4123 | 1218009.3733 | 2724053.0354 | 1218004.2865 | 2724043.5349 | 1218032.7999 | 2724030.071 | 1218048.5542 | 2724028.47 | 1218052.8798 | 2724027.7371 | 1218060.3593 | 2724026.8714 | 1218061.8202
35 | 2724206.8436 | 1218058.6108 | 2724198.2011 | 1218053.6045 | 2724193.715 | 1218050.2639 | 2724190.4829 | 1218046.5047 | 2724187.3704 | 1218041.3803 | 2724184.7282 | 1218034.0973
36 | 2724026.8714 | 1218061.8202 | 2724027.3302 | 1218066.4495
37 | 2724206.8436 | 1218058.6108 | 2724208.8162 | 1218052.1357 | 2724214.2061 | 1218052.9153 | 2724218.3533 | 1218052.4792 | 2724222.6278 | 1218051.0338
38 | 2724206.8436 | 1218058.6108 | 2724207.1053 | 1218065.7218 | 2724208.06 | 1218068.7329 | 2724208.4612 | 1218069.9279
39 | 2724222.6278 | 1218051.0338 | 2724227.2847 | 1218054.9229 | 2724233.4052 | 1218059.6208 | 2724242.634 | 1218066.0071 | 2724244.7234 | 1218068.486 | 2724246.0202 | 1218079.4772 | 2724248.9084 | 1218106.9923 | 2724249.2971 | 1218108.0123 | 2724250.1993 | 1218108.4426 | 2724251.3636 | 1218107.9554 | 2724251.6827 | 1218106.85 | 2724252.7373 | 1218103.9809 | 2724254.1259 | 1218100.3848 | 2724255.9504 | 1218099.9114 | 2724256.4915 | 1218102.0021 | 2724258.9683 | 1218114.2967 | 2724259.1222 | 1218115.666
40 | 2724213.2025 | 1218085.583 | 2724212.4707 | 1218081.8685 | 2724208.4612 | 1218069.9279
41 | 2724337.0797 | 1217905.0174 | 2724342.5322 | 1217898.8041 | 2724343.9056 | 1217891.9385 | 2724345.2093 | 1217879.6409
42 | 2724094.3747 | 1217888.9338 | 2724097.5682 | 1217883.6859 | 2724098.3194 | 1217881.889 | 2724098.2867 | 1217880.1759 | 2724097.6354 | 1217878.6389 | 2724096.5203 | 1217877.4926 | 2724094.6202 | 1217875.8104
43 | 2724082.614 | 1217908.2604 | 2724094.3747 | 1217888.9338
44 | 2724088.6207 | 1217870.4988 | 2724094.6202 | 1217875.8104
45 | 2724082.614 | 1217908.2604 | 2724083.0049 | 1217915.3741
46 | 2724082.614 | 1217908.2604 | 2724072.1708 | 1217902.5607
47 | 2724074.7948 | 1217858.2584 | 2724088.6207 | 1217870.4988
48 | 2724074.7948 | 1217858.2584 | 2724060.8884 | 1217872.9344
49 | 2724074.7948 | 1217858.2584 | 2724089.0968 | 1217843.1642
50 | 2724050.2706 | 1217884.7909 | 2724053.7161 | 1217880.5037 | 2724060.8884 | 1217872.9344
51 | 2724097.8769 | 1217833.8978 | 2724089.0968 | 1217843.1642
52 | 2724040.2592 | 1217906.1103 | 2724042.0809 | 1217901.767
53 | 2724034.5155 | 1217919.757 | 2724040.2592 | 1217906.1103
54 | 2724042.0809 | 1217901.767 | 2724029.7037 | 1217897.0501
55 | 2724042.0809 | 1217901.767 | 2724046.2026 | 1217891.9896 | 2724048.009 | 1217888.3799 | 2724050.2706 | 1217884.7909
56 | 2724034.5155 | 1217919.757 | 2724034.2137 | 1217920.4747
57 | 2724005.5534 | 1218092.6785 | 2724016.5497 | 1218172.7827
58 | 2724076.2987 | 1218249.3849 | 2724014.5907 | 1218241.2195
59 | 2724016.5497 | 1218172.7827 | 2724014.5907 | 1218241.2195
60 | 2724025.0238 | 1217872.9069 | 2724016.3178 | 1217871.0867
61 | 2724041.7663 | 1217876.4073 | 2724025.0238 | 1217872.9069
62 | 2724041.7663 | 1217876.4073 | 2724042.145 | 1217865.8847 | 2724044.5538 | 1217854.1367 | 2724045.4307 | 1217852.5973
63 | 2724041.7663 | 1217876.4073 | 2724050.2706 | 1217884.7909
64 | 2724252.5545 | 1217937.3575 | 2724337.0797 | 1217905.0174
65 | 2724103.1642 | 1217828.3146 | 2724124.4499 | 1217803.7743
66 | 2724103.1642 | 1217828.3146 | 2724092.141 | 1217822.7474 | 2724089.0755 | 1217821.9162 | 2724083.739 | 1217822.5723 | 2724074.2932 | 1217824.7551 | 2724068.4981 | 1217825.5573 | 2724062.5045 | 1217824.5873 | 2724048.946 | 1217819.9105
67 | 2724103.1642 | 1217828.3146 | 2724097.8769 | 1217833.8978
68 | 2724048.946 | 1217819.9105 | 2724032.2165 | 1217814.1398
69 | 2724028.8128 | 1217812.9658 | 2724032.2165 | 1217814.1398
70 | 2724028.8128 | 1217812.9658 | 2724030.7694 | 1217797.9953
71 | 2724750.2361 | 1218257.1958 | 2724742.0987 | 1218274.1387 | 2724740.2045 | 1218284.3185
72 | 2724733.8327 | 1218299.3967 | 2724739.78 | 1218286.6 | 2724740.2045 | 1218284.3185
73 | 2724733.8327 | 1218299.3967 | 2724790.1403 | 1218452.2181
74 | 2724547.216 | 1218317.474 | 2724733.8327 | 1218299.3967
75 | 2724547.216 | 1218317.474 | 2724532.4235 | 1218314.6737
76 | 2724539.1535 | 1218285.4915 | 2724537.6514 | 1218289.0629 | 2724535.6996 | 1218293.8036 | 2724534.218 | 1218299.2992 | 2724533.505 | 1218303.9879 | 2724532.9531 | 1218308.9581 | 2724532.4235 | 1218314.6737
77 | 2724532.5014 | 1218348.7021 | 2724533.0282 | 1218336.5814 | 2724532.4235 | 1218314.6737
78 | 2724441.6201 | 1218452.9075 | 2724447.1989 | 1218449.7104 | 2724447.6256 | 1218448.9304
79 | 2724447.6256 | 1218448.9304 | 2724523.0588 | 1218377.2605
80 | 2724457.3051 | 1218483.0922 | 2724441.6201 | 1218452.9075
81 | 2724441.6201 | 1218452.9075 | 2724395.3809 | 1218363.9499 | 2724394.8758 | 1218362.7127
82 | 2724523.0588 | 1218377.2605 | 2724527.5285 | 1218378.8218 | 2724529.3506 | 1218379.9163 | 2724530.6486 | 1218381.7449 | 2724531.5942 | 1218384.0887 | 2724532.1399 | 1218387.4027
83 | 2724523.0588 | 1218377.2605 | 2724524.184 | 1218373.5589 | 2724528.831 | 1218362.0875
84 | 2724539.1535 | 1218285.4915 | 2724547.7324 | 1218289.5184 | 2724544.2729 | 1218298.0632
85 | 2724539.1535 | 1218285.4915 | 2724546.0565 | 1218273.8155 | 2724548.257 | 1218270.2475 | 2724542.9398 | 1218261.6519 | 2724541.7548 | 1218258.0465 | 2724541.1446 | 1218252.0068 | 2724540.6748 | 1218237.808 | 2724539.3294 | 1218234.6107 | 2724537.4458 | 1218232.1027 | 2724534.3756 | 1218229.6922 | 2724520.4236 | 1218224.4521 | 2724516.8604 | 1218221.6532 | 2724512.8553 | 1218218.2001
86 | 2724457.3051 | 1218483.0922 | 2724529.2942 | 1218482.0732
87 | 2724390.5271 | 1218352.0615 | 2724394.8758 | 1218362.7127
88 | 2724532.5014 | 1218348.7021 | 2724531.1989 | 1218355.4357 | 2724529.8121 | 1218359.6656 | 2724528.831 | 1218362.0875
89 | 2724529.2942 | 1218482.0732 | 2724539.667 | 1218506.676
90 | 2724529.2942 | 1218482.0732 | 2724532.6372 | 1218480.8755 | 2724534.7202 | 1218478.9286 | 2724540.9832 | 1218468.0732 | 2724541.9163 | 1218466.1585
91 | 2724384.8053 | 1218336.2963 | 2724388.3892 | 1218346.8238 | 2724390.5271 | 1218352.0615
92 | 2724343.0947 | 1218393.1068 | 2724341.3958 | 1218390.6107 | 2724337.3489 | 1218385.8893 | 2724333.7992 | 1218382.4458 | 2724325.3246 | 1218375.2321
93 | 2724320.9495 | 1218371.508 | 2724325.3246 | 1218375.2321
94 | 2724541.9163 | 1218466.1585 | 2724543.2361 | 1218463.45 | 2724545.9944 | 1218460.8056 | 2724549.5736 | 1218457.9965
95 | 2724555.5583 | 1218453.2996 | 2724549.5736 | 1218457.9965
96 | 2724555.5583 | 1218453.2996 | 2724562.8126 | 1218454.2186
97 | 2724384.8053 | 1218336.2963 | 2724379.2948 | 1218346.3892 | 2724380.8826 | 1218355.4295
98 | 2724512.8553 | 1218218.2001 | 2724510.7868 | 1218214.365 | 2724508.2394 | 1218209.8305
99 | 2724503.1865 | 1218198.0267 | 2724508.2394 | 1218209.8305
100 | 2724491.5784 | 1218179.8143 | 2724492.7532 | 1218184.9985 | 2724494.0979 | 1218187.8622 | 2724499.7831 | 1218194.1192 | 2724503.1865 | 1218198.0267
101 | 2724487.2409 | 1218160.6642 | 2724491.5784 | 1218179.8143
102 | 2724337.2923 | 1218192.2694 | 2724338.273 | 1218197.6608 | 2724338.6907 | 1218202.3843 | 2724338.7439 | 1218204.2022
103 | 2724337.5028 | 1218233.9427 | 2724338.0402 | 1218230.2593 | 2724339.1072 | 1218216.6153 | 2724338.7439 | 1218204.2022
104 | 2724337.2923 | 1218192.2694 | 2724336.0659 | 1218185.5497 | 2724334.9395 | 1218177.5133
105 | 2724337.5028 | 1218233.9427 | 2724336.7997 | 1218238.7623 | 2724336.3716 | 1218241.4657
106 | 2724487.2409 | 1218160.6642 | 2724542.321 | 1218121.351
107 | 2724542.321 | 1218121.351 | 2724542.4881 | 1218101.7502 | 2724546.1136 | 1218046.3936 | 2724546.4512 | 1218042.7966
108 | 2724258.7536 | 1218429.8273 | 2724258.6077 | 1218428.4468 | 2724258.8896 | 1218424.7609 | 2724260.1006 | 1218420.9387 | 2724261.6738 | 1218417.5911 | 2724265.3111 | 1218412.1071 | 2724270.9398 | 1218402.8839 | 2724271.7866 | 1218400.1438 | 2724272.1367 | 1218396.2002
109 | 2724307.6518 | 1218362.3956 | 2724291.5817 | 1218362.972 | 2724287.8616 | 1218364.0508 | 2724284.984 | 1218365.87 | 2724282.1189 | 1218368.9126 | 2724279.5409 | 1218372.7507 | 2724276.1683 | 1218378.6406 | 2724274.2865 | 1218383.6831 | 2724272.5906 | 1218391.0868 | 2724272.1367 | 1218396.2002
110 | 2724307.6518 | 1218362.3956 | 2724300.4518 | 1218369.0507 | 2724294.3862 | 1218385.3814 | 2724301.7269 | 1218388.348 | 2724302.0072 | 1218391.2895 | 2724297.7217 | 1218403.9425
111 | 2724307.6518 | 1218362.3956 | 2724315.8806 | 1218367.1933 | 2724320.9495 | 1218371.508
112 | 2724307.6518 | 1218362.3956 | 2724312.2291 | 1218346.5566
113 | 2724312.2303 | 1218346.5522 | 2724312.2291 | 1218346.5566
114 | 2724316.603 | 1218331.4211 | 2724312.2303 | 1218346.5522
115 | 2724246.1284 | 1218231.1206 | 2724241.0962 | 1218239.7669 | 2724239.2632 | 1218243.9208 | 2724237.9577 | 1218247.5409 | 2724237.3352 | 1218251.1752 | 2724237.3726 | 1218254.1116 | 2724238.4942 | 1218261.1294 | 2724238.0977 | 1218265.2132 | 2724236.8863 | 1218269.4135 | 2724235.1969 | 1218273.2368 | 2724223.7796 | 1218287.699 | 2724220.3784 | 1218293.1435 | 2724218.3188 | 1218299.4277
116 | 2724246.1284 | 1218231.1206 | 2724243.9728 | 1218221.5032
117 | 2724225.321 | 1218147.221 | 2724226.4902 | 1218151.5932 | 2724232.1052 | 1218164.1423 | 2724235.9502 | 1218176.3654 | 2724238.5578 | 1218195.8573 | 2724239.0921 | 1218199.727 | 2724243.9728 | 1218221.5032
118 | 2724319.5823 | 1218320.5108 | 2724319.2564 | 1218322.2396 | 2724316.603 | 1218331.4211
119 | 2724225.321 | 1218147.221 | 2724223.3426 | 1218139.785 | 2724221.2872 | 1218131.6596
120 | 2724322.3985 | 1218305.5698 | 2724319.5823 | 1218320.5108
121 | 2724322.3985 | 1218305.5698 | 2724306.2037 | 1218304.4755 | 2724306.0398 | 1218302.8995
122 | 2724322.3985 | 1218305.5698 | 2724325.0744 | 1218290.8697 | 2724326.464 | 1218283.226 | 2724328.0974 | 1218275.5429 | 2724334.5932 | 1218249.8917
123 | 2724306.0398 | 1218302.8995 | 2724305.1728 | 1218294.561
124 | 2724334.5932 | 1218249.8917 | 2724335.7764 | 1218245.2238 | 2724336.3716 | 1218241.4657
125 | 2724300.5914 | 1218270.3539 | 2724304.155 | 1218284.7729 | 2724305.1728 | 1218294.561
126 | 2724330.0068 | 1218147.738 | 2724333.6539 | 1218168.3414 | 2724334.9395 | 1218177.5133
127 | 2724330.0068 | 1218147.738 | 2724319.7804 | 1218141.1417 | 2724308.4656 | 1218135.0342
128 | 2724291.231 | 1218124.0772 | 2724299.895 | 1218130.2294 | 2724308.4656 | 1218135.0342
129 | 2724308.4656 | 1218135.0342 | 2724316.3034 | 1218122.2099 | 2724319.3369 | 1218119.2356
130 | 2724308.4656 | 1218135.0342 | 2724306.7002 | 1218137.7662 | 2724304.5086 | 1218143.4583 | 2724303.7252 | 1218145.4517
131 | 2724291.231 | 1218124.0772 | 2724288.3367 | 1218121.2368
132 | 2724291.231 | 1218124.0772 | 2724294.8792 | 1218118.0819 | 2724295.6683 | 1218106.4671 | 2724298.6105 | 1218101.5579 | 2724300.0735 | 1218099.7662
133 | 2724331.4057 | 1218114.5634 | 2724324.2099 | 1218114.4576 | 2724319.3369 | 1218119.2356
134 | 2724295.4372 | 1218155.3673 | 2724301.1888 | 1218151.9068 | 2724303.7252 | 1218145.4517
135 | 2724288.3367 | 1218121.2368 | 2724280.2586 | 1218123.0253 | 2724262.5075 | 1218123.3443 | 2724260.5028 | 1218122.9911 | 2724259.8328 | 1218121.9874 | 2724259.1222 | 1218115.666
136 | 2724288.3367 | 1218121.2368 | 2724285.6362 | 1218118.5673 | 2724280.2008 | 1218111.604 | 2724279.8217 | 1218110.9277
137 | 2724304.7416 | 1218094.7474 | 2724302.226 | 1218097.1299 | 2724300.0735 | 1218099.7662
138 | 2724331.4057 | 1218114.5634 | 2724461.2698 | 1218049.3343
139 | 2724279.8217 | 1218110.9277 | 2724276.7384 | 1218105.427 | 2724274.1666 | 1218099.1351 | 2724273.0718 | 1218094.1006
140 | 2724461.2698 | 1218049.3343 | 2724533.2935 | 1218012.0654
141 | 2724549.8265 | 1218006.829 | 2724546.4512 | 1218042.7966
142 | 2724533.2935 | 1218012.0654 | 2724528.4688 | 1218006.4046 | 2724527.7133 | 1218004.4094 | 2724527.6483 | 1218002.7957 | 2724528.0629 | 1218001.1253 | 2724529.3177 | 1217999.2167 | 2724532.8344 | 1217998.434 | 2724536.4072 | 1217998.9646 | 2724549.8265 | 1218006.829
143 | 2724549.8265 | 1218006.829 | 2724549.8751 | 1218000.514 | 2724548.9705 | 1217992.5777 | 2724547.6194 | 1217988.2016 | 2724542.7828 | 1217979.4826 | 2724537.9963 | 1217973.0886
144 | 2724252.5545 | 1217937.3575 | 2724241.2808 | 1217943.8164 | 2724225.3457 | 1217953.514
145 | 2724213.2025 | 1218085.583 | 2724213.8301 | 1218088.7689 | 2724215.487 | 1218103.2481 | 2724217.5909 | 1218117.0473 | 2724219.9364 | 1218126.3197
146 | 2724221.2872 | 1218131.6596 | 2724220.3002 | 1218127.7576
147 | 2724220.3002 | 1218127.7576 | 2724219.9364 | 1218126.3197

## bus_geodata
| x | y | coords
0 | 2724029.3993 | 1217967.3129
1 | 2724027.1983 | 1217966.2967
2 | 2724040.5399 | 1217972.457
3 | 2724020.9427 | 1217952.0331
4 | 2724044.0764 | 1217965.1553
5 | 2724033.8119 | 1217983.0442
6 | 2723993.2878 | 1218016.2634
7 | 2724025.9361 | 1217940.1587
8 | 2723993.8776 | 1218030.9713
9 | 2724029.9504 | 1217930.6129
10 | 2723998.1385 | 1218057.5189
11 | 2724145.7273 | 1217767.7387
12 | 2724148.2744 | 1217752.6287
13 | 2724144.3455 | 1217773.8742
14 | 2724150.0153 | 1217742.3009
15 | 2724140.596 | 1217781.5883
16 | 2724140.1952 | 1217715.8089
17 | 2724136.8745 | 1217788.4077
18 | 2724101.4738 | 1217747.648
19 | 2724131.5597 | 1217795.5775
20 | 2724100.8877 | 1217749.0742
21 | 2724097.5105 | 1217757.2913
22 | 2724183.926 | 1217845.802
23 | 2724249.5059 | 1217804.7234
24 | 2724257.5597 | 1217804.48
25 | 2724233.0217 | 1217853.0954
26 | 2724193.1608 | 1217968.8741
27 | 2724291.5387 | 1217785.9083
28 | 2724101.3011 | 1218002.5901
29 | 2724098.2417 | 1218025.878
30 | 2724184.7282 | 1218034.0973
31 | 2724088.0062 | 1218060.5031
32 | 2724026.8714 | 1218061.8202
33 | 2724206.8436 | 1218058.6108
34 | 2724027.3302 | 1218066.4495
35 | 2724222.6278 | 1218051.0338
36 | 2724208.4612 | 1218069.9279
37 | 2724345.2093 | 1217879.6409
38 | 2724094.3747 | 1217888.9339
39 | 2724094.6202 | 1217875.8104
40 | 2724082.614 | 1217908.2604
41 | 2724088.6207 | 1217870.4988
42 | 2724083.0049 | 1217915.3741
43 | 2724072.1708 | 1217902.5607
44 | 2724074.7948 | 1217858.2584
45 | 2724060.8884 | 1217872.9344
46 | 2724089.0968 | 1217843.1642
47 | 2724040.2592 | 1217906.1103
48 | 2724042.0809 | 1217901.767
49 | 2724034.5155 | 1217919.757
50 | 2724034.2137 | 1217920.4747
51 | 2724005.5534 | 1218092.6785
52 | 2724076.2987 | 1218249.3849
53 | 2724014.5907 | 1218241.2195
54 | 2724016.5497 | 1218172.7827
55 | 2724025.0238 | 1217872.9069
56 | 2724016.3178 | 1217871.0867
57 | 2724041.7663 | 1217876.4073
58 | 2724045.4307 | 1217852.5973
59 | 2724050.2706 | 1217884.7909
60 | 2724029.7037 | 1217897.0501
61 | 2724337.0797 | 1217905.0174
62 | 2724124.4499 | 1217803.7743
63 | 2724103.1642 | 1217828.3146
64 | 2724097.8769 | 1217833.8978
65 | 2724048.946 | 1217819.9105
66 | 2724032.2165 | 1217814.1398
67 | 2724028.8128 | 1217812.9658
68 | 2724740.2045 | 1218284.3185
69 | 2724750.2361 | 1218257.1958
70 | 2724733.8327 | 1218299.3967
71 | 2724790.1403 | 1218452.2181
72 | 2724547.216 | 1218317.474
73 | 2724532.4235 | 1218314.6737
74 | 2724447.6256 | 1218448.9304
75 | 2724441.6201 | 1218452.9075
76 | 2724523.0588 | 1218377.2605
77 | 2724544.2729 | 1218298.0632
78 | 2724539.1535 | 1218285.4915
79 | 2724457.3051 | 1218483.0922
80 | 2724394.8758 | 1218362.7127
81 | 2724532.1399 | 1218387.4027
82 | 2724528.831 | 1218362.0875
83 | 2724532.5014 | 1218348.7021
84 | 2724529.2942 | 1218482.0732
85 | 2724390.5271 | 1218352.0615
86 | 2724343.0947 | 1218393.1068
87 | 2724325.3246 | 1218375.2321
88 | 2724541.9163 | 1218466.1585
89 | 2724549.5736 | 1218457.9965
90 | 2724555.5583 | 1218453.2996
91 | 2724539.667 | 1218506.676
92 | 2724562.8126 | 1218454.2186
93 | 2724384.8053 | 1218336.2963
94 | 2724508.2394 | 1218209.8305
95 | 2724512.8553 | 1218218.2001
96 | 2724503.1865 | 1218198.0267
97 | 2724491.5784 | 1218179.8143
98 | 2724338.7439 | 1218204.2022
99 | 2724337.2923 | 1218192.2694
100 | 2724337.5028 | 1218233.9427
101 | 2724380.8826 | 1218355.4295
102 | 2724487.2409 | 1218160.6642
103 | 2724542.321 | 1218121.351
104 | 2724258.7536 | 1218429.8273
105 | 2724272.1367 | 1218396.2002
106 | 2724307.6518 | 1218362.3956
107 | 2724297.7217 | 1218403.9425
108 | 2724320.9495 | 1218371.508
109 | 2724312.2291 | 1218346.5566
110 | 2724312.2303 | 1218346.5522
111 | 2724246.1284 | 1218231.1206
112 | 2724218.3188 | 1218299.4277
113 | 2724243.9728 | 1218221.5032
114 | 2724316.603 | 1218331.4211
115 | 2724225.321 | 1218147.221
116 | 2724319.5823 | 1218320.5108
117 | 2724322.3985 | 1218305.5698
118 | 2724306.0398 | 1218302.8995
119 | 2724334.5932 | 1218249.8917
120 | 2724305.1728 | 1218294.561
121 | 2724336.3716 | 1218241.4657
122 | 2724300.5914 | 1218270.3539
123 | 2724334.9395 | 1218177.5133
124 | 2724330.0068 | 1218147.738
125 | 2724308.4656 | 1218135.0342
126 | 2724291.231 | 1218124.0772
127 | 2724319.3369 | 1218119.2356
128 | 2724303.7252 | 1218145.4517
129 | 2724288.3367 | 1218121.2368
130 | 2724300.0735 | 1218099.7662
131 | 2724331.4057 | 1218114.5634
132 | 2724295.4372 | 1218155.3673
133 | 2724259.1222 | 1218115.666
134 | 2724279.8217 | 1218110.9277
135 | 2724304.7416 | 1218094.7474
136 | 2724461.2698 | 1218049.3343
137 | 2724273.0718 | 1218094.1006
138 | 2724546.4512 | 1218042.7966
139 | 2724549.8265 | 1218006.829
140 | 2724533.2935 | 1218012.0654
141 | 2724252.5545 | 1217937.3575
142 | 2724225.3457 | 1217953.514
143 | 2724537.9963 | 1217973.0886
144 | 2724213.2025 | 1218085.583
145 | 2724221.2872 | 1218131.6596
146 | 2724220.3002 | 1218127.7576
147 | 2724219.9364 | 1218126.3197
148 | 2724030.7694 | 1217797.9953
149 | 2724184.7282 | 1218034.0973

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97996 | -0.38419 | 0.0027287 | 0.00068389
1 | 0.98001 | -0.38326 | 0 | 0
2 | 0.97975 | -0.38833 | 0 | 0
3 | 0.98044 | -0.3749 | 0 | 0
4 | 0.97965 | -0.39027 | 0.013145 | 0.0032945
5 | 0.97969 | -0.38956 | 0.0054186 | 0.001358
6 | 0.98244 | -0.33594 | 0 | 0
7 | 0.98013 | -0.38085 | 0.0019125 | 0.00047931
8 | 0.98286 | -0.32777 | 0.019913 | 0.0049906
9 | 0.97989 | -0.38554 | 0.00078611 | 0.00019702
10 | 0.98375 | -0.31039 | 0 | 0
11 | 0.97318 | -0.51727 | 0.0013659 | 0.00034233
12 | 0.97292 | -0.52232 | 0.0024251 | 0.00060779
13 | 0.97329 | -0.51504 | 0 | 0
14 | 0.97277 | -0.5253 | 0 | 0
15 | 0.97344 | -0.512 | 0.0020341 | 0.00050979
16 | 0.9717 | -0.54635 | 0 | 0
17 | 0.9736 | -0.50896 | 0 | 0
18 | 0.9709 | -0.56233 | 0.002472 | 0.00061953
19 | 0.97378 | -0.50547 | 0.0023297 | 0.00058387
20 | 0.97088 | -0.5627 | 0.01074 | 0.0026916
21 | 0.97086 | -0.56307 | 0.0022395 | 0.00056128
22 | 0.9978 | -0.042405 | 0.0023642 | 0.00059253
23 | 0.99797 | -0.039126 | 0 | 0
24 | 0.99799 | -0.038699 | 0 | 0
25 | 0.9986 | -0.026956 | 0 | 0
26 | 1 | 0 | -0.27762 | -0.07095
27 | 0.99755 | -0.04713 | 0.0047633 | 0.0011938
28 | 0.99165 | -0.15831 | 0 | 0
29 | 0.99074 | -0.17574 | 0 | 0
30 | 0.996 | -0.075585 | 0 | 0
31 | 0.99055 | -0.17943 | 0.0057277 | 0.0014355
32 | 0.98513 | -0.28362 | 0 | 0
33 | 0.9931 | -0.13101 | 0 | 0
34 | 0.9851 | -0.28425 | 0.0074291 | 0.0018619
35 | 0.99181 | -0.15585 | 0 | 0
36 | 0.99284 | -0.13604 | 0.0019229 | 0.00048193
37 | 0.99704 | -0.056925 | 0.0032524 | 0.00081513
38 | 0.97613 | -0.45913 | 0.0074235 | 0.0018605
39 | 0.97636 | -0.4547 | 0.0016964 | 0.00042516
40 | 0.97596 | -0.46247 | 0 | 0
41 | 0.97649 | -0.45218 | 0.00066298 | 0.00016616
42 | 0.97595 | -0.46271 | 0.0018593 | 0.00046598
43 | 0.9759 | -0.46383 | 0.0062191 | 0.0015586
44 | 0.97679 | -0.44615 | 0 | 0
45 | 0.97821 | -0.41836 | 0.00083029 | 0.00020809
46 | 0.97568 | -0.46802 | 0.009919 | 0.0024859
47 | 0.97929 | -0.39731 | 0 | 0
48 | 0.97918 | -0.39937 | 0 | 0
49 | 0.97962 | -0.39083 | 0 | 0
50 | 0.97964 | -0.39049 | 0.0027638 | 0.00069267
51 | 0.98339 | -0.31751 | 0 | 0
52 | 0.98213 | -0.34217 | 0.0022247 | 0.00055755
53 | 0.98226 | -0.33966 | 0.002741 | 0.00068695
54 | 0.98257 | -0.33352 | 0.0060038 | 0.0015047
55 | 0.97855 | -0.4118 | 0.0022067 | 0.00055306
56 | 0.97854 | -0.41192 | 0.00074019 | 0.00018551
57 | 0.97859 | -0.41088 | 0 | 0
58 | 0.97829 | -0.41684 | 0.013476 | 0.0033774
59 | 0.97878 | -0.40732 | 0 | 0
60 | 0.97914 | -0.40026 | 0.0037144 | 0.00093091
61 | 0.997 | -0.057855 | 0 | 0
62 | 0.97401 | -0.50076 | 0.0014088 | 0.00035307
63 | 0.97477 | -0.48584 | 0 | 0
64 | 0.97511 | -0.47914 | 0 | 0
65 | 0.97358 | -0.50938 | 0.018033 | 0.0045195
66 | 0.9735 | -0.51085 | 0.0022774 | 0.00057077
67 | 0.9735 | -0.511 | 0 | 0
68 | 0.9769 | -0.44651 | 0.0012017 | 0.00030117
69 | 0.9769 | -0.44663 | 0.00022874 | 5.7327e-05
70 | 0.97692 | -0.44608 | 0 | 0
71 | 0.97686 | -0.44739 | 0.00043665 | 0.00010943
72 | 0.97725 | -0.43966 | 0.00024722 | 6.1959e-05
73 | 0.97728 | -0.43907 | 0 | 0
74 | 0.9769 | -0.4466 | 0.00036858 | 9.2374e-05
75 | 0.97688 | -0.44687 | 0 | 0
76 | 0.97712 | -0.44214 | 0 | 0
77 | 0.9774 | -0.43656 | 0.00035346 | 8.8586e-05
78 | 0.97741 | -0.43644 | 0 | 0
79 | 0.97685 | -0.44748 | 0 | 0
80 | 0.97679 | -0.44873 | 0.00057433 | 0.00014394
81 | 0.97712 | -0.44218 | 0.00014728 | 3.6912e-05
82 | 0.97716 | -0.4414 | 0.00015148 | 3.7965e-05
83 | 0.97719 | -0.44072 | 0 | 0
84 | 0.97679 | -0.44876 | 0 | 0
85 | 0.97679 | -0.44881 | 0 | 0
86 | 0.98051 | -0.37519 | 0.00040128 | 0.00010057
87 | 0.98052 | -0.37501 | 0.000203 | 5.0878e-05
88 | 0.97678 | -0.44902 | 0.00036647 | 9.1846e-05
89 | 0.97677 | -0.44909 | 0.00015785 | 3.956e-05
90 | 0.97677 | -0.44911 | 0 | 0
91 | 0.97678 | -0.4489 | 0.00029117 | 7.2973e-05
92 | 0.97677 | -0.44913 | 0.00015721 | 3.9402e-05
93 | 0.97678 | -0.44894 | 0 | 0
94 | 0.97787 | -0.42738 | 0.00018501 | 4.6368e-05
95 | 0.97782 | -0.42827 | 0 | 0
96 | 0.97793 | -0.42613 | 0 | 0
97 | 0.97804 | -0.42399 | 0.00021253 | 5.3264e-05
98 | 0.98126 | -0.36045 | 0.0040722 | 0.0010206
99 | 0.98142 | -0.35737 | 0 | 0
100 | 0.98099 | -0.36587 | 0.0054956 | 0.0013773
101 | 0.97677 | -0.4491 | 0.0004228 | 0.00010596
102 | 0.97814 | -0.422 | 0 | 0
103 | 0.97848 | -0.41518 | 0 | 0
104 | 0.98051 | -0.37517 | 0.00018951 | 4.7497e-05
105 | 0.98052 | -0.37504 | 0.00020492 | 5.1357e-05
106 | 0.98054 | -0.37463 | 0 | 0
107 | 0.98052 | -0.37509 | 0.00049311 | 0.00012358
108 | 0.98052 | -0.37495 | 0.0004826 | 0.00012095
109 | 0.98057 | -0.37404 | 0.00040442 | 0.00010136
110 | 0.98057 | -0.37404 | 0.00039738 | 9.9592e-05
111 | 0.99122 | -0.16745 | 0 | 0
112 | 0.9912 | -0.16794 | 0.00035889 | 8.9947e-05
113 | 0.99123 | -0.16739 | 0.004994 | 0.0012516
114 | 0.98061 | -0.37324 | 0.00032217 | 8.0743e-05
115 | 0.9916 | -0.16008 | 0 | 0
116 | 0.98064 | -0.3726 | 0.00016941 | 4.2457e-05
117 | 0.98069 | -0.3717 | 0 | 0
118 | 0.98067 | -0.37206 | 0.00016703 | 4.1861e-05
119 | 0.98092 | -0.36718 | 0 | 0
120 | 0.98066 | -0.3722 | 0.00054809 | 0.00013736
121 | 0.98095 | -0.36649 | 0.00016257 | 4.0744e-05
122 | 0.98066 | -0.37237 | 0.00038428 | 9.631e-05
123 | 0.98161 | -0.35356 | 0.0038699 | 0.00096988
124 | 0.98212 | -0.34374 | 0 | 0
125 | 0.98253 | -0.33563 | 0 | 0
126 | 0.98352 | -0.31628 | 0 | 0
127 | 0.98214 | -0.34323 | 0.0037366 | 0.00093648
128 | 0.98239 | -0.33828 | 0.0070999 | 0.0017794
129 | 0.98374 | -0.31204 | 0 | 0
130 | 0.98338 | -0.31895 | 0.0020426 | 0.00051193
131 | 0.98191 | -0.34781 | 0.0054405 | 0.0013635
132 | 0.98232 | -0.33968 | 0.0056683 | 0.0014206
133 | 0.98583 | -0.27124 | 0.00346 | 0.00086715
134 | 0.98367 | -0.31339 | 0.0027686 | 0.00069387
135 | 0.98336 | -0.31938 | 0.0035024 | 0.00087778
136 | 0.98021 | -0.38105 | 0.0019349 | 0.00048494
137 | 0.98362 | -0.31433 | 0.0028312 | 0.00070957
138 | 0.97889 | -0.40724 | 0.0013304 | 0.00033342
139 | 0.97911 | -0.40273 | 0 | 0
140 | 0.97941 | -0.3968 | 0.002089 | 0.00052355
141 | 0.99684 | -0.060899 | 0 | 0
142 | 0.99678 | -0.061961 | 0.0019154 | 0.00048005
143 | 0.97906 | -0.40388 | 0.0017267 | 0.00043276
144 | 0.9925 | -0.14264 | 0.0027711 | 0.00069452
145 | 0.99168 | -0.15855 | 0.0066129 | 0.0016573
146 | 0.99173 | -0.1577 | 0.0041021 | 0.0010281
147 | 0.99175 | -0.15727 | 0.003917 | 0.00098171
148 | 0.97347 | -0.51162 | 0.0022331 | 0.00055966
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.021298 | -0.0053393 | 0.021299 | 0.0053399 | 9.508e-07 | 5.7797e-07 | 0.03234 | 0.03234 | 0.03234 | 0.97996 | -0.38419 | 0.98001 | -0.38326 | 8.8846
1 | 0.018569 | 0.0046554 | -0.018565 | -0.0046532 | 3.6584e-06 | 2.1868e-06 | 0.028196 | 0.028196 | 0.028196 | 0.97996 | -0.38419 | 0.97975 | -0.38833 | 7.7463
2 | -0.021299 | -0.0053399 | 0.021307 | 0.005345 | 8.4814e-06 | 5.1555e-06 | 0.03234 | 0.03234 | 0.03234 | 0.98001 | -0.38326 | 0.98044 | -0.3749 | 8.8846
3 | 0.013146 | 0.0032952 | -0.013145 | -0.0032945 | 1.2129e-06 | 6.7408e-07 | 0.019966 | 0.019966 | 0.019966 | 0.97975 | -0.38833 | 0.97965 | -0.39027 | 5.4853
4 | 0.0054189 | 0.0013581 | -0.0054186 | -0.001358 | 3.1863e-07 | 4.596e-08 | 0.0082301 | 0.0082302 | 0.0082302 | 0.97975 | -0.38833 | 0.97969 | -0.38956 | 2.261
5 | -0.12358 | -0.031164 | 0.12381 | 0.031308 | 0.00023093 | 0.00014426 | 0.18763 | 0.18763 | 0.18763 | 0.98044 | -0.3749 | 0.98244 | -0.33594 | 12.8867
6 | 0.10228 | 0.025819 | -0.10225 | -0.025801 | 2.9123e-05 | 1.7989e-05 | 0.15529 | 0.15529 | 0.15529 | 0.98044 | -0.3749 | 0.98013 | -0.38085 | 10.6656
7 | -0.12381 | -0.031308 | 0.12386 | 0.031339 | 4.8582e-05 | 3.0346e-05 | 0.18763 | 0.18763 | 0.18763 | 0.98244 | -0.33594 | 0.98286 | -0.32777 | 12.8867
8 | 0.10033 | 0.025322 | -0.10031 | -0.025308 | 2.2545e-05 | 1.3907e-05 | 0.15239 | 0.15239 | 0.15239 | 0.98013 | -0.38085 | 0.97989 | -0.38554 | 10.4662
9 | -0.14377 | -0.036329 | 0.14389 | 0.036405 | 0.00011985 | 7.5338e-05 | 0.21778 | 0.21778 | 0.21778 | 0.98286 | -0.32777 | 0.98375 | -0.31039 | 14.9572
10 | 0.099525 | 0.025111 | -0.099502 | -0.025096 | 2.357e-05 | 1.4531e-05 | 0.15119 | 0.15119 | 0.15119 | 0.97989 | -0.38554 | 0.97964 | -0.39049 | 10.3842
11 | 0.010983 | 0.0027549 | -0.01098 | -0.002753 | 3.7268e-06 | 1.9282e-06 | 0.016614 | 0.016614 | 0.016614 | 0.98375 | -0.31039 | 0.98339 | -0.31751 | 4.5643
12 | -0.15488 | -0.039159 | 0.15508 | 0.039285 | 0.00019911 | 0.00012547 | 0.23439 | 0.23439 | 0.23439 | 0.98375 | -0.31039 | 0.98513 | -0.28362 | 16.0982
13 | 0.01791 | 0.0045 | -0.017906 | -0.0044974 | 4.3107e-06 | 2.5685e-06 | 0.02739 | 0.02739 | 0.02739 | 0.97318 | -0.51727 | 0.97292 | -0.52232 | 7.5246
14 | -0.019276 | -0.0048423 | 0.019278 | 0.0048435 | 2.0506e-06 | 1.2342e-06 | 0.029478 | 0.029478 | 0.029478 | 0.97318 | -0.51727 | 0.97329 | -0.51504 | 8.0984
15 | 0.015481 | 0.0038896 | -0.015479 | -0.0038883 | 2.2025e-06 | 1.2795e-06 | 0.023681 | 0.023681 | 0.023681 | 0.97292 | -0.52232 | 0.97277 | -0.5253 | 6.5057
16 | -0.019278 | -0.0048435 | 0.019281 | 0.0048452 | 2.7988e-06 | 1.6845e-06 | 0.029478 | 0.029478 | 0.029478 | 0.97329 | -0.51504 | 0.97344 | -0.512 | 8.0984
17 | 0.015479 | 0.0038883 | -0.015463 | -0.0038793 | 1.5532e-05 | 9.0247e-06 | 0.023681 | 0.023681 | 0.023681 | 0.97277 | -0.5253 | 0.9717 | -0.54635 | 6.5058
18 | -0.021315 | -0.005355 | 0.021318 | 0.0053569 | 3.0937e-06 | 1.8834e-06 | 0.032587 | 0.032587 | 0.032587 | 0.97344 | -0.512 | 0.9736 | -0.50896 | 8.9526
19 | 0.015463 | 0.0038793 | -0.015451 | -0.0038725 | 1.1775e-05 | 6.8427e-06 | 0.023681 | 0.023681 | 0.023681 | 0.9717 | -0.54635 | 0.9709 | -0.56233 | 6.5058
20 | -0.021318 | -0.0053569 | 0.021322 | 0.0053591 | 3.5549e-06 | 2.1641e-06 | 0.032587 | 0.032587 | 0.032587 | 0.9736 | -0.50896 | 0.97378 | -0.50547 | 8.9526
21 | 0.012979 | 0.0032529 | -0.012979 | -0.0032528 | 2.2882e-07 | 1.2738e-07 | 0.019893 | 0.019893 | 0.019893 | 0.9709 | -0.56233 | 0.97088 | -0.5627 | 5.465
22 | -0.023652 | -0.0059429 | 0.023657 | 0.0059462 | 5.3166e-06 | 3.2676e-06 | 0.036147 | 0.036147 | 0.036147 | 0.97378 | -0.50547 | 0.97401 | -0.50076 | 9.9306
23 | 0.0022396 | 0.00056119 | -0.0022395 | -0.00056128 | 3.9251e-08 | -8.4739e-08 | 0.0034324 | 0.0034325 | 0.0034325 | 0.97088 | -0.5627 | 0.97086 | -0.56307 | 0.94299
24 | -0.0023642 | -0.00059253 | 0.0023646 | 0.00059173 | 3.6913e-07 | -7.9832e-07 | 0.0035258 | 0.0035254 | 0.0035258 | 0.9978 | -0.042405 | 0.99797 | -0.039126 | 0.96862
25 | -0.0023646 | -0.00059173 | 0.0023646 | 0.00059163 | 4.8042e-08 | -1.0394e-07 | 0.0035254 | 0.0035254 | 0.0035254 | 0.99797 | -0.039126 | 0.99799 | -0.038699 | 0.96852
26 | 0.009938 | 0.0024894 | -0.009934 | -0.0024875 | 3.9886e-06 | 1.92e-06 | 0.014817 | 0.014818 | 0.014818 | 0.99799 | -0.038699 | 0.99755 | -0.04713 | 4.0707
27 | -0.012303 | -0.003081 | 0.01231 | 0.0030847 | 6.8824e-06 | 3.6915e-06 | 0.018343 | 0.018342 | 0.018343 | 0.99799 | -0.038699 | 0.9986 | -0.026956 | 5.0392
28 | -0.01231 | -0.0030847 | 0.012325 | 0.0030932 | 1.5825e-05 | 8.4846e-06 | 0.018342 | 0.018342 | 0.018342 | 0.9986 | -0.026956 | 1 | 0 | 5.0391
29 | 0.26365 | 0.067857 | -0.26268 | -0.067243 | 0.00096537 | 0.00061435 | 0.39294 | 0.39294 | 0.39294 | 1 | 0 | 0.996 | -0.075585 | 26.9879
30 | 0.0051707 | 0.0012937 | -0.0051683 | -0.0012935 | 2.4092e-06 | 1.3254e-07 | 0.0077122 | 0.0077127 | 0.0077127 | 0.99755 | -0.04713 | 0.99704 | -0.056925 | 2.1189
31 | 0.16922 | 0.043207 | -0.16908 | -0.043117 | 0.00014246 | 8.9961e-05 | 0.25421 | 0.25421 | 0.25421 | 0.99165 | -0.15831 | 0.99074 | -0.17574 | 17.4596
32 | -0.16922 | -0.043207 | 0.1699 | 0.043636 | 0.00067946 | 0.00042904 | 0.25421 | 0.25421 | 0.25421 | 0.99165 | -0.15831 | 0.996 | -0.075585 | 17.4596
33 | 0.0057287 | 0.0014357 | -0.0057277 | -0.0014355 | 1.0073e-06 | 1.7752e-07 | 0.008604 | 0.0086042 | 0.0086042 | 0.99074 | -0.17574 | 0.99055 | -0.17943 | 2.3638
34 | 0.16335 | 0.041681 | -0.16251 | -0.041147 | 0.00084652 | 0.00053411 | 0.24561 | 0.24561 | 0.24561 | 0.99074 | -0.17574 | 0.98513 | -0.28362 | 16.8689
35 | 0.092778 | 0.023607 | -0.092531 | -0.023449 | 0.00024712 | 0.00015771 | 0.13874 | 0.13874 | 0.13874 | 0.996 | -0.075585 | 0.9931 | -0.13101 | 38.1141
36 | 0.0074293 | 0.001862 | -0.0074291 | -0.0018619 | 2.1968e-07 | 8.1366e-08 | 0.011222 | 0.011222 | 0.011222 | 0.98513 | -0.28362 | 0.9851 | -0.28425 | 3.0829
37 | 0.067822 | 0.017248 | -0.067741 | -0.017196 | 8.1067e-05 | 5.1613e-05 | 0.10171 | 0.10171 | 0.10171 | 0.9931 | -0.13101 | 0.99181 | -0.15585 | 27.9422
38 | 0.024709 | 0.0062011 | -0.024703 | -0.0061975 | 5.9301e-06 | 3.6461e-06 | 0.037026 | 0.037026 | 0.037026 | 0.9931 | -0.13101 | 0.99284 | -0.13604 | 10.1719
39 | 0.067741 | 0.017196 | -0.067367 | -0.016958 | 0.00037382 | 0.00023801 | 0.10171 | 0.10171 | 0.10171 | 0.99181 | -0.15585 | 0.98583 | -0.27124 | 27.9423
40 | 0.02278 | 0.0057155 | -0.022773 | -0.0057112 | 7.1617e-06 | 4.3717e-06 | 0.034144 | 0.034144 | 0.034144 | 0.99284 | -0.13604 | 0.9925 | -0.14264 | 9.3802
41 | 0.0019159 | 0.0004784 | -0.0019158 | -0.0004787 | 8.4693e-08 | -3.0619e-07 | 0.0028587 | 0.0028588 | 0.0028588 | 0.99704 | -0.056925 | 0.997 | -0.057855 | 0.7854
42 | -0.015504 | -0.0038857 | 0.015507 | 0.0038876 | 3.2697e-06 | 1.8974e-06 | 0.023634 | 0.023634 | 0.023634 | 0.97613 | -0.45913 | 0.97636 | -0.4547 | 6.4928
43 | 0.00808 | 0.0020252 | -0.0080788 | -0.0020247 | 1.2871e-06 | 5.4101e-07 | 0.012317 | 0.012317 | 0.012317 | 0.97613 | -0.45913 | 0.97596 | -0.46247 | 3.3839
44 | -0.017203 | -0.0043128 | 0.017205 | 0.004314 | 2.0656e-06 | 1.2218e-06 | 0.026219 | 0.026219 | 0.026219 | 0.97636 | -0.4547 | 0.97649 | -0.45218 | 7.203
45 | 0.0018593 | 0.0004659 | -0.0018593 | -0.00046598 | 2.1469e-08 | -7.5287e-08 | 0.0028348 | 0.0028348 | 0.0028348 | 0.97596 | -0.46247 | 0.97595 | -0.46271 | 0.77879
46 | 0.0062195 | 0.0015588 | -0.0062191 | -0.0015586 | 4.0118e-07 | 1.0809e-07 | 0.0094826 | 0.0094827 | 0.0094827 | 0.97596 | -0.46247 | 0.9759 | -0.46383 | 2.6051
47 | -0.017868 | -0.0044801 | 0.017873 | 0.0044832 | 5.1341e-06 | 3.0548e-06 | 0.027229 | 0.027229 | 0.027229 | 0.97649 | -0.45218 | 0.97679 | -0.44615 | 7.4806
48 | -0.075546 | -0.019009 | 0.075646 | 0.019073 | 0.00010046 | 6.4043e-05 | 0.11511 | 0.11511 | 0.11511 | 0.97679 | -0.44615 | 0.97821 | -0.41836 | 31.624
49 | 0.057673 | 0.014525 | -0.057612 | -0.014487 | 6.0224e-05 | 3.8283e-05 | 0.087882 | 0.087882 | 0.087882 | 0.97679 | -0.44615 | 0.97568 | -0.46802 | 24.1435
50 | -0.076477 | -0.019281 | 0.076517 | 0.019306 | 4.0446e-05 | 2.5485e-05 | 0.11637 | 0.11637 | 0.11637 | 0.97821 | -0.41836 | 0.97878 | -0.40732 | 15.9855
51 | 0.047693 | 0.012001 | -0.047668 | -0.011985 | 2.5339e-05 | 1.6058e-05 | 0.072755 | 0.072755 | 0.072755 | 0.97568 | -0.46802 | 0.97511 | -0.47914 | 19.9876
52 | 0.096706 | 0.024384 | -0.096697 | -0.024378 | 9.5393e-06 | 5.8682e-06 | 0.147 | 0.147 | 0.147 | 0.97929 | -0.39731 | 0.97918 | -0.39937 | 10.0959
53 | -0.096706 | -0.024384 | 0.096736 | 0.024403 | 2.9987e-05 | 1.8447e-05 | 0.147 | 0.147 | 0.147 | 0.97929 | -0.39731 | 0.97962 | -0.39083 | 10.0959
54 | 0.0037145 | 0.00093084 | -0.0037144 | -0.00093091 | 1.5785e-07 | -6.5143e-08 | 0.0056447 | 0.0056448 | 0.0056448 | 0.97918 | -0.39937 | 0.97914 | -0.40026 | 1.5508
55 | 0.092982 | 0.023447 | -0.092947 | -0.023426 | 3.5369e-05 | 2.1687e-05 | 0.14135 | 0.14135 | 0.14135 | 0.97918 | -0.39937 | 0.97878 | -0.40732 | 9.7083
56 | -0.096736 | -0.024403 | 0.096738 | 0.024404 | 1.5773e-06 | 9.7028e-07 | 0.147 | 0.147 | 0.147 | 0.97962 | -0.39083 | 0.97964 | -0.39049 | 10.0959
57 | 0.01098 | 0.002753 | -0.010971 | -0.0027487 | 8.3697e-06 | 4.3316e-06 | 0.016614 | 0.016615 | 0.016615 | 0.98339 | -0.31751 | 0.98257 | -0.33352 | 4.5644
58 | -0.0022247 | -0.00055755 | 0.0022249 | 0.00055694 | 2.6516e-07 | -6.1809e-07 | 0.0033706 | 0.0033703 | 0.0033706 | 0.98213 | -0.34217 | 0.98226 | -0.33966 | 0.92598
59 | -0.0049659 | -0.0012439 | 0.0049674 | 0.001244 | 1.4528e-06 | 6.2922e-08 | 0.0075226 | 0.0075223 | 0.0075226 | 0.98226 | -0.33966 | 0.98257 | -0.33352 | 2.0666
60 | 0.00074019 | 0.0001854 | -0.00074019 | -0.00018551 | 4.2254e-09 | -1.0903e-07 | 0.0011255 | 0.0011256 | 0.0011256 | 0.97855 | -0.4118 | 0.97854 | -0.41192 | 0.30922
61 | -0.0029469 | -0.00073846 | 0.002947 | 0.00073833 | 1.288e-07 | -1.3245e-07 | 0.0044812 | 0.0044811 | 0.0044812 | 0.97855 | -0.4118 | 0.97859 | -0.41088 | 1.2311
62 | 0.01348 | 0.0033795 | -0.013476 | -0.0033774 | 3.8275e-06 | 2.1445e-06 | 0.020497 | 0.020497 | 0.020497 | 0.97859 | -0.41088 | 0.97829 | -0.41684 | 5.6312
63 | -0.016427 | -0.0041179 | 0.01643 | 0.0041195 | 2.7899e-06 | 1.6357e-06 | 0.024978 | 0.024978 | 0.024978 | 0.97859 | -0.41088 | 0.97878 | -0.40732 | 6.8622
64 | 0.0019158 | 0.0004787 | -0.0019155 | -0.0004797 | 2.7741e-07 | -1.0025e-06 | 0.0028588 | 0.0028593 | 0.0028593 | 0.997 | -0.057855 | 0.99684 | -0.060899 | 0.78551
65 | -0.025066 | -0.0062993 | 0.025084 | 0.0063103 | 1.7869e-05 | 1.1032e-05 | 0.038299 | 0.038299 | 0.038299 | 0.97401 | -0.50076 | 0.97477 | -0.48584 | 10.5218
66 | 0.022569 | 0.0056652 | -0.022544 | -0.0056497 | 2.5315e-05 | 1.5493e-05 | 0.034456 | 0.034456 | 0.034456 | 0.97477 | -0.48584 | 0.97358 | -0.50938 | 9.4659
67 | -0.047653 | -0.011976 | 0.047668 | 0.011985 | 1.5245e-05 | 9.6608e-06 | 0.072755 | 0.072755 | 0.072755 | 0.97477 | -0.48584 | 0.97511 | -0.47914 | 19.9876
68 | 0.0045109 | 0.0011302 | -0.0045105 | -0.0011302 | 3.1543e-07 | -1.8169e-08 | 0.0068943 | 0.0068944 | 0.0068944 | 0.97358 | -0.50938 | 0.9735 | -0.51085 | 1.8941
69 | 0.0022331 | 0.00055948 | -0.0022331 | -0.00055951 | 1.5731e-08 | -3.4698e-08 | 0.0034133 | 0.0034133 | 0.0034133 | 0.9735 | -0.51085 | 0.9735 | -0.511 | 0.93773
70 | 0.0022331 | 0.00055951 | -0.0022331 | -0.00055966 | 6.5965e-08 | -1.4549e-07 | 0.0034133 | 0.0034134 | 0.0034134 | 0.9735 | -0.511 | 0.97347 | -0.51162 | 0.93775
71 | 0.00022874 | 5.6963e-05 | -0.00022874 | -5.7327e-05 | 1.3265e-09 | -3.6412e-07 | 0.00034829 | 0.00034842 | 0.00034842 | 0.9769 | -0.44651 | 0.9769 | -0.44663 | 0.095719
72 | -0.0014304 | -0.00035814 | 0.0014305 | 0.00035795 | 2.9248e-08 | -1.8702e-07 | 0.0021787 | 0.0021786 | 0.0021787 | 0.9769 | -0.44651 | 0.97692 | -0.44608 | 0.59855
73 | 0.00043667 | 0.00010741 | -0.00043665 | -0.00010943 | 2.699e-08 | -2.0218e-06 | 0.0006644 | 0.00066513 | 0.00066513 | 0.97692 | -0.44608 | 0.97686 | -0.44739 | 0.18273
74 | -0.0018671 | -0.00046536 | 0.0018677 | 0.00046338 | 5.6813e-07 | -1.9847e-06 | 0.002843 | 0.0028422 | 0.002843 | 0.97692 | -0.44608 | 0.97725 | -0.43966 | 0.78106
75 | -0.0021149 | -0.00052534 | 0.002115 | 0.00052519 | 5.8318e-08 | -1.5077e-07 | 0.0032186 | 0.0032186 | 0.0032186 | 0.97725 | -0.43966 | 0.97728 | -0.43907 | 0.88424
76 | -0.0047532 | -0.0011803 | 0.0047538 | 0.0011803 | 5.9211e-07 | 7.7254e-10 | 0.0072334 | 0.0072333 | 0.0072334 | 0.97728 | -0.43907 | 0.97741 | -0.43644 | 1.9872
77 | 0.0026383 | 0.00065511 | -0.0026381 | -0.0006554 | 2.0585e-07 | -2.9491e-07 | 0.0040149 | 0.004015 | 0.004015 | 0.97728 | -0.43907 | 0.97719 | -0.44072 | 1.103
78 | 0.00197 | 0.0004896 | -0.00197 | -0.00048967 | 2.4691e-08 | -7.5833e-08 | 0.0029993 | 0.0029993 | 0.0029993 | 0.9769 | -0.4466 | 0.97688 | -0.44687 | 0.82399
79 | -0.0023386 | -0.00058197 | 0.0023391 | 0.00058098 | 4.9465e-07 | -9.8646e-07 | 0.0035607 | 0.0035603 | 0.0035607 | 0.9769 | -0.4466 | 0.97712 | -0.44214 | 0.97822
80 | 0.0009728 | 0.00024159 | -0.00097277 | -0.000242 | 2.7967e-08 | -4.0775e-07 | 0.001481 | 0.0014811 | 0.0014811 | 0.97688 | -0.44687 | 0.97685 | -0.44748 | 0.40691
81 | 0.00099722 | 0.00024808 | -0.00099714 | -0.0002493 | 8.7855e-08 | -1.2156e-06 | 0.0015183 | 0.0015188 | 0.0015188 | 0.97688 | -0.44687 | 0.97679 | -0.44873 | 0.41725
82 | 0.00014728 | 3.6725e-05 | -0.00014728 | -3.6912e-05 | 2.823e-10 | -1.8732e-07 | 0.00022422 | 0.00022429 | 0.00022429 | 0.97712 | -0.44214 | 0.97712 | -0.44218 | 0.061618
83 | -0.0024864 | -0.00061771 | 0.0024865 | 0.00061756 | 8.7252e-08 | -1.4766e-07 | 0.0037845 | 0.0037844 | 0.0037845 | 0.97712 | -0.44214 | 0.97716 | -0.4414 | 1.0397
84 | -0.00035346 | -8.8586e-05 | 0.00035346 | 8.8353e-05 | 2.0298e-09 | -2.3302e-07 | 0.00053811 | 0.00053803 | 0.00053811 | 0.9774 | -0.43656 | 0.97741 | -0.43644 | 0.14783
85 | -0.0051073 | -0.0012686 | 0.0051093 | 0.0012688 | 1.974e-06 | 1.7042e-07 | 0.0077713 | 0.0077709 | 0.0077713 | 0.97741 | -0.43644 | 0.97782 | -0.42827 | 2.135
86 | 0.00097277 | 0.000242 | -0.00097271 | -0.00024286 | 5.9242e-08 | -8.6335e-07 | 0.0014811 | 0.0014815 | 0.0014815 | 0.97685 | -0.44748 | 0.97679 | -0.44876 | 0.407
87 | 0.00042281 | 0.00010536 | -0.00042281 | -0.0001055 | 1.7888e-09 | -1.4286e-07 | 0.00064388 | 0.00064393 | 0.00064393 | 0.97679 | -0.44873 | 0.97679 | -0.44881 | 0.1769
88 | -0.002638 | -0.00065552 | 0.0026381 | 0.0006554 | 8.4167e-08 | -1.2055e-07 | 0.0040151 | 0.004015 | 0.0040151 | 0.97716 | -0.4414 | 0.97719 | -0.44072 | 1.103
89 | 0.00029117 | 7.264e-05 | -0.00029117 | -7.2973e-05 | 1.9687e-09 | -3.3284e-07 | 0.00044344 | 0.00044356 | 0.00044356 | 0.97679 | -0.44876 | 0.97678 | -0.4489 | 0.12186
90 | 0.00068154 | 0.00017022 | -0.00068153 | -0.00017048 | 8.5123e-09 | -2.5822e-07 | 0.001038 | 0.0010381 | 0.0010381 | 0.97679 | -0.44876 | 0.97678 | -0.44902 | 0.2852
91 | 0.00042281 | 0.0001055 | -0.00042281 | -0.00010571 | 2.6085e-09 | -2.0829e-07 | 0.00064393 | 0.00064401 | 0.00064401 | 0.97679 | -0.44881 | 0.97678 | -0.44894 | 0.17692
92 | -0.00040128 | -0.00010057 | 0.00040128 | 0.00010025 | 3.5196e-09 | -3.1701e-07 | 0.00060898 | 0.00060887 | 0.00060898 | 0.98051 | -0.37519 | 0.98052 | -0.37501 | 0.1673
93 | -0.00060429 | -0.00015113 | 0.00060429 | 0.00015106 | 1.8115e-09 | -7.131e-08 | 0.00091694 | 0.00091691 | 0.00091694 | 0.98052 | -0.37501 | 0.98052 | -0.37495 | 0.25191
94 | 0.00031506 | 7.8633e-05 | -0.00031506 | -7.8775e-05 | 9.8305e-10 | -1.4186e-07 | 0.00047985 | 0.0004799 | 0.0004799 | 0.97678 | -0.44902 | 0.97677 | -0.44909 | 0.13184
95 | 0.00015721 | 3.9215e-05 | -0.00015721 | -3.931e-05 | 1.6358e-10 | -9.5121e-08 | 0.00023943 | 0.00023947 | 0.00023947 | 0.97677 | -0.44909 | 0.97677 | -0.44911 | 0.065788
96 | 0.00015721 | 3.931e-05 | -0.00015721 | -3.9402e-05 | 1.568e-10 | -9.116e-08 | 0.00023947 | 0.0002395 | 0.0002395 | 0.97677 | -0.44911 | 0.97677 | -0.44913 | 0.065797
97 | 0.00042281 | 0.00010571 | -0.0004228 | -0.00010596 | 3.2157e-09 | -2.5671e-07 | 0.00064401 | 0.0006441 | 0.0006441 | 0.97678 | -0.44894 | 0.97677 | -0.4491 | 0.17695
98 | 0.0051095 | 0.0012688 | -0.0051093 | -0.0012688 | 2.1645e-07 | 1.8625e-08 | 0.0077709 | 0.0077709 | 0.0077709 | 0.97787 | -0.42738 | 0.97782 | -0.42827 | 2.1349
99 | -0.0052945 | -0.0013152 | 0.0052948 | 0.0013152 | 3.122e-07 | 3.8725e-08 | 0.0080524 | 0.0080524 | 0.0080524 | 0.97787 | -0.42738 | 0.97793 | -0.42613 | 2.2122
100 | -0.0052948 | -0.0013152 | 0.0052953 | 0.0013153 | 5.3729e-07 | 6.659e-08 | 0.0080524 | 0.0080523 | 0.0080524 | 0.97793 | -0.42613 | 0.97804 | -0.42399 | 2.2122
101 | -0.0055079 | -0.0013686 | 0.0055084 | 0.0013687 | 5.1652e-07 | 8.4142e-08 | 0.0083756 | 0.0083755 | 0.0083756 | 0.97804 | -0.42399 | 0.97814 | -0.422 | 2.301
102 | -0.014102 | -0.0035308 | 0.014104 | 0.003532 | 2.0645e-06 | 1.1692e-06 | 0.021383 | 0.021383 | 0.021383 | 0.98126 | -0.36045 | 0.98142 | -0.35737 | 5.8745
103 | 0.01003 | 0.0025102 | -0.010027 | -0.0025089 | 2.5869e-06 | 1.279e-06 | 0.015208 | 0.015208 | 0.015208 | 0.98126 | -0.36045 | 0.98099 | -0.36587 | 4.1781
104 | -0.014104 | -0.003532 | 0.014107 | 0.0035334 | 2.5627e-06 | 1.4512e-06 | 0.021383 | 0.021383 | 0.021383 | 0.98142 | -0.35737 | 0.98161 | -0.35356 | 5.8745
105 | 0.0045314 | 0.0011316 | -0.0045313 | -0.0011316 | 1.3473e-07 | -9.8179e-09 | 0.0068721 | 0.0068721 | 0.0068721 | 0.98099 | -0.36587 | 0.98095 | -0.36649 | 1.8879
106 | -0.0055084 | -0.0013687 | 0.0055102 | 0.0013689 | 1.7801e-06 | 2.8955e-07 | 0.0083755 | 0.0083752 | 0.0083755 | 0.97814 | -0.422 | 0.97848 | -0.41518 | 2.301
107 | -0.0055102 | -0.0013689 | 0.0055122 | 0.0013693 | 2.0698e-06 | 3.3584e-07 | 0.0083752 | 0.0083749 | 0.0083752 | 0.97848 | -0.41518 | 0.97889 | -0.40724 | 2.3009
108 | -0.00018951 | -4.7497e-05 | 0.00018952 | 4.7031e-05 | 1.1472e-09 | -4.6602e-07 | 0.0002876 | 0.00028744 | 0.0002876 | 0.98051 | -0.37517 | 0.98052 | -0.37504 | 0.079012
109 | -0.00039443 | -9.8387e-05 | 0.00039444 | 9.7673e-05 | 7.659e-09 | -7.1481e-07 | 0.00059841 | 0.00059816 | 0.00059841 | 0.98052 | -0.37504 | 0.98054 | -0.37463 | 0.1644
110 | 0.00049312 | 0.00012294 | -0.00049311 | -0.00012358 | 1.0803e-08 | -6.4213e-07 | 0.0007481 | 0.00074833 | 0.00074833 | 0.98054 | -0.37463 | 0.98052 | -0.37509 | 0.20559
111 | 0.0010869 | 0.00027182 | -0.0010869 | -0.00027201 | 1.6506e-08 | -1.9355e-07 | 0.0016492 | 0.0016493 | 0.0016493 | 0.98054 | -0.37463 | 0.98052 | -0.37495 | 0.4531
112 | -0.0019745 | -0.00049243 | 0.0019745 | 0.00049226 | 5.5476e-08 | -1.7247e-07 | 0.0029955 | 0.0029954 | 0.0029955 | 0.98054 | -0.37463 | 0.98057 | -0.37404 | 0.82294
113 | -0.0023789 | -0.00059362 | 0.0023789 | 0.00059362 | 2.1859e-11 | -4.2847e-11 | 0.0036091 | 0.0036091 | 0.0036091 | 0.98057 | -0.37404 | 0.98057 | -0.37404 | 0.99152
114 | -0.0027763 | -0.00069321 | 0.0027764 | 0.00069308 | 1.0479e-07 | -1.3162e-07 | 0.0042121 | 0.0042121 | 0.0042121 | 0.98057 | -0.37404 | 0.98061 | -0.37324 | 1.1572
115 | 0.0003589 | 8.897e-05 | -0.00035889 | -8.9947e-05 | 8.2906e-09 | -9.77e-07 | 0.00053844 | 0.00053878 | 0.00053878 | 0.99122 | -0.16745 | 0.9912 | -0.16794 | 0.14802
116 | -0.0003589 | -8.897e-05 | 0.0003589 | 8.8844e-05 | 1.0714e-09 | -1.2636e-07 | 0.00053844 | 0.00053839 | 0.00053844 | 0.99122 | -0.16745 | 0.99123 | -0.16739 | 0.14792
117 | -0.0053529 | -0.0013405 | 0.0053547 | 0.0013407 | 1.8637e-06 | 2.0015e-07 | 0.0080353 | 0.0080349 | 0.0080353 | 0.99123 | -0.16739 | 0.9916 | -0.16008 | 2.2075
118 | -0.0030986 | -0.00077382 | 0.0030987 | 0.00077374 | 9.3779e-08 | -8.2749e-08 | 0.0047009 | 0.0047009 | 0.0047009 | 0.98061 | -0.37324 | 0.98064 | -0.3726 | 1.2915
119 | -0.0053547 | -0.0013407 | 0.0053551 | 0.0013407 | 3.892e-07 | 4.1691e-08 | 0.0080349 | 0.0080349 | 0.0080349 | 0.9916 | -0.16008 | 0.99168 | -0.15855 | 2.2074
120 | -0.0032681 | -0.0008162 | 0.0032682 | 0.00081609 | 1.4015e-07 | -1.0213e-07 | 0.0049579 | 0.0049579 | 0.0049579 | 0.98064 | -0.3726 | 0.98069 | -0.3717 | 1.3621
121 | 0.0010994 | 0.00027491 | -0.0010994 | -0.00027512 | 1.8588e-08 | -2.129e-07 | 0.0016679 | 0.001668 | 0.001668 | 0.98069 | -0.3717 | 0.98067 | -0.37206 | 0.45825
122 | -0.0043677 | -0.001091 | 0.0043686 | 0.0010909 | 9.3879e-07 | -1.1887e-07 | 0.0066258 | 0.0066256 | 0.0066258 | 0.98069 | -0.3717 | 0.98092 | -0.36718 | 1.8203
123 | 0.00093238 | 0.00023326 | -0.00093237 | -0.00023336 | 6.2911e-09 | -1.0175e-07 | 0.0014146 | 0.0014146 | 0.0014146 | 0.98067 | -0.37206 | 0.98066 | -0.3722 | 0.38863
124 | -0.0043686 | -0.0010909 | 0.0043687 | 0.0010909 | 1.4191e-07 | -1.8003e-08 | 0.0066256 | 0.0066255 | 0.0066256 | 0.98092 | -0.36718 | 0.98095 | -0.36649 | 1.8202
125 | 0.00038429 | 9.6001e-05 | -0.00038428 | -9.631e-05 | 3.1479e-09 | -3.0954e-07 | 0.00058299 | 0.0005831 | 0.0005831 | 0.98066 | -0.3722 | 0.98066 | -0.37237 | 0.16019
126 | -0.017976 | -0.0045033 | 0.017985 | 0.0045083 | 8.4051e-06 | 4.9975e-06 | 0.027249 | 0.027249 | 0.027249 | 0.98161 | -0.35356 | 0.98212 | -0.34374 | 7.4861
127 | -0.017985 | -0.0045083 | 0.017992 | 0.0045125 | 6.9537e-06 | 4.1342e-06 | 0.027249 | 0.027249 | 0.027249 | 0.98212 | -0.34374 | 0.98253 | -0.33563 | 7.4861
128 | -0.052576 | -0.013181 | 0.052625 | 0.013211 | 4.8528e-05 | 3.0799e-05 | 0.079626 | 0.079626 | 0.079626 | 0.98253 | -0.33563 | 0.98352 | -0.31628 | 21.8754
129 | 0.021814 | 0.0054673 | -0.021806 | -0.0054624 | 7.8903e-06 | 4.8057e-06 | 0.033037 | 0.033037 | 0.033037 | 0.98253 | -0.33563 | 0.98214 | -0.34323 | 9.0761
130 | 0.01277 | 0.003201 | -0.012769 | -0.0032001 | 1.6123e-06 | 8.8629e-07 | 0.01934 | 0.01934 | 0.01934 | 0.98253 | -0.33563 | 0.98239 | -0.33828 | 5.3133
131 | -0.05817 | -0.014601 | 0.058182 | 0.014609 | 1.1763e-05 | 7.4768e-06 | 0.088017 | 0.088017 | 0.088017 | 0.98352 | -0.31628 | 0.98374 | -0.31204 | 24.1804
132 | 0.0055458 | 0.0013898 | -0.0055451 | -0.0013897 | 7.0479e-07 | 1.1232e-07 | 0.0083905 | 0.0083906 | 0.0083906 | 0.98352 | -0.31628 | 0.98338 | -0.31895 | 2.3051
133 | 0.01807 | 0.004526 | -0.018066 | -0.0045236 | 3.9405e-06 | 2.3445e-06 | 0.027376 | 0.027376 | 0.027376 | 0.98214 | -0.34323 | 0.98191 | -0.34781 | 7.5208
134 | 0.0056687 | 0.0014207 | -0.0056683 | -0.0014206 | 3.7732e-07 | 6.8696e-08 | 0.0085863 | 0.0085863 | 0.0085863 | 0.98239 | -0.33828 | 0.98232 | -0.33968 | 2.3589
135 | -0.063782 | -0.016012 | 0.063907 | 0.016091 | 0.0001244 | 7.916e-05 | 0.096488 | 0.096488 | 0.096488 | 0.98374 | -0.31204 | 0.98583 | -0.27124 | 26.5076
136 | 0.0056003 | 0.0014034 | -0.0055999 | -0.0014033 | 3.6075e-07 | 6.0686e-08 | 0.008471 | 0.0084711 | 0.0084711 | 0.98374 | -0.31204 | 0.98367 | -0.31339 | 2.3272
137 | 0.0035024 | 0.00087774 | -0.0035024 | -0.00087778 | 7.2341e-08 | -4.0836e-08 | 0.0052997 | 0.0052998 | 0.0052998 | 0.98338 | -0.31895 | 0.98336 | -0.31938 | 1.456
138 | 0.012625 | 0.0031601 | -0.012605 | -0.0031492 | 1.9947e-05 | 1.0931e-05 | 0.019131 | 0.019132 | 0.019132 | 0.98191 | -0.34781 | 0.98021 | -0.38105 | 5.256
139 | 0.0028313 | 0.00070942 | -0.0028312 | -0.00070957 | 1.2558e-07 | -1.5136e-07 | 0.004283 | 0.0042831 | 0.0042831 | 0.98367 | -0.31339 | 0.98362 | -0.31433 | 1.1767
140 | 0.01067 | 0.0026642 | -0.010662 | -0.0026602 | 7.9757e-06 | 4.083e-06 | 0.016194 | 0.016195 | 0.016195 | 0.98021 | -0.38105 | 0.97941 | -0.3968 | 4.4491
141 | -0.0068426 | -0.0017027 | 0.0068441 | 0.0017032 | 1.4644e-06 | 4.8299e-07 | 0.010397 | 0.010397 | 0.010397 | 0.97889 | -0.40724 | 0.97911 | -0.40273 | 2.8564
142 | -0.0085709 | -0.0021355 | 0.0085733 | 0.0021366 | 2.4095e-06 | 1.0653e-06 | 0.013021 | 0.013021 | 0.013021 | 0.97911 | -0.40273 | 0.97941 | -0.3968 | 3.5773
143 | 0.0017268 | 0.00043236 | -0.0017267 | -0.00043276 | 9.5144e-08 | -4.0242e-07 | 0.0026242 | 0.0026244 | 0.0026244 | 0.97911 | -0.40273 | 0.97906 | -0.40388 | 0.72098
144 | 0.0019155 | 0.0004797 | -0.0019154 | -0.00048005 | 9.6828e-08 | -3.4973e-07 | 0.0028593 | 0.0028594 | 0.0028594 | 0.99684 | -0.060899 | 0.99678 | -0.061961 | 0.78555
145 | 0.020002 | 0.0050167 | -0.019988 | -0.0050083 | 1.3944e-05 | 8.3901e-06 | 0.029989 | 0.029989 | 0.029989 | 0.9925 | -0.14264 | 0.99175 | -0.15727 | 8.2389
146 | -0.011968 | -0.002998 | 0.011968 | 0.0029983 | 4.8672e-07 | 2.5957e-07 | 0.017957 | 0.017957 | 0.017957 | 0.99168 | -0.15855 | 0.99173 | -0.1577 | 4.9334
147 | -0.016071 | -0.0040264 | 0.016071 | 0.0040266 | 3.2336e-07 | 1.8781e-07 | 0.024112 | 0.024112 | 0.024112 | 0.99173 | -0.1577 | 0.99175 | -0.15727 | 6.6243

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27905 | 0.071307

## res_load
| p_mw | q_mvar
0 | 0.0027287 | 0.00068389
1 | 0.013145 | 0.0032945
2 | 0.0054186 | 0.001358
3 | 0.0019125 | 0.00047931
4 | 0.019913 | 0.0049906
5 | 0.00078611 | 0.00019702
6 | 0.0013659 | 0.00034233
7 | 0.0024251 | 0.00060779
8 | 0.0020341 | 0.00050979
9 | 0.002472 | 0.00061953
10 | 0.0023297 | 0.00058387
11 | 0.01074 | 0.0026916
12 | 0.0022395 | 0.00056128
13 | 0.0023642 | 0.00059253
14 | 0.0014239 | 0.00035687
15 | 0.0047633 | 0.0011938
16 | 0.0057277 | 0.0014355
17 | 0.0074291 | 0.0018619
18 | 0.0019229 | 0.00048193
19 | 0.0032524 | 0.00081513
20 | 0.0074235 | 0.0018605
21 | 0.0016964 | 0.00042516
22 | 0.00066298 | 0.00016616
23 | 0.0018593 | 0.00046598
24 | 0.0062191 | 0.0015586
25 | 0.00083029 | 0.00020809
26 | 0.009919 | 0.0024859
27 | 0.0027638 | 0.00069267
28 | 0.0022247 | 0.00055755
29 | 0.002741 | 0.00068695
30 | 0.0060038 | 0.0015047
31 | 0.0022067 | 0.00055306
32 | 0.00074019 | 0.00018551
33 | 0.013476 | 0.0033774
34 | 0.0037144 | 0.00093091
35 | 0.0014088 | 0.00035307
36 | 0.018033 | 0.0045195
37 | 0.0022774 | 0.00057077
38 | 0.0012017 | 0.00030117
39 | 0.00022874 | 5.7327e-05
40 | 0.00043665 | 0.00010943
41 | 0.00024722 | 6.1959e-05
42 | 0.00036858 | 9.2374e-05
43 | 0.00035346 | 8.8586e-05
44 | 0.00057433 | 0.00014394
45 | 0.00014728 | 3.6912e-05
46 | 0.00015148 | 3.7965e-05
47 | 0.00040128 | 0.00010057
48 | 0.000203 | 5.0878e-05
49 | 0.00036647 | 9.1846e-05
50 | 0.00015785 | 3.956e-05
51 | 0.00029117 | 7.2973e-05
52 | 0.00015721 | 3.9402e-05
53 | 0.00018501 | 4.6368e-05
54 | 0.00021253 | 5.3264e-05
55 | 0.0040722 | 0.0010206
56 | 0.0054956 | 0.0013773
57 | 0.0004228 | 0.00010596
58 | 0.00018951 | 4.7497e-05
59 | 0.00020492 | 5.1357e-05
60 | 0.00049311 | 0.00012358
61 | 0.0004826 | 0.00012095
62 | 0.00040442 | 0.00010136
63 | 0.00039738 | 9.9592e-05
64 | 0.00035889 | 8.9947e-05
65 | 0.004994 | 0.0012516
66 | 0.00032217 | 8.0743e-05
67 | 0.00016941 | 4.2457e-05
68 | 0.00016703 | 4.1861e-05
69 | 0.00054809 | 0.00013736
70 | 0.00016257 | 4.0744e-05
71 | 0.00038428 | 9.631e-05
72 | 0.0038699 | 0.00096988
73 | 0.0037366 | 0.00093648
74 | 0.0070999 | 0.0017794
75 | 0.0020426 | 0.00051193
76 | 0.0054405 | 0.0013635
77 | 0.0056683 | 0.0014206
78 | 0.00346 | 0.00086715
79 | 0.0027686 | 0.00069387
80 | 0.0035024 | 0.00087778
81 | 0.0019349 | 0.00048494
82 | 0.0028312 | 0.00070957
83 | 0.0013304 | 0.00033342
84 | 0.002089 | 0.00052355
85 | 0.0019154 | 0.00048005
86 | 0.0017267 | 0.00043276
87 | 0.0027711 | 0.00069452
88 | 0.0066129 | 0.0016573
89 | 0.0041021 | 0.0010281
90 | 0.003917 | 0.00098171
91 | 0.0022331 | 0.00055966

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1