## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-73_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-73_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-73_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-73_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-73_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-73_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1630-73_0_8_node_20 | 0.4 | n |  | TRUE
7 | bus_LV_1630-73_0_8_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_1630-73_0_8_node_19 | 0.4 | n |  | TRUE
9 | bus_LV_1630-73_0_8_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1630-73_0_8_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1630-73_0_8_node_44 | 0.4 | n |  | TRUE
12 | bus_LV_1630-73_0_8_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1630-73_0_8_node_41 | 0.4 | n |  | TRUE
14 | bus_LV_1630-73_0_8_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_1630-73_0_8_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_1630-73_0_8_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_1630-73_0_8_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1630-73_0_8_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1630-73_0_8_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1630-73_0_8_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1630-73_0_8_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_1630-73_0_8_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1630-73_0_8_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_1630-73_0_8_node_49 | 0.4 | n |  | TRUE
25 | bus_LV_1630-73_0_8_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1630-73_0_8_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1630-73_0_8_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_1630-73_0_8_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1630-73_0_8_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1630-73_0_8_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1630-73_0_8_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_1630-73_0_8_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_1630-73_0_8_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_1630-73_0_8_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_1630-73_0_8_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_1630-73_0_8_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_1630-73_0_8_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_1630-73_0_8_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_1630-73_0_8_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1630-73_0_8_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_1630-73_0_8_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_1630-73_0_8_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_1630-73_0_8_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_1630-73_0_8_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_1630-73_0_8_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_1630-73_0_8_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_1630-73_0_8_node_72 | 0.4 | n |  | TRUE
48 | bus_LV_1630-73_0_8_node_71 | 0.4 | n |  | TRUE
49 | bus_LV_1630-73_0_8_node_75 | 0.4 | n |  | TRUE
50 | bus_LV_1630-73_0_8_node_58 | 0.4 | n |  | TRUE
51 | bus_LV_1630-73_0_8_node_57 | 0.4 | n |  | TRUE
52 | bus_LV_1630-73_0_8_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_1630-73_0_8_node_74 | 0.4 | n |  | TRUE
54 | bus_LV_1630-73_0_8_node_54 | 0.4 | n |  | TRUE
55 | bus_LV_1630-73_0_8_node_70 | 0.4 | n |  | TRUE
56 | bus_LV_1630-73_0_8_node_66 | 0.4 | n |  | TRUE
57 | bus_LV_1630-73_0_8_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_1630-73_0_8_node_51 | 0.4 | n |  | TRUE
59 | bus_LV_1630-73_0_8_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_1630-73_0_8_node_53 | 0.4 | n |  | TRUE
61 | bus_LV_1630-73_0_8_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_1630-73_0_8_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_1630-73_0_8_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_1630-73_0_8_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_1630-73_0_8_node_73 | 0.4 | n |  | TRUE
66 | bus_LV_1630-73_0_8_node_67 | 0.4 | n |  | TRUE
67 | bus_LV_1630-73_0_8_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_1630-73_0_8_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_1630-73_0_8_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_1630-73_0_8_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_1630-73_0_8_node_69 | 0.4 | n |  | TRUE
72 | bus_LV_1630-73_0_8_node_45 | 0.4 | n |  | TRUE
73 | bus_LV_1630-73_0_8_node_46 | 0.4 | n |  | TRUE
74 | bus_LV_1630-73_0_8_node_48 | 0.4 | n |  | TRUE
75 | bus_MV_152_0_node_123 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-73_0_8_load_0 | 0 | 0.008888 | 0.0022275 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-73_0_8_load_1 | 1 | 0.0080454 | 0.0020164 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-73_0_8_load_4 | 4 | 0.010712 | 0.0026847 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-73_0_8_load_5 | 5 | 0.0079292 | 0.0019873 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-73_0_8_load_22 | 7 | 0.061263 | 0.015354 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-73_0_8_load_7 | 10 | 0.0071456 | 0.0017909 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-73_0_8_load_44 | 11 | 0.0068636 | 0.0017202 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-73_0_8_load_42 | 14 | 0.0024206 | 0.00060665 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-73_0_8_load_39 | 15 | 0.0091684 | 0.0022978 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-73_0_8_load_10 | 17 | 0.0075256 | 0.0018861 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-73_0_8_load_11 | 18 | 0.013056 | 0.0032721 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-73_0_8_load_12 | 19 | 0.010715 | 0.0026854 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-73_0_8_load_13 | 20 | 0.0071445 | 0.0017906 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-73_0_8_load_30 | 21 | 0.01059 | 0.0026541 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-73_0_8_load_29 | 23 | 0.016664 | 0.0041763 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-73_0_8_load_49 | 24 | 0.016657 | 0.0041746 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-73_0_8_load_14 | 25 | 0.0071512 | 0.0017923 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-73_0_8_load_15 | 26 | 0.00794 | 0.00199 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-73_0_8_load_31 | 27 | 0.011464 | 0.0028731 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-73_0_8_load_16 | 28 | 0.0013185 | 0.00033045 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-73_0_8_load_17 | 29 | 0.062181 | 0.015584 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-73_0_8_load_18 | 30 | 0.0013766 | 0.000345 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-73_0_8_load_32 | 33 | 0.0082367 | 0.0020643 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-73_0_8_load_25 | 35 | 0.045191 | 0.011326 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-73_0_8_load_43 | 37 | 0.0013307 | 0.0003335 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-73_0_8_load_40 | 38 | 0.002815 | 0.00070552 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-73_0_8_load_37 | 39 | 0.0012836 | 0.00032171 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-73_0_8_load_26 | 41 | 0.066681 | 0.016712 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-73_0_8_load_27 | 44 | 0.04865 | 0.012193 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-73_0_8_load_38 | 46 | 0.0027864 | 0.00069833 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-73_0_8_load_72 | 47 | 0.00048771 | 0.00012223 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1630-73_0_8_load_75 | 49 | 0.00084407 | 0.00021154 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1630-73_0_8_load_65 | 52 | 0.0037446 | 0.00093849 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1630-73_0_8_load_74 | 53 | 0.00076418 | 0.00019152 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1630-73_0_8_load_70 | 55 | 0.0031083 | 0.00077901 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1630-73_0_8_load_68 | 57 | 0.0022154 | 0.00055524 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1630-73_0_8_load_51 | 58 | 0.002343 | 0.00058722 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1630-73_0_8_load_52 | 59 | 0.00059889 | 0.0001501 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1630-73_0_8_load_60 | 64 | 0.00039068 | 9.7913e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1630-73_0_8_load_73 | 65 | 0.00092421 | 0.00023163 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1630-73_0_8_load_67 | 66 | 0.00071072 | 0.00017812 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1630-73_0_8_load_61 | 68 | 0.0059062 | 0.0014802 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1630-73_0_8_load_62 | 69 | 0.0012419 | 0.00031126 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1630-73_0_8_load_69 | 71 | 0.0005847 | 0.00014654 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1630-73_0_8_load_45 | 72 | 0.03212 | 0.00805 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1630-73_0_8_load_46 | 73 | 0.052416 | 0.013137 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1630-73_0_8_load_48 | 74 | 0.021704 | 0.0054395 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-73_0_8_line_0 |  | 0 | 1 | 0.069781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-73_0_8_line_1 |  | 0 | 2 | 0.0082072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-73_0_8_line_2 |  | 1 | 3 | 0.028682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-73_0_8_line_3 |  | 2 | 4 | 0.020009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-73_0_8_line_4 |  | 2 | 5 | 0.017127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-73_0_8_line_5 |  | 3 | 9 | 0.042137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-73_0_8_line_6 |  | 5 | 10 | 0.009426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-73_0_8_line_7 |  | 6 | 7 | 0.020325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1630-73_0_8_line_8 |  | 6 | 8 | 0.044554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_1630-73_0_8_line_9 |  | 7 | 34 | 0.013933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1630-73_0_8_line_10 |  | 8 | 31 | 0.046035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-73_0_8_line_11 |  | 8 | 30 | 0.0177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-73_0_8_line_12 |  | 9 | 11 | 0.056687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-73_0_8_line_13 |  | 10 | 12 | 0.010273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-73_0_8_line_14 |  | 12 | 16 | 0.029182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-73_0_8_line_15 |  | 12 | 17 | 0.0011664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-73_0_8_line_16 |  | 13 | 14 | 0.013741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-73_0_8_line_17 |  | 13 | 15 | 0.026648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-73_0_8_line_18 |  | 14 | 57 | 0.16846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-73_0_8_line_19 |  | 15 | 38 | 0.048221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-73_0_8_line_20 |  | 16 | 18 | 0.01105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-73_0_8_line_21 |  | 16 | 19 | 0.0048326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-73_0_8_line_22 |  | 17 | 20 | 0.010818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-73_0_8_line_23 |  | 19 | 21 | 0.033451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-73_0_8_line_24 |  | 20 | 26 | 0.0167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-73_0_8_line_25 |  | 21 | 27 | 0.012497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-73_0_8_line_26 |  | 22 | 23 | 0.015566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1630-73_0_8_line_27 |  | 22 | 24 | 0.014916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-73_0_8_line_28 |  | 22 | 25 | 0.064867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-73_0_8_line_29 |  | 23 | 42 | 0.025238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1630-73_0_8_line_30 |  | 24 | 43 | 0.044577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-73_0_8_line_31 |  | 25 | 26 | 0.010998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-73_0_8_line_32 |  | 28 | 29 | 0.0085992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-73_0_8_line_33 |  | 28 | 30 | 0.024602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-73_0_8_line_34 |  | 31 | 32 | 0.037252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1630-73_0_8_line_35 |  | 31 | 33 | 0.025213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-73_0_8_line_36 |  | 32 | 39 | 0.01101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-73_0_8_line_37 |  | 32 | 40 | 0.007712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-73_0_8_line_38 |  | 32 | 36 | 0.062198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-73_0_8_line_39 |  | 34 | 35 | 0.015975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1630-73_0_8_line_40 |  | 35 | 41 | 0.012766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1630-73_0_8_line_41 |  | 36 | 37 | 0.008742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-73_0_8_line_42 |  | 36 | 38 | 0.043067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-73_0_8_line_43 |  | 40 | 45 | 0.011293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-73_0_8_line_44 |  | 41 | 42 | 0.013942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1630-73_0_8_line_45 |  | 42 | 44 | 0.016627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1630-73_0_8_line_46 |  | 43 | 72 | 0.01552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1630-73_0_8_line_47 |  | 45 | 46 | 0.068498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1630-73_0_8_line_48 |  | 47 | 48 | 0.038156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1630-73_0_8_line_49 |  | 48 | 56 | 0.058165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1630-73_0_8_line_50 |  | 49 | 50 | 0.047591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1630-73_0_8_line_51 |  | 50 | 53 | 0.009632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1630-73_0_8_line_52 |  | 50 | 54 | 0.16156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1630-73_0_8_line_53 |  | 50 | 51 | 0.041796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1630-73_0_8_line_54 |  | 51 | 52 | 0.11738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1630-73_0_8_line_55 |  | 52 | 55 | 0.023885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1630-73_0_8_line_56 |  | 54 | 62 | 0.13428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1630-73_0_8_line_57 |  | 54 | 59 | 0.010637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1630-73_0_8_line_58 |  | 55 | 56 | 0.008902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1630-73_0_8_line_59 |  | 57 | 70 | 0.14492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1630-73_0_8_line_60 |  | 58 | 59 | 0.021742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1630-73_0_8_line_61 |  | 58 | 60 | 0.019072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1630-73_0_8_line_62 |  | 60 | 61 | 0.16636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1630-73_0_8_line_63 |  | 61 | 63 | 0.097022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1630-73_0_8_line_64 |  | 61 | 64 | 0.069288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1630-73_0_8_line_65 |  | 62 | 65 | 0.045634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1630-73_0_8_line_66 |  | 63 | 66 | 0.02197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1630-73_0_8_line_67 |  | 63 | 67 | 0.049038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1630-73_0_8_line_68 |  | 66 | 71 | 0.0051317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1630-73_0_8_line_69 |  | 67 | 70 | 0.13495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1630-73_0_8_line_70 |  | 67 | 68 | 0.039092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1630-73_0_8_line_71 |  | 68 | 69 | 0.041425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1630-73_0_8_line_72 |  | 72 | 73 | 0.012551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1630-73_0_8_line_73 |  | 73 | 74 | 0.0064412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-73_0_8_trafo_23 | 0.63 MVA 20/0.4 kV | 75 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2723006.3328 | 1216694.6017 | 2723008.0593 | 1216694.2154 | 2723013.3994 | 1216693.425 | 2723018.9011 | 1216694.0056 | 2723032.5062 | 1216698.2564 | 2723038.7157 | 1216699.4967 | 2723044.4887 | 1216698.7041 | 2723055.1308 | 1216691.6183 | 2723059.3874 | 1216689.9716 | 2723063.918 | 1216689.765 | 2723072.6909 | 1216690.2027
1 | 2722998.3237 | 1216696.3939 | 2723006.3328 | 1216694.6017
2 | 2723100.532 | 1216687.8974 | 2723097.597 | 1216689.905 | 2723093.2104 | 1216691.2265 | 2723072.6909 | 1216690.2027
3 | 2722998.3237 | 1216696.3939 | 2722999.8573 | 1216705.9775 | 2723004.8275 | 1216715.0093
4 | 2722998.3237 | 1216696.3939 | 2722981.6087 | 1216700.1278
5 | 2723114.3003 | 1216650.0857 | 2723110.5121 | 1216652.9541 | 2723107.5085 | 1216657.1732 | 2723105.9812 | 1216661.9898 | 2723104.9375 | 1216677.9473 | 2723104.2893 | 1216682.1149 | 2723102.7967 | 1216685.2532 | 2723100.532 | 1216687.8974
6 | 2722972.5258 | 1216702.5783 | 2722975.4497 | 1216701.5037 | 2722981.6087 | 1216700.1278
7 | 2722877.9259 | 1216663.7074 | 2722866.8091 | 1216665.1015 | 2722867.3302 | 1216674.2074
8 | 2722877.9259 | 1216663.7074 | 2722862.9877 | 1216621.7224
9 | 2722865.9808 | 1216687.9467 | 2722867.6743 | 1216680.22 | 2722867.3302 | 1216674.2074
10 | 2722862.9877 | 1216621.7224 | 2722849.2058 | 1216577.7931
11 | 2722862.9877 | 1216621.7224 | 2722845.7758 | 1216625.8499
12 | 2723058.6732 | 1216644.0434 | 2723101.4342 | 1216644.6157 | 2723110.719 | 1216647.721 | 2723114.3003 | 1216650.0857
13 | 2722963.6426 | 1216707.6426 | 2722970.0929 | 1216703.4725 | 2722972.5258 | 1216702.5783
14 | 2722963.6426 | 1216707.6426 | 2722970.1561 | 1216736.088
15 | 2722963.6426 | 1216707.6426 | 2722962.7179 | 1216708.3536
16 | 2722980.3374 | 1216462.2187 | 2722985.3669 | 1216475.0102
17 | 2722985.3669 | 1216475.0102 | 2722976.6285 | 1216478.8995 | 2722964.3655 | 1216480.9815 | 2722959.8551 | 1216482.091
18 | 2722980.3374 | 1216462.2187 | 2722937.3635 | 1216299.328
19 | 2722959.8551 | 1216482.091 | 2722956.4418 | 1216482.9307 | 2722944.2956 | 1216487.8172 | 2722937.3208 | 1216491.9989 | 2722925.426 | 1216500.8938 | 2722917.8412 | 1216505.007
20 | 2722970.1561 | 1216736.088 | 2722981.0299 | 1216733.9551
21 | 2722970.1561 | 1216736.088 | 2722971.2351 | 1216740.7986
22 | 2722962.7179 | 1216708.3536 | 2722954.1419 | 1216714.9471
23 | 2722971.2351 | 1216740.7986 | 2722974.1201 | 1216753.3943 | 2722955.4112 | 1216761.846
24 | 2722940.9024 | 1216725.1261 | 2722954.1419 | 1216714.9471
25 | 2722955.4112 | 1216761.846 | 2722944.0229 | 1216766.9907
26 | 2722868.0094 | 1216741.2855 | 2722852.4505 | 1216740.8088
27 | 2722868.0094 | 1216741.2855 | 2722866.7396 | 1216756.1476
28 | 2722868.0094 | 1216741.2855 | 2722932.1837 | 1216731.8295
29 | 2722851.277 | 1216715.5984 | 2722852.4505 | 1216740.8088
30 | 2722865.1438 | 1216800.6725 | 2722865.1079 | 1216789.5298 | 2722865.7266 | 1216768.0036 | 2722866.7396 | 1216756.1476
31 | 2722932.1837 | 1216731.8295 | 2722940.9024 | 1216725.1261
32 | 2722834.024 | 1216646.289 | 2722834.024 | 1216646.289 | 2722832.0815 | 1216637.9121
33 | 2722845.7758 | 1216625.8499 | 2722830.1532 | 1216629.5962 | 2722832.0815 | 1216637.9121
34 | 2722837.8009 | 1216542.3306 | 2722841.882 | 1216555.4582 | 2722849.2058 | 1216577.7931
35 | 2722849.2058 | 1216577.7931 | 2722834.4696 | 1216580.1246 | 2722831.2448 | 1216570.3494
36 | 2722837.8009 | 1216542.3306 | 2722848.1842 | 1216538.5861
37 | 2722835.5073 | 1216534.9665 | 2722837.8009 | 1216542.3306
38 | 2722837.8009 | 1216542.3306 | 2722841.882 | 1216555.4582 | 2722862.0421 | 1216544.5986 | 2722871.5315 | 1216538.534 | 2722883.0155 | 1216530.0308
39 | 2722865.9808 | 1216687.9467 | 2722850.035 | 1216688.9187 | 2722850.035 | 1216688.9187
40 | 2722850.035 | 1216688.9187 | 2722850.6287 | 1216701.6713
41 | 2722886.8021 | 1216537.915 | 2722883.0155 | 1216530.0308
42 | 2722883.0155 | 1216530.0308 | 2722901.4286 | 1216514.4094 | 2722909.1889 | 1216509.6991 | 2722917.8412 | 1216505.007
43 | 2722835.5073 | 1216534.9665 | 2722832.1985 | 1216524.1677
44 | 2722851.277 | 1216715.5984 | 2722850.6287 | 1216701.6713
45 | 2722851.277 | 1216715.5984 | 2722834.677 | 1216716.5384
46 | 2722865.1438 | 1216800.6725 | 2722849.7712 | 1216802.8066
47 | 2722832.1985 | 1216524.1677 | 2722895.1403 | 1216496.7327
48 | 2722772.8994 | 1216301.9625 | 2722759.5079 | 1216304.244 | 2722750.9325 | 1216305.3794 | 2722734.921 | 1216306.1725
49 | 2722772.8994 | 1216301.9625 | 2722770.4489 | 1216289.6691 | 2722763.609 | 1216244.56
50 | 2722683.7139 | 1216114.8701 | 2722708.3682 | 1216119.2921 | 2722712.9027 | 1216119.2854 | 2722731.0467 | 1216118.9698
51 | 2722731.0467 | 1216118.9698 | 2722730.7285 | 1216109.3447
52 | 2722731.0467 | 1216118.9698 | 2722749.639 | 1216118.6413 | 2722745.8202 | 1216031.9511 | 2722746.7247 | 1215994.6964 | 2722764.0984 | 1215987.1817
53 | 2722731.0467 | 1216118.9698 | 2722749.639 | 1216118.6413 | 2722772.8229 | 1216117.7514
54 | 2722772.8229 | 1216117.7514 | 2722782.4505 | 1216193.8087 | 2722766.2821 | 1216195.5659 | 2722769.4015 | 1216219.8177
55 | 2722769.4015 | 1216219.8177 | 2722772.4486 | 1216243.5079
56 | 2722752.3798 | 1215879.5014 | 2722747.7302 | 1215953.2739 | 2722746.7247 | 1215994.6964 | 2722764.0984 | 1215987.1817
57 | 2722764.0984 | 1215987.1817 | 2722770.7248 | 1215995.5024
58 | 2722763.609 | 1216244.56 | 2722772.4486 | 1216243.5079
59 | 2723070.6645 | 1216245.6482 | 2723064.0867 | 1216251.9172 | 2723014.464 | 1216267.5495 | 2722973.0046 | 1216282.5279 | 2722945.3926 | 1216297.8035 | 2722937.3635 | 1216299.328
60 | 2722792.1895 | 1215992.043 | 2722770.7248 | 1215995.5024
61 | 2722802.7813 | 1215981.6853 | 2722802.4118 | 1215990.3956 | 2722792.1895 | 1215992.043
62 | 2722967.1368 | 1215984.3755 | 2722953.5594 | 1215988.9991 | 2722933.8007 | 1215993.9287 | 2722916.6082 | 1215995.2307 | 2722900.3956 | 1215995.0519 | 2722883.8945 | 1215993.7662 | 2722815.1934 | 1215981.9968 | 2722802.7813 | 1215981.6853
63 | 2722967.1368 | 1215984.3755 | 2722980.0904 | 1216022.1054 | 2723001.5472 | 1216075.0781
64 | 2722967.1368 | 1215984.3755 | 2722961.2318 | 1215966.1396 | 2722940.2432 | 1215946.3803 | 2722936.4183 | 1215941.8089 | 2722932.1822 | 1215936.5508 | 2722929.7933 | 1215931.5866 | 2722928.7198 | 1215928.7085
65 | 2722752.3798 | 1215879.5014 | 2722736.7938 | 1215878.3907 | 2722708.084 | 1215887.5401
66 | 2723001.5472 | 1216075.0781 | 2722979.5887 | 1216075.7785
67 | 2723020.2598 | 1216120.4216 | 2723001.5472 | 1216075.0781
68 | 2722974.4596 | 1216075.9421 | 2722979.5887 | 1216075.7785
69 | 2723020.2598 | 1216120.4216 | 2723070.6645 | 1216245.6482
70 | 2723020.2598 | 1216120.4216 | 2722981.2138 | 1216122.3207
71 | 2722981.2138 | 1216122.3207 | 2722970.0274 | 1216122.8648 | 2722965.0815 | 1216122.5625 | 2722960.7595 | 1216121.4725 | 2722956.5831 | 1216119.5849 | 2722953.2859 | 1216117.0483 | 2722946.5633 | 1216112.3059 | 2722942.7975 | 1216111.5384
72 | 2722849.7712 | 1216802.8066 | 2722837.3394 | 1216804.5324
73 | 2722837.3394 | 1216804.5324 | 2722830.9593 | 1216805.4181

## bus_geodata
| x | y | coords
0 | 2723006.3328 | 1216694.6017
1 | 2723072.6909 | 1216690.2027
2 | 2722998.3237 | 1216696.3939
3 | 2723100.532 | 1216687.8974
4 | 2723004.8275 | 1216715.0093
5 | 2722981.6087 | 1216700.1278
6 | 2722877.9259 | 1216663.7074
7 | 2722867.3302 | 1216674.2074
8 | 2722862.9877 | 1216621.7224
9 | 2723114.3003 | 1216650.0857
10 | 2722972.5258 | 1216702.5783
11 | 2723058.6732 | 1216644.0434
12 | 2722963.6426 | 1216707.6426
13 | 2722985.3669 | 1216475.0102
14 | 2722980.3374 | 1216462.2187
15 | 2722959.8551 | 1216482.091
16 | 2722970.1561 | 1216736.088
17 | 2722962.7179 | 1216708.3536
18 | 2722981.0299 | 1216733.9551
19 | 2722971.2351 | 1216740.7986
20 | 2722954.1419 | 1216714.9471
21 | 2722955.4112 | 1216761.846
22 | 2722868.0094 | 1216741.2855
23 | 2722852.4505 | 1216740.8088
24 | 2722866.7396 | 1216756.1476
25 | 2722932.1837 | 1216731.8295
26 | 2722940.9024 | 1216725.1261
27 | 2722944.0229 | 1216766.9907
28 | 2722832.0815 | 1216637.9121
29 | 2722834.024 | 1216646.289
30 | 2722845.7758 | 1216625.8499
31 | 2722849.2058 | 1216577.7931
32 | 2722837.8009 | 1216542.3306
33 | 2722831.2448 | 1216570.3494
34 | 2722865.9808 | 1216687.9467
35 | 2722850.035 | 1216688.9187
36 | 2722883.0155 | 1216530.0308
37 | 2722886.8021 | 1216537.915
38 | 2722917.8412 | 1216505.007
39 | 2722848.1842 | 1216538.5861
40 | 2722835.5073 | 1216534.9665
41 | 2722850.6287 | 1216701.6713
42 | 2722851.277 | 1216715.5984
43 | 2722865.1438 | 1216800.6725
44 | 2722834.677 | 1216716.5384
45 | 2722832.1985 | 1216524.1677
46 | 2722895.1403 | 1216496.7327
47 | 2722734.921 | 1216306.1725
48 | 2722772.8994 | 1216301.9625
49 | 2722683.7139 | 1216114.8701
50 | 2722731.0467 | 1216118.9698
51 | 2722772.8229 | 1216117.7514
52 | 2722769.4015 | 1216219.8177
53 | 2722730.7285 | 1216109.3447
54 | 2722764.0984 | 1215987.1817
55 | 2722772.4486 | 1216243.5079
56 | 2722763.609 | 1216244.56
57 | 2722937.3635 | 1216299.328
58 | 2722792.1895 | 1215992.043
59 | 2722770.7248 | 1215995.5024
60 | 2722802.7813 | 1215981.6853
61 | 2722967.1368 | 1215984.3755
62 | 2722752.3798 | 1215879.5014
63 | 2723001.5472 | 1216075.0781
64 | 2722928.7198 | 1215928.7085
65 | 2722708.084 | 1215887.5401
66 | 2722979.5887 | 1216075.7785
67 | 2723020.2598 | 1216120.4216
68 | 2722981.2138 | 1216122.3207
69 | 2722942.7975 | 1216111.5384
70 | 2723070.6645 | 1216245.6482
71 | 2722974.4596 | 1216075.9421
72 | 2722849.7712 | 1216802.8066
73 | 2722837.3394 | 1216804.5324
74 | 2722830.9593 | 1216805.4181
75 | 2722872.3668 | 1216692.7821

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97988 | -0.38746 | 0.008888 | 0.0022275
1 | 0.97891 | -0.40637 | 0.0080454 | 0.0020164
2 | 0.98006 | -0.38391 | 0 | 0
3 | 0.97873 | -0.40995 | 0 | 0
4 | 0.97986 | -0.3878 | 0.010712 | 0.0026847
5 | 0.98061 | -0.37319 | 0.0079292 | 0.0019873
6 | 0.99889 | -0.021186 | 0 | 0
7 | 0.99943 | -0.01082 | 0.061263 | 0.015354
8 | 0.9973 | -0.051549 | 0 | 0
9 | 0.97846 | -0.41522 | 0 | 0
10 | 0.98098 | -0.36594 | 0.0071456 | 0.0017909
11 | 0.9781 | -0.4223 | 0.0068636 | 0.0017202
12 | 0.98145 | -0.35672 | 0 | 0
13 | 0.98755 | -0.23831 | 0 | 0
14 | 0.98721 | -0.24478 | 0.0024206 | 0.00060665
15 | 0.9882 | -0.22577 | 0.0091684 | 0.0022978
16 | 0.98021 | -0.38095 | 0 | 0
17 | 0.98155 | -0.3547 | 0.0075256 | 0.0018861
18 | 0.98008 | -0.38356 | 0.013056 | 0.0032721
19 | 0.98006 | -0.38382 | 0.010715 | 0.0026854
20 | 0.98258 | -0.33458 | 0.0071445 | 0.0017906
21 | 0.97938 | -0.39722 | 0.01059 | 0.0026541
22 | 0.993 | -0.13349 | 0 | 0
23 | 0.99478 | -0.09942 | 0.016664 | 0.0041763
24 | 0.99131 | -0.16595 | 0.016657 | 0.0041746
25 | 0.98548 | -0.27812 | 0.0071512 | 0.0017923
26 | 0.98428 | -0.30144 | 0.00794 | 0.00199
27 | 0.97925 | -0.39982 | 0.011464 | 0.0028731
28 | 0.99483 | -0.099166 | 0.0013185 | 0.00033045
29 | 0.99434 | -0.10859 | 0.062181 | 0.015584
30 | 0.99625 | -0.071693 | 0.0013766 | 0.000345
31 | 0.99509 | -0.093569 | 0 | 0
32 | 0.99359 | -0.12229 | 0 | 0
33 | 0.99491 | -0.097225 | 0.0082367 | 0.0020643
34 | 1 | 0 | -0.61051 | -0.15472
35 | 0.99844 | -0.02965 | 0.045191 | 0.011326
36 | 0.99131 | -0.16594 | 0 | 0
37 | 0.9913 | -0.16614 | 0.0013307 | 0.0003335
38 | 0.98978 | -0.19526 | 0.002815 | 0.00070552
39 | 0.99358 | -0.12254 | 0.0012836 | 0.00032171
40 | 0.99357 | -0.12267 | 0 | 0
41 | 0.99733 | -0.050883 | 0.066681 | 0.016712
42 | 0.99632 | -0.070044 | 0 | 0
43 | 0.98695 | -0.25032 | 0 | 0
44 | 0.99558 | -0.084258 | 0.04865 | 0.012193
45 | 0.99354 | -0.12322 | 0 | 0
46 | 0.99337 | -0.1266 | 0.0027864 | 0.00069833
47 | 0.97088 | -0.56423 | 0.00048771 | 0.00012223
48 | 0.9709 | -0.56388 | 0 | 0
49 | 0.97206 | -0.54083 | 0.00084407 | 0.00021154
50 | 0.9721 | -0.54009 | 0 | 0
51 | 0.97181 | -0.54576 | 0 | 0
52 | 0.97101 | -0.56168 | 0.0037446 | 0.00093849
53 | 0.97209 | -0.54023 | 0.00076418 | 0.00019152
54 | 0.97345 | -0.51342 | 0 | 0
55 | 0.97093 | -0.56327 | 0.0031083 | 0.00077901
56 | 0.97092 | -0.56335 | 0 | 0
57 | 0.98347 | -0.31711 | 0.0022154 | 0.00055524
58 | 0.97376 | -0.50729 | 0.002343 | 0.00058722
59 | 0.97355 | -0.51148 | 0.00059889 | 0.0001501
60 | 0.97399 | -0.50279 | 0 | 0
61 | 0.97597 | -0.46362 | 0 | 0
62 | 0.97333 | -0.51571 | 0 | 0
63 | 0.97717 | -0.44015 | 0 | 0
64 | 0.97595 | -0.46412 | 0.00039068 | 9.7913e-05
65 | 0.97329 | -0.51649 | 0.00092421 | 0.00023163
66 | 0.97714 | -0.44067 | 0.00071072 | 0.00017812
67 | 0.97783 | -0.42714 | 0 | 0
68 | 0.97757 | -0.43224 | 0.0059062 | 0.0014802
69 | 0.97753 | -0.43318 | 0.0012419 | 0.00031126
70 | 0.98055 | -0.37393 | 0 | 0
71 | 0.97714 | -0.44072 | 0.0005847 | 0.00014654
72 | 0.98543 | -0.27987 | 0.03212 | 0.00805
73 | 0.98457 | -0.29658 | 0.052416 | 0.013137
74 | 0.98444 | -0.29909 | 0.021704 | 0.0054395
75 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.014928 | 0.003746 | -0.014914 | -0.0037383 | 1.3449e-05 | 7.7293e-06 | 0.02267 | 0.022671 | 0.022671 | 0.97988 | -0.38746 | 0.97891 | -0.40637 | 6.2282
1 | -0.023816 | -0.0059735 | 0.02382 | 0.005976 | 4.0259e-06 | 2.4732e-06 | 0.036167 | 0.036167 | 0.036167 | 0.97988 | -0.38746 | 0.98006 | -0.38391 | 9.9361
2 | 0.0068688 | 0.0017219 | -0.0068676 | -0.0017215 | 1.1726e-06 | 3.8994e-07 | 0.010441 | 0.010441 | 0.010441 | 0.97891 | -0.40637 | 0.97873 | -0.40995 | 2.8685
3 | 0.010714 | 0.0026858 | -0.010712 | -0.0026847 | 1.9856e-06 | 1.0187e-06 | 0.016268 | 0.016268 | 0.016268 | 0.98006 | -0.38391 | 0.97986 | -0.3878 | 4.4691
4 | -0.034534 | -0.0086618 | 0.034552 | 0.0086729 | 1.7658e-05 | 1.1085e-05 | 0.052435 | 0.052435 | 0.052435 | 0.98006 | -0.38391 | 0.98061 | -0.37319 | 14.4052
5 | 0.0068676 | 0.0017215 | -0.0068659 | -0.0017209 | 1.7227e-06 | 5.7314e-07 | 0.010441 | 0.010441 | 0.010441 | 0.97873 | -0.40995 | 0.97846 | -0.41522 | 2.8685
6 | -0.042481 | -0.01066 | 0.042495 | 0.010669 | 1.469e-05 | 9.2829e-06 | 0.064467 | 0.064467 | 0.064467 | 0.98061 | -0.37319 | 0.98098 | -0.36594 | 17.7107
7 | -0.11779 | -0.029882 | 0.11784 | 0.029919 | 5.8748e-05 | 3.6534e-05 | 0.17559 | 0.17559 | 0.17559 | 0.99889 | -0.021186 | 0.99943 | -0.01082 | 12.0598
8 | 0.11779 | 0.029882 | -0.11761 | -0.029774 | 0.00017171 | 0.00010815 | 0.17559 | 0.17559 | 0.17559 | 0.99889 | -0.021186 | 0.9973 | -0.051549 | 16.0798
9 | -0.17911 | -0.045273 | 0.1792 | 0.045332 | 9.2978e-05 | 5.8775e-05 | 0.2668 | 0.2668 | 0.2668 | 0.99943 | -0.01082 | 1 | 0 | 18.3243
10 | 0.052565 | 0.013404 | -0.052458 | -0.013337 | 0.00010641 | 6.7502e-05 | 0.078511 | 0.078511 | 0.078511 | 0.9973 | -0.051549 | 0.99509 | -0.093569 | 21.5689
11 | 0.065049 | 0.01637 | -0.064987 | -0.01633 | 6.2556e-05 | 3.9805e-05 | 0.09708 | 0.097081 | 0.097081 | 0.9973 | -0.051549 | 0.99625 | -0.071693 | 26.6705
12 | 0.0068659 | 0.0017209 | -0.0068636 | -0.0017202 | 2.3177e-06 | 7.7156e-07 | 0.010441 | 0.010442 | 0.010442 | 0.97846 | -0.41522 | 0.9781 | -0.4223 | 2.8686
13 | -0.049641 | -0.01246 | 0.049663 | 0.012474 | 2.1847e-05 | 1.3852e-05 | 0.075306 | 0.075306 | 0.075306 | 0.98098 | -0.36594 | 0.98145 | -0.35672 | 20.6885
14 | 0.0459 | 0.011531 | -0.045847 | -0.011498 | 5.3011e-05 | 3.3559e-05 | 0.0696 | 0.0696 | 0.0696 | 0.98145 | -0.35672 | 0.98021 | -0.38095 | 19.121
15 | -0.095562 | -0.024006 | 0.095572 | 0.024011 | 9.1847e-06 | 5.8635e-06 | 0.14491 | 0.14491 | 0.14491 | 0.98145 | -0.35672 | 0.98155 | -0.3547 | 39.8094
16 | 0.026567 | 0.0067469 | -0.026559 | -0.0067417 | 8.2703e-06 | 5.1172e-06 | 0.040062 | 0.040062 | 0.040062 | 0.98755 | -0.23831 | 0.98721 | -0.24478 | 11.0061
17 | -0.026567 | -0.0067469 | 0.026583 | 0.0067568 | 1.6039e-05 | 9.9235e-06 | 0.040062 | 0.040062 | 0.040062 | 0.98755 | -0.23831 | 0.9882 | -0.22577 | 11.0061
18 | 0.024138 | 0.0061351 | -0.024054 | -0.0060836 | 8.3768e-05 | 5.1466e-05 | 0.036414 | 0.036414 | 0.036414 | 0.98721 | -0.24478 | 0.98347 | -0.31711 | 10.004
19 | -0.035751 | -0.0090546 | 0.035804 | 0.0090876 | 5.2471e-05 | 3.2963e-05 | 0.053868 | 0.053867 | 0.053868 | 0.9882 | -0.22577 | 0.98978 | -0.19526 | 14.7988
20 | 0.013058 | 0.003273 | -0.013056 | -0.0032721 | 1.6282e-06 | 9.0278e-07 | 0.019822 | 0.019822 | 0.019822 | 0.98021 | -0.38095 | 0.98008 | -0.38356 | 5.4457
21 | 0.032789 | 0.0082248 | -0.032784 | -0.008222 | 4.4904e-06 | 2.8129e-06 | 0.049778 | 0.049778 | 0.049778 | 0.98021 | -0.38095 | 0.98006 | -0.38382 | 13.6753
22 | -0.1031 | -0.025898 | 0.1032 | 0.025961 | 9.9121e-05 | 6.3301e-05 | 0.15631 | 0.15631 | 0.15631 | 0.98155 | -0.3547 | 0.98258 | -0.33458 | 42.9437
23 | 0.022069 | 0.0055366 | -0.022055 | -0.005528 | 1.4086e-05 | 8.5938e-06 | 0.03351 | 0.03351 | 0.03351 | 0.98006 | -0.38382 | 0.97938 | -0.39722 | 9.206
24 | -0.11034 | -0.027751 | 0.11052 | 0.027863 | 0.00017494 | 0.00011175 | 0.16713 | 0.16713 | 0.16713 | 0.98258 | -0.33458 | 0.98428 | -0.30144 | 45.9161
25 | 0.011465 | 0.0028739 | -0.011464 | -0.0028731 | 1.4221e-06 | 7.5289e-07 | 0.01742 | 0.01742 | 0.01742 | 0.97938 | -0.39722 | 0.97925 | -0.39982 | 4.7857
26 | -0.25035 | -0.063625 | 0.25076 | 0.063888 | 0.00041145 | 0.00026293 | 0.37546 | 0.37546 | 0.37546 | 0.993 | -0.13349 | 0.99478 | -0.09942 | 51.5748
27 | 0.12373 | 0.031334 | -0.12354 | -0.031211 | 0.00019254 | 0.00012303 | 0.18553 | 0.18553 | 0.18553 | 0.993 | -0.13349 | 0.99131 | -0.16595 | 50.9695
28 | 0.12662 | 0.032291 | -0.12574 | -0.03173 | 0.00087755 | 0.0005608 | 0.18994 | 0.18994 | 0.18994 | 0.993 | -0.13349 | 0.98548 | -0.27812 | 52.1802
29 | -0.26742 | -0.068064 | 0.2678 | 0.068305 | 0.0003793 | 0.00024144 | 0.40039 | 0.40039 | 0.40039 | 0.99478 | -0.09942 | 0.99632 | -0.070044 | 27.4993
30 | 0.10688 | 0.027036 | -0.10645 | -0.026761 | 0.00043076 | 0.00027511 | 0.16053 | 0.16053 | 0.16053 | 0.99131 | -0.16595 | 0.98695 | -0.25032 | 44.1007
31 | 0.11859 | 0.029938 | -0.11846 | -0.029853 | 0.00013235 | 8.4562e-05 | 0.17914 | 0.17914 | 0.17914 | 0.98548 | -0.27812 | 0.98428 | -0.30144 | 49.2138
32 | 0.062209 | 0.015602 | -0.062181 | -0.015584 | 2.7922e-05 | 1.7758e-05 | 0.093052 | 0.093052 | 0.093052 | 0.99483 | -0.099166 | 0.99434 | -0.10859 | 25.5639
33 | -0.063527 | -0.015932 | 0.06361 | 0.015985 | 8.3305e-05 | 5.2995e-05 | 0.095025 | 0.095024 | 0.095025 | 0.99483 | -0.099166 | 0.99625 | -0.071693 | 26.1057
34 | 0.04422 | 0.011272 | -0.044159 | -0.011233 | 6.1206e-05 | 3.8689e-05 | 0.066192 | 0.066192 | 0.066192 | 0.99509 | -0.093569 | 0.99359 | -0.12229 | 18.1846
35 | 0.0082382 | 0.0020649 | -0.0082367 | -0.0020643 | 1.4349e-06 | 5.9083e-07 | 0.012319 | 0.012319 | 0.012319 | 0.99509 | -0.093569 | 0.99491 | -0.097225 | 3.3844
36 | 0.0012837 | 0.00032158 | -0.0012836 | -0.00032171 | 1.5258e-08 | -1.3283e-07 | 0.0019224 | 0.0019224 | 0.0019224 | 0.99359 | -0.12229 | 0.99358 | -0.12254 | 0.52814
37 | 0.0027869 | 0.00069756 | -0.0027869 | -0.00069763 | 5.0373e-08 | -6.7643e-08 | 0.0041735 | 0.0041735 | 0.0041735 | 0.99359 | -0.12229 | 0.99357 | -0.12267 | 1.1466
38 | 0.040088 | 0.010214 | -0.040004 | -0.010161 | 8.4237e-05 | 5.3108e-05 | 0.060096 | 0.060097 | 0.060097 | 0.99359 | -0.12229 | 0.99131 | -0.16594 | 16.5101
39 | 0.42966 | 0.10939 | -0.42904 | -0.10899 | 0.00061334 | 0.0003917 | 0.63994 | 0.63994 | 0.63994 | 1 | 0 | 0.99844 | -0.02965 | 43.9518
40 | 0.38385 | 0.097668 | -0.38346 | -0.097417 | 0.0003924 | 0.00025047 | 0.57259 | 0.57259 | 0.57259 | 0.99844 | -0.02965 | 0.99733 | -0.050883 | 39.3262
41 | 0.0013307 | 0.00033339 | -0.0013307 | -0.0003335 | 1.3079e-08 | -1.0433e-07 | 0.0019974 | 0.0019974 | 0.0019974 | 0.99131 | -0.16594 | 0.9913 | -0.16614 | 0.54875
42 | 0.038673 | 0.0098274 | -0.038619 | -0.0097931 | 5.4516e-05 | 3.4336e-05 | 0.058099 | 0.058099 | 0.058099 | 0.99131 | -0.16594 | 0.98978 | -0.19526 | 15.9614
43 | 0.0027869 | 0.00069763 | -0.0027868 | -0.00069773 | 7.3764e-08 | -9.9044e-08 | 0.0041735 | 0.0041735 | 0.0041735 | 0.99357 | -0.12267 | 0.99354 | -0.12322 | 1.1466
44 | 0.31678 | 0.080706 | -0.31649 | -0.080519 | 0.00029256 | 0.00018651 | 0.4731 | 0.4731 | 0.4731 | 0.99733 | -0.050883 | 0.99632 | -0.070044 | 32.4932
45 | 0.048683 | 0.012214 | -0.04865 | -0.012193 | 3.2965e-05 | 2.0881e-05 | 0.072712 | 0.072712 | 0.072712 | 0.99632 | -0.070044 | 0.99558 | -0.084258 | 19.976
46 | 0.10645 | 0.026761 | -0.1063 | -0.026666 | 0.00014997 | 9.5785e-05 | 0.16053 | 0.16053 | 0.16053 | 0.98695 | -0.25032 | 0.98543 | -0.27987 | 44.1007
47 | 0.0027868 | 0.00069773 | -0.0027864 | -0.00069833 | 4.4746e-07 | -6.0055e-07 | 0.0041735 | 0.0041739 | 0.0041739 | 0.99354 | -0.12322 | 0.99337 | -0.1266 | 1.1467
48 | -0.00048771 | -0.00012223 | 0.00048772 | 0.00012177 | 7.993e-09 | -4.6674e-07 | 0.00074749 | 0.00074732 | 0.00074749 | 0.97088 | -0.56423 | 0.9709 | -0.56388 | 0.20535
49 | -0.00048772 | -0.00012177 | 0.00048773 | 0.00012105 | 1.2177e-08 | -7.1154e-07 | 0.00074732 | 0.00074706 | 0.00074732 | 0.9709 | -0.56388 | 0.97092 | -0.56335 | 0.20531
50 | -0.00084407 | -0.00021154 | 0.0008441 | 0.00021097 | 2.979e-08 | -5.7092e-07 | 0.0012921 | 0.0012919 | 0.0012921 | 0.97206 | -0.54083 | 0.9721 | -0.54009 | 0.35497
51 | 0.00076419 | 0.00019141 | -0.00076418 | -0.00019152 | 4.9423e-09 | -1.1625e-07 | 0.0011697 | 0.0011698 | 0.0011698 | 0.9721 | -0.54009 | 0.97209 | -0.54023 | 0.32136
52 | -0.0089568 | -0.0022436 | 0.0089681 | 0.0022488 | 1.1387e-05 | 5.2821e-06 | 0.01371 | 0.013709 | 0.01371 | 0.9721 | -0.54009 | 0.97345 | -0.51342 | 3.7665
53 | 0.0073485 | 0.0018412 | -0.0073465 | -0.0018404 | 1.9831e-06 | 7.5119e-07 | 0.011248 | 0.011248 | 0.011248 | 0.9721 | -0.54009 | 0.97181 | -0.54576 | 3.0902
54 | 0.0073465 | 0.0018404 | -0.0073409 | -0.0018383 | 5.5697e-06 | 2.1115e-06 | 0.011248 | 0.011249 | 0.011249 | 0.97181 | -0.54576 | 0.97101 | -0.56168 | 3.0904
55 | 0.0035963 | 0.00089983 | -0.003596 | -0.00089995 | 2.72e-07 | -1.2135e-07 | 0.0055106 | 0.0055107 | 0.0055107 | 0.97101 | -0.56168 | 0.97093 | -0.56327 | 1.5139
56 | 0.00092435 | 0.00022948 | -0.00092425 | -0.00023108 | 1.0047e-07 | -1.6049e-06 | 0.0014122 | 0.0014128 | 0.0014128 | 0.97345 | -0.51342 | 0.97333 | -0.51571 | 0.38813
57 | -0.0098925 | -0.0024783 | 0.0098934 | 0.0024788 | 9.1206e-07 | 4.5147e-07 | 0.015121 | 0.015121 | 0.015121 | 0.97345 | -0.51342 | 0.97355 | -0.51148 | 4.1542
58 | 0.00048773 | 0.00012095 | -0.00048773 | -0.00012105 | 1.863e-09 | -1.089e-07 | 0.00074702 | 0.00074706 | 0.00074706 | 0.97093 | -0.56327 | 0.97092 | -0.56335 | 0.20524
59 | 0.021839 | 0.0055284 | -0.02178 | -0.0054922 | 5.9409e-05 | 3.6188e-05 | 0.033063 | 0.033063 | 0.033063 | 0.98347 | -0.31711 | 0.98055 | -0.37393 | 9.0833
60 | 0.010494 | 0.0026299 | -0.010492 | -0.0026289 | 2.0968e-06 | 1.0715e-06 | 0.016037 | 0.016037 | 0.016037 | 0.97376 | -0.50729 | 0.97355 | -0.51148 | 4.4057
61 | -0.012837 | -0.0032172 | 0.01284 | 0.0032187 | 2.7523e-06 | 1.5242e-06 | 0.019617 | 0.019617 | 0.019617 | 0.97376 | -0.50729 | 0.97399 | -0.50279 | 5.3893
62 | -0.01284 | -0.0032187 | 0.012864 | 0.003232 | 2.4006e-05 | 1.3289e-05 | 0.019617 | 0.019616 | 0.019617 | 0.97399 | -0.50279 | 0.97597 | -0.46362 | 5.3893
63 | -0.013255 | -0.003329 | 0.01327 | 0.0033373 | 1.4862e-05 | 8.2981e-06 | 0.020212 | 0.020211 | 0.020212 | 0.97597 | -0.46362 | 0.97717 | -0.44015 | 5.5526
64 | 0.00039069 | 9.7053e-05 | -0.00039068 | -9.7913e-05 | 9.2142e-09 | -8.5994e-07 | 0.00059535 | 0.00059566 | 0.00059566 | 0.97597 | -0.46362 | 0.97595 | -0.46412 | 0.16364
65 | 0.00092425 | 0.00023108 | -0.00092421 | -0.00023163 | 3.4161e-08 | -5.4529e-07 | 0.0014128 | 0.001413 | 0.001413 | 0.97333 | -0.51571 | 0.97329 | -0.51649 | 0.38818
66 | 0.0012955 | 0.00032435 | -0.0012954 | -0.0003246 | 3.2059e-08 | -2.5469e-07 | 0.0019726 | 0.0019727 | 0.0019727 | 0.97717 | -0.44015 | 0.97714 | -0.44067 | 0.54195
67 | -0.014565 | -0.0036617 | 0.014574 | 0.0036669 | 9.0495e-06 | 5.177e-06 | 0.022184 | 0.022183 | 0.022184 | 0.97717 | -0.44015 | 0.97783 | -0.42714 | 6.0944
68 | 0.0005847 | 0.00014648 | -0.0005847 | -0.00014654 | 1.5256e-09 | -6.3305e-08 | 0.00089038 | 0.0008904 | 0.0008904 | 0.97714 | -0.44067 | 0.97714 | -0.44072 | 0.24462
69 | -0.021724 | -0.0054585 | 0.02178 | 0.0054922 | 5.5323e-05 | 3.3709e-05 | 0.033064 | 0.033063 | 0.033064 | 0.97783 | -0.42714 | 0.98055 | -0.37393 | 9.0835
70 | 0.00715 | 0.0017916 | -0.0071482 | -0.001791 | 1.7355e-06 | 6.2044e-07 | 0.01088 | 0.010881 | 0.010881 | 0.97783 | -0.42714 | 0.97757 | -0.43224 | 2.9892
71 | 0.001242 | 0.00031078 | -0.0012419 | -0.00031126 | 5.5516e-08 | -4.8381e-07 | 0.0018903 | 0.0018905 | 0.0018905 | 0.97757 | -0.43224 | 0.97753 | -0.43318 | 0.51937
72 | 0.074182 | 0.018616 | -0.074123 | -0.018578 | 5.9066e-05 | 3.7643e-05 | 0.11202 | 0.11202 | 0.11202 | 0.98543 | -0.27987 | 0.98457 | -0.29658 | 30.776
73 | 0.021707 | 0.0054411 | -0.021704 | -0.0054395 | 2.5996e-06 | 1.5819e-06 | 0.032806 | 0.032806 | 0.032806 | 0.98457 | -0.29658 | 0.98444 | -0.29909 | 9.0127

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61051 | 0.15472

## res_load
| p_mw | q_mvar
0 | 0.008888 | 0.0022275
1 | 0.0080454 | 0.0020164
2 | 0.010712 | 0.0026847
3 | 0.0079292 | 0.0019873
4 | 0.061263 | 0.015354
5 | 0.0071456 | 0.0017909
6 | 0.0068636 | 0.0017202
7 | 0.0024206 | 0.00060665
8 | 0.0091684 | 0.0022978
9 | 0.0075256 | 0.0018861
10 | 0.013056 | 0.0032721
11 | 0.010715 | 0.0026854
12 | 0.0071445 | 0.0017906
13 | 0.01059 | 0.0026541
14 | 0.016664 | 0.0041763
15 | 0.016657 | 0.0041746
16 | 0.0071512 | 0.0017923
17 | 0.00794 | 0.00199
18 | 0.011464 | 0.0028731
19 | 0.0013185 | 0.00033045
20 | 0.062181 | 0.015584
21 | 0.0013766 | 0.000345
22 | 0.0082367 | 0.0020643
23 | 0.045191 | 0.011326
24 | 0.0013307 | 0.0003335
25 | 0.002815 | 0.00070552
26 | 0.0012836 | 0.00032171
27 | 0.066681 | 0.016712
28 | 0.04865 | 0.012193
29 | 0.0027864 | 0.00069833
30 | 0.00048771 | 0.00012223
31 | 0.00084407 | 0.00021154
32 | 0.0037446 | 0.00093849
33 | 0.00076418 | 0.00019152
34 | 0.0031083 | 0.00077901
35 | 0.0022154 | 0.00055524
36 | 0.002343 | 0.00058722
37 | 0.00059889 | 0.0001501
38 | 0.00039068 | 9.7913e-05
39 | 0.00092421 | 0.00023163
40 | 0.00071072 | 0.00017812
41 | 0.0059062 | 0.0014802
42 | 0.0012419 | 0.00031126
43 | 0.0005847 | 0.00014654
44 | 0.03212 | 0.00805
45 | 0.052416 | 0.013137
46 | 0.021704 | 0.0054395

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1