## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-75_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-75_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-75_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-75_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-75_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-75_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1630-75_0_4_node_49 | 0.4 | n |  | TRUE
7 | bus_LV_1630-75_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_1630-75_0_4_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_1630-75_0_4_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_1630-75_0_4_node_45 | 0.4 | n |  | TRUE
11 | bus_LV_1630-75_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1630-75_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1630-75_0_4_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_1630-75_0_4_node_47 | 0.4 | n |  | TRUE
15 | bus_LV_1630-75_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1630-75_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1630-75_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1630-75_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1630-75_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1630-75_0_4_node_33 | 0.4 | n |  | TRUE
21 | bus_LV_1630-75_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1630-75_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1630-75_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1630-75_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1630-75_0_4_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_1630-75_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1630-75_0_4_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_1630-75_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1630-75_0_4_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_1630-75_0_4_node_35 | 0.4 | n |  | TRUE
31 | bus_LV_1630-75_0_4_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_1630-75_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_1630-75_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1630-75_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_1630-75_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_1630-75_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1630-75_0_4_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_1630-75_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1630-75_0_4_node_50 | 0.4 | n |  | TRUE
40 | bus_LV_1630-75_0_4_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1630-75_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_1630-75_0_4_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1630-75_0_4_node_51 | 0.4 | n |  | TRUE
44 | bus_LV_1630-75_0_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_1630-75_0_4_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_1630-75_0_4_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_1630-75_0_4_node_52 | 0.4 | n |  | TRUE
48 | bus_LV_1630-75_0_4_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_1630-75_0_4_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_1630-75_0_4_node_46 | 0.4 | n |  | TRUE
51 | bus_MV_152_0_node_96 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-75_0_4_load_0 | 0 | 0.0088575 | 0.0022199 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-75_0_4_load_1 | 1 | 0.0074804 | 0.0018748 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-75_0_4_load_3 | 3 | 0.010276 | 0.0025754 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-75_0_4_load_5 | 5 | 0.0082968 | 0.0020794 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-75_0_4_load_49 | 6 | 0.0097705 | 0.0024487 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-75_0_4_load_11 | 7 | 0.013785 | 0.0034547 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-75_0_4_load_29 | 8 | 0.014688 | 0.0036811 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-75_0_4_load_28 | 12 | 0.015642 | 0.0039202 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-75_0_4_load_47 | 14 | 0.013517 | 0.0033877 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-75_0_4_load_6 | 15 | 0.010661 | 0.0026719 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-75_0_4_load_7 | 16 | 0.012652 | 0.0031709 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-75_0_4_load_9 | 17 | 0.0083311 | 0.002088 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-75_0_4_load_10 | 18 | 0.012447 | 0.0031195 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-75_0_4_load_33 | 20 | 0.018099 | 0.0045359 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-75_0_4_load_19 | 21 | 0.0064735 | 0.0016224 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-75_0_4_load_13 | 22 | 0.0070279 | 0.0017614 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-75_0_4_load_12 | 23 | 0.0096711 | 0.0024238 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-75_0_4_load_16 | 24 | 0.012632 | 0.0031658 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-75_0_4_load_36 | 27 | 0.0093392 | 0.0023406 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-75_0_4_load_17 | 28 | 0.0083502 | 0.0020927 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-75_0_4_load_20 | 29 | 0.0091527 | 0.0022939 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-75_0_4_load_35 | 30 | 0.010697 | 0.002681 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-75_0_4_load_34 | 31 | 0.01021 | 0.0025588 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-75_0_4_load_21 | 32 | 0.059428 | 0.014894 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-75_0_4_load_27 | 35 | 0.044659 | 0.011193 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-75_0_4_load_53 | 37 | 0.029113 | 0.0072965 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-75_0_4_load_50 | 39 | 0.0055083 | 0.0013805 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-75_0_4_load_32 | 40 | 0.01021 | 0.002559 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-75_0_4_load_30 | 41 | 0.033669 | 0.0084384 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-75_0_4_load_43 | 42 | 0.0072945 | 0.0018282 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-75_0_4_load_51 | 43 | 0.007698 | 0.0019293 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1630-75_0_4_load_31 | 44 | 0.046835 | 0.011738 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1630-75_0_4_load_52 | 47 | 0.0090851 | 0.0022769 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1630-75_0_4_load_40 | 48 | 0.0084115 | 0.0021081 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1630-75_0_4_load_41 | 49 | 0.0067499 | 0.0016917 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1630-75_0_4_load_46 | 50 | 0.01049 | 0.002629 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-75_0_4_line_0 |  | 0 | 1 | 0.0078644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-75_0_4_line_1 |  | 0 | 2 | 0.021826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-75_0_4_line_2 |  | 1 | 3 | 0.0037635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-75_0_4_line_3 |  | 2 | 4 | 0.013541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_1630-75_0_4_line_4 |  | 2 | 5 | 0.026265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-75_0_4_line_5 |  | 3 | 6 | 0.020413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-75_0_4_line_6 |  | 4 | 7 | 0.01624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1630-75_0_4_line_7 |  | 4 | 8 | 0.013498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1630-75_0_4_line_8 |  | 5 | 9 | 0.0078342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-75_0_4_line_9 |  | 6 | 10 | 0.02036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-75_0_4_line_10 |  | 7 | 11 | 0.011477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1630-75_0_4_line_11 |  | 8 | 12 | 0.011377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1630-75_0_4_line_12 |  | 9 | 13 | 0.024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-75_0_4_line_13 |  | 9 | 14 | 0.014094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-75_0_4_line_14 |  | 10 | 46 | 0.008422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-75_0_4_line_15 |  | 11 | 18 | 0.013893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-75_0_4_line_16 |  | 11 | 15 | 0.012368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1630-75_0_4_line_17 |  | 13 | 42 | 0.014458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-75_0_4_line_18 |  | 13 | 38 | 0.027602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-75_0_4_line_19 |  | 14 | 50 | 0.0099326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-75_0_4_line_20 |  | 15 | 16 | 0.021501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1630-75_0_4_line_21 |  | 16 | 17 | 0.0015661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1630-75_0_4_line_22 |  | 17 | 19 | 0.018432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1630-75_0_4_line_23 |  | 18 | 20 | 0.011802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-75_0_4_line_24 |  | 19 | 21 | 0.0029348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1630-75_0_4_line_25 |  | 19 | 22 | 0.019381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-75_0_4_line_26 |  | 21 | 26 | 0.022747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_1630-75_0_4_line_27 |  | 22 | 23 | 0.020293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-75_0_4_line_28 |  | 24 | 25 | 0.013948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-75_0_4_line_29 |  | 25 | 27 | 0.010556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-75_0_4_line_30 |  | 26 | 29 | 0.0018668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1630-75_0_4_line_31 |  | 26 | 28 | 0.019368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-75_0_4_line_32 |  | 27 | 45 | 0.023149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-75_0_4_line_33 |  | 29 | 30 | 0.0098231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_1630-75_0_4_line_34 |  | 30 | 31 | 0.016376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_1630-75_0_4_line_35 |  | 31 | 40 | 0.00564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1630-75_0_4_line_36 |  | 32 | 33 | 0.02678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-75_0_4_line_37 |  | 33 | 34 | 0.046476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-75_0_4_line_38 |  | 33 | 35 | 0.027853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-75_0_4_line_39 |  | 34 | 40 | 0.048041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_1630-75_0_4_line_40 |  | 34 | 41 | 0.025504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-75_0_4_line_41 |  | 36 | 37 | 0.003423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-75_0_4_line_42 |  | 36 | 38 | 0.068036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-75_0_4_line_43 |  | 38 | 39 | 0.015916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-75_0_4_line_44 |  | 39 | 43 | 0.0007853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1630-75_0_4_line_45 |  | 41 | 44 | 0.0027226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1630-75_0_4_line_46 |  | 42 | 49 | 0.0096005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1630-75_0_4_line_47 |  | 45 | 46 | 0.006293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1630-75_0_4_line_48 |  | 46 | 47 | 0.015369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1630-75_0_4_line_49 |  | 48 | 49 | 0.023048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-75_0_4_trafo_28 | 0.63 MVA 20/0.4 kV | 51 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2723293.3599 | 1216784.2832 | 2723285.7865 | 1216786.403
1 | 2723311.0069 | 1216773.4036 | 2723305.1694 | 1216780.9776 | 2723293.3599 | 1216784.2832
2 | 2723285.7865 | 1216786.403 | 2723282.1623 | 1216787.4175
3 | 2723311.0069 | 1216773.4036 | 2723305.0925 | 1216761.2162
4 | 2723311.0069 | 1216773.4036 | 2723314.1905 | 1216783.9665 | 2723317.2013 | 1216798.8988
5 | 2723262.2101 | 1216791.5862 | 2723266.3192 | 1216791.1041 | 2723276.2798 | 1216789.064 | 2723282.1623 | 1216787.4175
6 | 2723305.0925 | 1216761.2162 | 2723300.2339 | 1216745.7203
7 | 2723305.0925 | 1216761.2162 | 2723317.95 | 1216757.1063
8 | 2723318.7498 | 1216806.5785 | 2723317.2013 | 1216798.8988
9 | 2723241.9884 | 1216793.9587 | 2723262.2101 | 1216791.5862
10 | 2723296.8001 | 1216734.7685 | 2723300.2339 | 1216745.7203
11 | 2723317.95 | 1216757.1063 | 2723328.7867 | 1216753.6425
12 | 2723318.7498 | 1216806.5785 | 2723325.8822 | 1216829.6218
13 | 2723318.7498 | 1216806.5785 | 2723332.2886 | 1216802.6605
14 | 2723241.9884 | 1216793.9587 | 2723240.8319 | 1216785.6172
15 | 2723296.8001 | 1216734.7685 | 2723310.0642 | 1216730.637
16 | 2723296.8001 | 1216734.7685 | 2723293.3542 | 1216722.9324 | 2723293.3448 | 1216722.8932
17 | 2723325.8822 | 1216829.6218 | 2723311.977 | 1216833.5813
18 | 2723325.8822 | 1216829.6218 | 2723328.3449 | 1216837.59 | 2723335.524 | 1216835.6371 | 2723338.9069 | 1216835.8406 | 2723341.8401 | 1216836.4907 | 2723346.6404 | 1216839.0253
19 | 2723341.8297 | 1216799.8993 | 2723332.2886 | 1216802.6605
20 | 2723293.3448 | 1216722.8932 | 2723291.7814 | 1216716.3614 | 2723289.6211 | 1216701.7353
21 | 2723289.6211 | 1216701.7353 | 2723289.3923 | 1216700.1861
22 | 2723286.6991 | 1216681.9518 | 2723289.3923 | 1216700.1861
23 | 2723321.3318 | 1216727.1273 | 2723310.0642 | 1216730.637
24 | 2723286.6991 | 1216681.9518 | 2723289.5803 | 1216681.3932
25 | 2723286.6991 | 1216681.9518 | 2723267.4924 | 1216684.5428
26 | 2723311.2787 | 1216674.8102 | 2723297.8929 | 1216679.7816 | 2723289.5803 | 1216681.3932
27 | 2723247.3812 | 1216687.2558 | 2723267.4924 | 1216684.5428
28 | 2723235.3636 | 1216745.9955 | 2723233.4676 | 1216732.1772
29 | 2723235.3636 | 1216745.9955 | 2723236.8074 | 1216756.4522
30 | 2723311.2787 | 1216674.8102 | 2723312.9614 | 1216674.0019
31 | 2723311.2787 | 1216674.8102 | 2723317.5015 | 1216693.1518
32 | 2723239.9737 | 1216779.3835 | 2723236.8074 | 1216756.4522
33 | 2723321.8159 | 1216669.7485 | 2723312.9614 | 1216674.0019
34 | 2723336.5773 | 1216662.6576 | 2723336.5773 | 1216662.6576 | 2723321.8159 | 1216669.7485
35 | 2723336.5773 | 1216662.6576 | 2723341.5497 | 1216661.2927 | 2723342.0333 | 1216661.2823
36 | 2723392.1166 | 1216735.2414 | 2723403.3655 | 1216759.5445
37 | 2723392.1166 | 1216735.2414 | 2723372.5841 | 1216693.0486
38 | 2723392.1166 | 1216735.2414 | 2723382.1047 | 1216740.4826 | 2723366.2703 | 1216745.3029
39 | 2723372.5841 | 1216693.0486 | 2723362.7632 | 1216671.84 | 2723360.389 | 1216668.3993 | 2723357.6644 | 1216665.7408 | 2723354.0676 | 1216663.3979 | 2723350.7239 | 1216662.0276 | 2723346.5567 | 1216661.1852 | 2723342.0333 | 1216661.2823
40 | 2723372.5841 | 1216693.0486 | 2723348.2397 | 1216700.65
41 | 2723395.1547 | 1216822.0941 | 2723394.2052 | 1216818.8052
42 | 2723346.6404 | 1216839.0253 | 2723348.8266 | 1216840.1714 | 2723354.8732 | 1216843.3991 | 2723361.0919 | 1216844.5509 | 2723365.1822 | 1216843.9685 | 2723368.0003 | 1216843.5709 | 2723377.5868 | 1216840.8895 | 2723398.8605 | 1216834.9364 | 2723395.1547 | 1216822.0941
43 | 2723346.6404 | 1216839.0253 | 2723350.1289 | 1216823.4965 | 2723350.1289 | 1216823.4965
44 | 2723350.8671 | 1216823.2289 | 2723350.1289 | 1216823.4965
45 | 2723345.6408 | 1216701.4614 | 2723348.2397 | 1216700.65
46 | 2723311.977 | 1216833.5813 | 2723302.7436 | 1216836.2106
47 | 2723239.9737 | 1216779.3835 | 2723240.8319 | 1216785.6172
48 | 2723240.8319 | 1216785.6172 | 2723256.1349 | 1216783.7766
49 | 2723280.5763 | 1216842.5229 | 2723302.7436 | 1216836.2106

## bus_geodata
| x | y | coords
0 | 2723293.3599 | 1216784.2832
1 | 2723285.7865 | 1216786.403
2 | 2723311.0069 | 1216773.4036
3 | 2723282.1623 | 1216787.4175
4 | 2723305.0925 | 1216761.2162
5 | 2723317.2013 | 1216798.8988
6 | 2723262.2101 | 1216791.5862
7 | 2723300.2339 | 1216745.7203
8 | 2723317.95 | 1216757.1063
9 | 2723318.7498 | 1216806.5785
10 | 2723241.9884 | 1216793.9587
11 | 2723296.8001 | 1216734.7685
12 | 2723328.7867 | 1216753.6425
13 | 2723325.8822 | 1216829.6218
14 | 2723332.2886 | 1216802.6605
15 | 2723293.3448 | 1216722.8932
16 | 2723289.6211 | 1216701.7353
17 | 2723289.3923 | 1216700.1861
18 | 2723310.0642 | 1216730.637
19 | 2723286.6991 | 1216681.9518
20 | 2723321.3318 | 1216727.1273
21 | 2723289.5803 | 1216681.3932
22 | 2723267.4924 | 1216684.5428
23 | 2723247.3812 | 1216687.2558
24 | 2723233.4676 | 1216732.1772
25 | 2723235.3636 | 1216745.9955
26 | 2723311.2787 | 1216674.8102
27 | 2723236.8074 | 1216756.4522
28 | 2723317.5015 | 1216693.1518
29 | 2723312.9614 | 1216674.0019
30 | 2723321.8159 | 1216669.7485
31 | 2723336.5773 | 1216662.6576
32 | 2723403.3655 | 1216759.5445
33 | 2723392.1166 | 1216735.2414
34 | 2723372.5841 | 1216693.0486
35 | 2723366.2703 | 1216745.3029
36 | 2723395.1547 | 1216822.0941
37 | 2723394.2052 | 1216818.8052
38 | 2723346.6404 | 1216839.0253
39 | 2723350.1289 | 1216823.4965
40 | 2723342.0333 | 1216661.2823
41 | 2723348.2397 | 1216700.65
42 | 2723311.9771 | 1216833.5813
43 | 2723350.8671 | 1216823.2289
44 | 2723345.6408 | 1216701.4614
45 | 2723239.9737 | 1216779.3835
46 | 2723240.8319 | 1216785.6172
47 | 2723256.1349 | 1216783.7766
48 | 2723280.5763 | 1216842.5229
49 | 2723302.7436 | 1216836.2106
50 | 2723341.8297 | 1216799.8993
51 | 2723333.8762 | 1216752.0157

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99476 | -0.10019 | 0.0088575 | 0.0022199
1 | 0.99434 | -0.10831 | 0.0074804 | 0.0018748
2 | 0.9961 | -0.074295 | 0 | 0
3 | 0.99416 | -0.1117 | 0.010276 | 0.0025754
4 | 0.99712 | -0.054747 | 0 | 0
5 | 0.99377 | -0.11919 | 0.0082968 | 0.0020794
6 | 0.9934 | -0.12641 | 0.0097705 | 0.0024487
7 | 0.99588 | -0.078433 | 0.013785 | 0.0034547
8 | 0.99866 | -0.025396 | 0.014688 | 0.0036811
9 | 0.99313 | -0.13148 | 0 | 0
10 | 0.99282 | -0.13758 | 0 | 0
11 | 0.99504 | -0.094512 | 0 | 0
12 | 1 | 0 | -0.51891 | -0.13183
13 | 0.9917 | -0.15913 | 0 | 0
14 | 0.99282 | -0.13746 | 0.013517 | 0.0033877
15 | 0.99422 | -0.1102 | 0.010661 | 0.0026719
16 | 0.99284 | -0.13653 | 0.012652 | 0.0031709
17 | 0.99275 | -0.13836 | 0.0083311 | 0.002088
18 | 0.99465 | -0.10199 | 0.012447 | 0.0031195
19 | 0.99165 | -0.15928 | 0 | 0
20 | 0.99446 | -0.10575 | 0.018099 | 0.0045359
21 | 0.99149 | -0.1624 | 0.0064735 | 0.0016224
22 | 0.99136 | -0.16502 | 0.0070279 | 0.0017614
23 | 0.99118 | -0.1685 | 0.0096711 | 0.0024238
24 | 0.99171 | -0.15914 | 0.012632 | 0.0031658
25 | 0.99187 | -0.15602 | 0 | 0
26 | 0.99027 | -0.18594 | 0 | 0
27 | 0.99199 | -0.15366 | 0.0093392 | 0.0023406
28 | 0.99012 | -0.18882 | 0.0083502 | 0.0020927
29 | 0.99017 | -0.18781 | 0.0091527 | 0.0022939
30 | 0.98968 | -0.19723 | 0.010697 | 0.002681
31 | 0.9889 | -0.21218 | 0.01021 | 0.0025588
32 | 0.97859 | -0.41278 | 0.059428 | 0.014894
33 | 0.98006 | -0.38386 | 0 | 0
34 | 0.98455 | -0.29647 | 0 | 0
35 | 0.97891 | -0.40646 | 0.044659 | 0.011193
36 | 0.98882 | -0.2151 | 0 | 0
37 | 0.98872 | -0.21688 | 0.029113 | 0.0072965
38 | 0.99063 | -0.17985 | 0 | 0
39 | 0.99044 | -0.18359 | 0.0055083 | 0.0013805
40 | 0.98865 | -0.21708 | 0.01021 | 0.002559
41 | 0.98265 | -0.33346 | 0.033669 | 0.0084384
42 | 0.99141 | -0.16488 | 0.0072945 | 0.0018282
43 | 0.99043 | -0.1837 | 0.007698 | 0.0019293
44 | 0.98254 | -0.33577 | 0.046835 | 0.011738
45 | 0.99246 | -0.14466 | 0 | 0
46 | 0.99259 | -0.14221 | 0 | 0
47 | 0.99246 | -0.14468 | 0.0090851 | 0.0022769
48 | 0.9911 | -0.17091 | 0.0084115 | 0.0021081
49 | 0.99127 | -0.16747 | 0.0067499 | 0.0016917
50 | 0.99273 | -0.1393 | 0.01049 | 0.002629
51 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.058682 | 0.014744 | -0.058659 | -0.01473 | 2.2731e-05 | 1.4446e-05 | 0.087793 | 0.087793 | 0.087793 | 0.99476 | -0.10019 | 0.99434 | -0.10831 | 24.119
1 | -0.06754 | -0.016964 | 0.067623 | 0.017017 | 8.3563e-05 | 5.3196e-05 | 0.10104 | 0.10104 | 0.10104 | 0.99476 | -0.10019 | 0.9961 | -0.074295 | 27.7589
2 | 0.051179 | 0.012855 | -0.051171 | -0.01285 | 8.2807e-06 | 5.2508e-06 | 0.076599 | 0.076599 | 0.076599 | 0.99434 | -0.10831 | 0.99416 | -0.1117 | 21.0436
3 | -0.16516 | -0.041639 | 0.16532 | 0.041738 | 0.00015466 | 9.8631e-05 | 0.24681 | 0.24681 | 0.24681 | 0.9961 | -0.074295 | 0.99712 | -0.054747 | 33.9028
4 | 0.097539 | 0.024622 | -0.09733 | -0.024488 | 0.00020929 | 0.0001336 | 0.14577 | 0.14577 | 0.14577 | 0.9961 | -0.074295 | 0.99377 | -0.11919 | 40.0467
5 | 0.040895 | 0.010274 | -0.040866 | -0.010256 | 2.8688e-05 | 1.8096e-05 | 0.061218 | 0.061218 | 0.061218 | 0.99416 | -0.1117 | 0.9934 | -0.12641 | 16.8182
6 | 0.33591 | 0.085557 | -0.33552 | -0.085313 | 0.00038331 | 0.00024447 | 0.50176 | 0.50177 | 0.50177 | 0.99712 | -0.054747 | 0.99588 | -0.078433 | 34.4619
7 | -0.50123 | -0.12729 | 0.50193 | 0.12775 | 0.00070913 | 0.00045314 | 0.74858 | 0.74858 | 0.74858 | 0.99712 | -0.054747 | 0.99866 | -0.025396 | 51.4132
8 | 0.089033 | 0.022409 | -0.088981 | -0.022375 | 5.2239e-05 | 3.3331e-05 | 0.13335 | 0.13335 | 0.13335 | 0.99377 | -0.11919 | 0.99313 | -0.13148 | 36.6338
9 | 0.031096 | 0.0078075 | -0.031079 | -0.0077972 | 1.6568e-05 | 1.034e-05 | 0.046583 | 0.046583 | 0.046583 | 0.9934 | -0.12641 | 0.99282 | -0.13758 | 12.7976
10 | 0.32174 | 0.081858 | -0.32149 | -0.081699 | 0.00024912 | 0.00015884 | 0.48117 | 0.48117 | 0.48117 | 0.99588 | -0.078433 | 0.99504 | -0.094512 | 33.0473
11 | -0.51662 | -0.13143 | 0.51726 | 0.13183 | 0.00063313 | 0.00040461 | 0.77046 | 0.77046 | 0.77046 | 0.99866 | -0.025396 | 1 | 0 | 52.9163
12 | 0.064967 | 0.016354 | -0.064881 | -0.0163 | 8.5743e-05 | 5.4564e-05 | 0.097365 | 0.097365 | 0.097365 | 0.99313 | -0.13148 | 0.9917 | -0.15913 | 26.7487
13 | 0.024014 | 0.0060213 | -0.024008 | -0.0060171 | 6.843e-06 | 4.1972e-06 | 0.035982 | 0.035982 | 0.035982 | 0.99313 | -0.13148 | 0.99282 | -0.13746 | 9.8851
14 | 0.031079 | 0.0077972 | -0.031072 | -0.0077929 | 6.8534e-06 | 4.2773e-06 | 0.046583 | 0.046583 | 0.046583 | 0.99282 | -0.13758 | 0.99259 | -0.14221 | 12.7976
15 | 0.03056 | 0.0076642 | -0.030549 | -0.0076574 | 1.0881e-05 | 6.7837e-06 | 0.045702 | 0.045702 | 0.045702 | 0.99504 | -0.094512 | 0.99465 | -0.10199 | 12.5555
16 | 0.29093 | 0.074035 | -0.29071 | -0.073895 | 0.00021987 | 0.00014008 | 0.43547 | 0.43547 | 0.43547 | 0.99504 | -0.094512 | 0.99422 | -0.1102 | 29.9085
17 | 0.022465 | 0.0056334 | -0.022459 | -0.0056296 | 6.1609e-06 | 3.7565e-06 | 0.03371 | 0.03371 | 0.03371 | 0.9917 | -0.15913 | 0.99141 | -0.16488 | 9.2609
18 | 0.042415 | 0.010666 | -0.042374 | -0.01064 | 4.1942e-05 | 2.6487e-05 | 0.063656 | 0.063656 | 0.063656 | 0.9917 | -0.15913 | 0.99063 | -0.17985 | 17.4879
19 | 0.010491 | 0.0026294 | -0.01049 | -0.002629 | 9.2083e-07 | 4.609e-07 | 0.015723 | 0.015723 | 0.015723 | 0.99282 | -0.13746 | 0.99273 | -0.1393 | 4.3196
20 | 0.28005 | 0.071223 | -0.2797 | -0.070997 | 0.00035475 | 0.00022592 | 0.41951 | 0.41951 | 0.41951 | 0.99422 | -0.1102 | 0.99284 | -0.13653 | 28.8126
21 | 0.26704 | 0.067826 | -0.26702 | -0.067811 | 2.3556e-05 | 1.4995e-05 | 0.40055 | 0.40055 | 0.40055 | 0.99284 | -0.13653 | 0.99275 | -0.13836 | 27.5103
22 | 0.25869 | 0.065723 | -0.25843 | -0.065557 | 0.00026023 | 0.00016559 | 0.38806 | 0.38806 | 0.38806 | 0.99275 | -0.13836 | 0.99165 | -0.15928 | 26.6527
23 | 0.018102 | 0.0045379 | -0.018099 | -0.0045359 | 3.2457e-06 | 1.9241e-06 | 0.027081 | 0.027081 | 0.027081 | 0.99465 | -0.10199 | 0.99446 | -0.10575 | 7.4399
24 | 0.24172 | 0.061369 | -0.24169 | -0.061346 | 3.6254e-05 | 2.3051e-05 | 0.363 | 0.363 | 0.363 | 0.99165 | -0.15928 | 0.99149 | -0.1624 | 24.931
25 | 0.016705 | 0.0041886 | -0.016701 | -0.0041859 | 4.5668e-06 | 2.6728e-06 | 0.025067 | 0.025067 | 0.025067 | 0.99165 | -0.15928 | 0.99136 | -0.16502 | 6.8866
26 | 0.23521 | 0.059723 | -0.23495 | -0.059554 | 0.00026615 | 0.00016916 | 0.35328 | 0.35328 | 0.35328 | 0.99149 | -0.1624 | 0.99027 | -0.18594 | 24.2638
27 | 0.0096727 | 0.0024246 | -0.0096711 | -0.0024238 | 1.6041e-06 | 7.6504e-07 | 0.014519 | 0.014519 | 0.014519 | 0.99136 | -0.16502 | 0.99118 | -0.1685 | 3.9887
28 | -0.012632 | -0.0031658 | 0.012633 | 0.0031668 | 1.8788e-06 | 1.0225e-06 | 0.018953 | 0.018953 | 0.018953 | 0.99171 | -0.15914 | 0.99187 | -0.15602 | 5.2069
29 | -0.012633 | -0.0031668 | 0.012635 | 0.0031675 | 1.4219e-06 | 7.7378e-07 | 0.018953 | 0.018953 | 0.018953 | 0.99187 | -0.15602 | 0.99199 | -0.15366 | 5.2068
30 | 0.2266 | 0.057461 | -0.22658 | -0.057448 | 2.0318e-05 | 1.2908e-05 | 0.34073 | 0.34073 | 0.34073 | 0.99027 | -0.18594 | 0.99017 | -0.18781 | 23.4019
31 | 0.0083513 | 0.0020932 | -0.0083502 | -0.0020927 | 1.1438e-06 | 4.8289e-07 | 0.012549 | 0.012549 | 0.012549 | 0.99027 | -0.18594 | 0.99012 | -0.18882 | 3.4476
32 | -0.021974 | -0.0055082 | 0.021983 | 0.0055139 | 9.4315e-06 | 5.7372e-06 | 0.032962 | 0.032962 | 0.032962 | 0.99199 | -0.15366 | 0.99246 | -0.14466 | 9.0555
33 | 0.21742 | 0.055154 | -0.21732 | -0.055092 | 9.8459e-05 | 6.2509e-05 | 0.32698 | 0.32698 | 0.32698 | 0.99017 | -0.18781 | 0.98968 | -0.19723 | 22.4572
34 | 0.20663 | 0.052411 | -0.20648 | -0.052317 | 0.00014839 | 9.4129e-05 | 0.31089 | 0.31089 | 0.31089 | 0.98968 | -0.19723 | 0.9889 | -0.21218 | 21.3526
35 | 0.19627 | 0.049758 | -0.19622 | -0.049728 | 4.6181e-05 | 2.9266e-05 | 0.29553 | 0.29553 | 0.29553 | 0.9889 | -0.21218 | 0.98865 | -0.21708 | 20.2975
36 | -0.059428 | -0.014894 | 0.05951 | 0.014946 | 8.2005e-05 | 5.2146e-05 | 0.090365 | 0.090364 | 0.090365 | 0.97859 | -0.41278 | 0.98006 | -0.38386 | 24.8254
37 | -0.10422 | -0.026169 | 0.10465 | 0.026448 | 0.00043646 | 0.00027874 | 0.15825 | 0.15825 | 0.15825 | 0.98006 | -0.38386 | 0.98455 | -0.29647 | 43.475
38 | 0.044707 | 0.011223 | -0.044659 | -0.011193 | 4.8133e-05 | 3.0454e-05 | 0.067885 | 0.067885 | 0.067885 | 0.98006 | -0.38386 | 0.97891 | -0.40646 | 18.6497
39 | -0.18531 | -0.046718 | 0.18601 | 0.04717 | 0.00070703 | 0.00045127 | 0.28016 | 0.28016 | 0.28016 | 0.98455 | -0.29647 | 0.98865 | -0.21708 | 38.4841
40 | 0.080652 | 0.02027 | -0.08051 | -0.02018 | 0.00014215 | 9.0653e-05 | 0.12192 | 0.12192 | 0.12192 | 0.98455 | -0.29647 | 0.98265 | -0.33346 | 33.4932
41 | 0.029116 | 0.007298 | -0.029113 | -0.0072965 | 2.4643e-06 | 1.5332e-06 | 0.043815 | 0.043815 | 0.043815 | 0.98882 | -0.2151 | 0.98872 | -0.21688 | 12.0372
42 | -0.029116 | -0.007298 | 0.029165 | 0.0073285 | 4.898e-05 | 3.0473e-05 | 0.043815 | 0.043815 | 0.043815 | 0.98882 | -0.2151 | 0.99063 | -0.17985 | 12.0372
43 | 0.013209 | 0.0033111 | -0.013206 | -0.0033098 | 2.3495e-06 | 1.2988e-06 | 0.019841 | 0.019841 | 0.019841 | 0.99063 | -0.17985 | 0.99044 | -0.18359 | 5.4508
44 | 0.007698 | 0.0019293 | -0.007698 | -0.0019293 | 3.939e-08 | 1.5103e-08 | 0.011565 | 0.011565 | 0.011565 | 0.99044 | -0.18359 | 0.99043 | -0.1837 | 3.1773
45 | 0.04684 | 0.011741 | -0.046835 | -0.011738 | 5.1366e-06 | 3.2529e-06 | 0.07093 | 0.07093 | 0.07093 | 0.98265 | -0.33346 | 0.98254 | -0.33577 | 19.4863
46 | 0.015165 | 0.0038015 | -0.015163 | -0.0038004 | 1.8652e-06 | 1.0699e-06 | 0.022761 | 0.022761 | 0.022761 | 0.99141 | -0.16488 | 0.99127 | -0.16747 | 6.2531
47 | -0.021983 | -0.0055139 | 0.021986 | 0.0055155 | 2.564e-06 | 1.5596e-06 | 0.032962 | 0.032962 | 0.032962 | 0.99246 | -0.14466 | 0.99259 | -0.14221 | 9.0554
48 | 0.0090861 | 0.0022774 | -0.0090851 | -0.0022769 | 1.0694e-06 | 4.8576e-07 | 0.013621 | 0.013621 | 0.013621 | 0.99259 | -0.14221 | 0.99246 | -0.14468 | 3.7422
49 | -0.0084115 | -0.0021081 | 0.0084129 | 0.0021087 | 1.3785e-06 | 5.8516e-07 | 0.012629 | 0.012629 | 0.012629 | 0.9911 | -0.17091 | 0.99127 | -0.16747 | 3.4695

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53455 | 0.13575

## res_load
| p_mw | q_mvar
0 | 0.0088575 | 0.0022199
1 | 0.0074804 | 0.0018748
2 | 0.010276 | 0.0025754
3 | 0.0082968 | 0.0020794
4 | 0.0097705 | 0.0024487
5 | 0.013785 | 0.0034547
6 | 0.014688 | 0.0036811
7 | 0.015642 | 0.0039202
8 | 0.013517 | 0.0033877
9 | 0.010661 | 0.0026719
10 | 0.012652 | 0.0031709
11 | 0.0083311 | 0.002088
12 | 0.012447 | 0.0031195
13 | 0.018099 | 0.0045359
14 | 0.0064735 | 0.0016224
15 | 0.0070279 | 0.0017614
16 | 0.0096711 | 0.0024238
17 | 0.012632 | 0.0031658
18 | 0.0093392 | 0.0023406
19 | 0.0083502 | 0.0020927
20 | 0.0091527 | 0.0022939
21 | 0.010697 | 0.002681
22 | 0.01021 | 0.0025588
23 | 0.059428 | 0.014894
24 | 0.044659 | 0.011193
25 | 0.029113 | 0.0072965
26 | 0.0055083 | 0.0013805
27 | 0.01021 | 0.002559
28 | 0.033669 | 0.0084384
29 | 0.0072945 | 0.0018282
30 | 0.007698 | 0.0019293
31 | 0.046835 | 0.011738
32 | 0.0090851 | 0.0022769
33 | 0.0084115 | 0.0021081
34 | 0.0067499 | 0.0016917
35 | 0.01049 | 0.002629

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1