## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-78_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-78_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-78_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-78_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-78_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-78_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1630-78_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1630-78_0_4_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_1630-78_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1630-78_0_4_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_1630-78_0_4_node_36 | 0.4 | n |  | TRUE
11 | bus_LV_1630-78_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1630-78_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_1630-78_0_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_1630-78_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1630-78_0_4_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_1630-78_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1630-78_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1630-78_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1630-78_0_4_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1630-78_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1630-78_0_4_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_1630-78_0_4_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_1630-78_0_4_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1630-78_0_4_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_1630-78_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1630-78_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1630-78_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1630-78_0_4_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_1630-78_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1630-78_0_4_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_1630-78_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_1630-78_0_4_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_1630-78_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1630-78_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_1630-78_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_MV_225_0_node_111 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-78_0_4_load_0 | 0 | 0.070945 | 0.017781 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-78_0_4_load_3 | 3 | 0.051304 | 0.012858 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-78_0_4_load_5 | 5 | 0.074032 | 0.018554 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-78_0_4_load_8 | 6 | 0.060101 | 0.015063 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-78_0_4_load_36 | 10 | 0.021706 | 0.0054401 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-78_0_4_load_18 | 12 | 0.026799 | 0.0067164 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-78_0_4_load_16 | 13 | 0.017777 | 0.0044553 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-78_0_4_load_29 | 15 | 0.004899 | 0.0012278 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-78_0_4_load_27 | 19 | 0.0095909 | 0.0024037 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-78_0_4_load_32 | 22 | 0.050916 | 0.012761 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-78_0_4_load_21 | 23 | 0.049638 | 0.012441 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-78_0_4_load_22 | 25 | 0.009625 | 0.0024123 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-78_0_4_load_26 | 26 | 0.0093958 | 0.0023548 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-78_0_4_load_37 | 28 | 0.024738 | 0.0062 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-78_0_4_load_30 | 30 | 0.00071271 | 0.00017862 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-78_0_4_load_34 | 32 | 0.012573 | 0.0031512 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-78_0_4_load_25 | 33 | 0.010521 | 0.0026368 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-78_0_4_load_20 | 34 | 0.03882 | 0.0097292 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-78_0_4_load_28 | 35 | 0.013549 | 0.0033957 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-78_0_4_line_0 |  | 0 | 1 | 0.026261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_1630-78_0_4_line_1 |  | 0 | 2 | 0.019591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1630-78_0_4_line_2 |  | 1 | 3 | 0.023034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1630-78_0_4_line_3 |  | 1 | 4 | 0.009367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-78_0_4_line_4 |  | 2 | 5 | 0.022084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_1630-78_0_4_line_5 |  | 4 | 6 | 0.025024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-78_0_4_line_6 |  | 5 | 7 | 0.040371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1630-78_0_4_line_7 |  | 7 | 23 | 0.017331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1630-78_0_4_line_8 |  | 7 | 14 | 0.25963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-78_0_4_line_9 |  | 8 | 9 | 0.01258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1630-78_0_4_line_10 |  | 8 | 10 | 0.014875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-78_0_4_line_11 |  | 8 | 11 | 0.06337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1630-78_0_4_line_12 |  | 9 | 28 | 0.00648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-78_0_4_line_13 |  | 9 | 27 | 0.034657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1630-78_0_4_line_14 |  | 11 | 12 | 0.005251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-78_0_4_line_15 |  | 11 | 13 | 0.019279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1630-78_0_4_line_16 |  | 13 | 29 | 0.024021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1630-78_0_4_line_17 |  | 14 | 15 | 0.086677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-78_0_4_line_18 |  | 15 | 30 | 0.014176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-78_0_4_line_19 |  | 16 | 17 | 0.057079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-78_0_4_line_20 |  | 16 | 18 | 0.039554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1630-78_0_4_line_21 |  | 16 | 19 | 0.014662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1630-78_0_4_line_22 |  | 17 | 26 | 0.013779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-78_0_4_line_23 |  | 18 | 24 | 0.064363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1630-78_0_4_line_24 |  | 18 | 25 | 0.01379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-78_0_4_line_25 |  | 19 | 31 | 0.01117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1630-78_0_4_line_26 |  | 20 | 21 | 0.28779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1630-78_0_4_line_27 |  | 20 | 22 | 0.0021106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_1630-78_0_4_line_28 |  | 21 | 32 | 0.055366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-78_0_4_line_29 |  | 22 | 24 | 0.036659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1630-78_0_4_line_30 |  | 23 | 27 | 0.042607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1630-78_0_4_line_31 |  | 26 | 33 | 0.0043935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-78_0_4_line_32 |  | 29 | 31 | 0.011659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1630-78_0_4_line_33 |  | 29 | 34 | 0.018391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-78_0_4_line_34 |  | 31 | 35 | 0.010739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-78_0_4_trafo_3 | 0.63 MVA 20/0.4 kV | 36 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2723596.3774 | 1218574.7326 | 2723570.7976 | 1218568.7882
1 | 2723551.7154 | 1218564.3537 | 2723570.7976 | 1218568.7882
2 | 2723596.3774 | 1218574.7326 | 2723602.0113 | 1218552.3986
3 | 2723605.5274 | 1218576.8574 | 2723596.3774 | 1218574.7326
4 | 2723551.7154 | 1218564.3537 | 2723530.2026 | 1218559.3617
5 | 2723605.5274 | 1218576.8574 | 2723611.4175 | 1218552.5364
6 | 2723497.5407 | 1218539.678 | 2723499.1461 | 1218543.5365 | 2723504.1451 | 1218549.9674 | 2723510.0569 | 1218554.1154 | 2723520.1925 | 1218557.0389 | 2723530.2026 | 1218559.3617
7 | 2723497.5407 | 1218539.678 | 2723496.2566 | 1218534.9699 | 2723496.1024 | 1218528.495 | 2723497.7324 | 1218522.7471
8 | 2723366.368 | 1218686.6979 | 2723368.6998 | 1218681.5199 | 2723367.1853 | 1218679.865 | 2723406.8826 | 1218591.2956 | 2723418.3472 | 1218583.2156 | 2723422.3527 | 1218573.1129 | 2723426.088 | 1218563.227 | 2723426.7356 | 1218558.7258 | 2723426.093 | 1218555.6656 | 2723425.7923 | 1218553.3242 | 2723426.288 | 1218549.1868 | 2723430.9893 | 1218537.3861 | 2723439.3286 | 1218516.3646 | 2723440.4811 | 1218513.5085 | 2723474.2147 | 1218539.8058 | 2723477.2783 | 1218541.0814 | 2723480.4836 | 1218541.7483 | 2723484.1196 | 1218541.7792 | 2723497.5407 | 1218539.678
9 | 2723559.8676 | 1218486.8843 | 2723557.6467 | 1218488.1726 | 2723547.8033 | 1218490.1812
10 | 2723559.8676 | 1218486.8843 | 2723566.8989 | 1218482.8159 | 2723563.3824 | 1218477.0273
11 | 2723559.8676 | 1218486.8843 | 2723564.922 | 1218496.1297 | 2723572.0007 | 1218516.8483 | 2723590.7687 | 1218513.5572 | 2723601.7648 | 1218509.0484
12 | 2723545.4297 | 1218484.9279 | 2723547.0583 | 1218485.4732 | 2723547.8033 | 1218490.1812
13 | 2723547.8033 | 1218490.1812 | 2723538.2726 | 1218492.1296 | 2723514.7139 | 1218483.7012
14 | 2723598.0304 | 1218505.3458 | 2723601.7648 | 1218509.0484
15 | 2723601.7648 | 1218509.0484 | 2723617.6243 | 1218502.1387 | 2723619.3905 | 1218501.2435
16 | 2723639.601 | 1218488.3839 | 2723633.0495 | 1218493.1072 | 2723627.2769 | 1218497.2462 | 2723619.3905 | 1218501.2435
17 | 2723366.368 | 1218686.6979 | 2723370.5012 | 1218686.917 | 2723372.6732 | 1218686.1503 | 2723375.2313 | 1218684.3351 | 2723384.1782 | 1218667.3182 | 2723387.834 | 1218663.8245 | 2723391.4563 | 1218661.9536 | 2723396.4355 | 1218661.2784 | 2723414.7249 | 1218668.5963 | 2723430.3093 | 1218678.5825 | 2723435.354 | 1218680.7866
18 | 2723435.354 | 1218680.7866 | 2723448.344 | 1218686.4623
19 | 2723603.3903 | 1218428.9194 | 2723654.7689 | 1218454.094
20 | 2723654.7689 | 1218454.094 | 2723689.1688 | 1218470.9546 | 2723690.265 | 1218471.5444
21 | 2723654.7689 | 1218454.094 | 2723648.8366 | 1218467.5026
22 | 2723603.3903 | 1218428.9194 | 2723598.003 | 1218441.6021
23 | 2723686.4026 | 1218524.0721 | 2723704.299 | 1218479.0528 | 2723698.0052 | 1218475.7529 | 2723692.7575 | 1218472.8972 | 2723690.265 | 1218471.5444
24 | 2723690.265 | 1218471.5444 | 2723684.3857 | 1218484.0181
25 | 2723644.3172 | 1218477.7179 | 2723648.8366 | 1218467.5026
26 | 2723629.9733 | 1218669.0367 | 2723633.2433 | 1218666.9474 | 2723636.4886 | 1218666.0473 | 2723640.2223 | 1218666.1249 | 2723682.6687 | 1218680.784 | 2723716.1901 | 1218692.3556 | 2723729.4415 | 1218654.5679 | 2723733.8718 | 1218642.3169 | 2723753.0318 | 1218589.4734 | 2723748.7416 | 1218588.0388 | 2723686.0979 | 1218566.877 | 2723671.2297 | 1218559.6961
27 | 2723671.2297 | 1218559.6961 | 2723672.2998 | 1218557.877
28 | 2723629.9733 | 1218669.0367 | 2723642.0287 | 1218635.8053 | 2723622.6472 | 1218630.81
29 | 2723686.4026 | 1218524.0721 | 2723675.3951 | 1218551.7875 | 2723673.4334 | 1218555.9501 | 2723672.2998 | 1218557.877
30 | 2723514.7139 | 1218483.7012 | 2723498.5352 | 1218519.9165 | 2723497.7324 | 1218522.7471
31 | 2723596.2853 | 1218445.6459 | 2723598.003 | 1218441.6021
32 | 2723644.3172 | 1218477.7179 | 2723639.601 | 1218488.3839
33 | 2723639.601 | 1218488.3839 | 2723657.0066 | 1218494.3242
34 | 2723644.3172 | 1218477.7179 | 2723653.8479 | 1218482.7196

## bus_geodata
| x | y | coords
0 | 2723570.7976 | 1218568.7882
1 | 2723596.3774 | 1218574.7326
2 | 2723551.7154 | 1218564.3537
3 | 2723602.0113 | 1218552.3986
4 | 2723605.5274 | 1218576.8574
5 | 2723530.2026 | 1218559.3617
6 | 2723611.4175 | 1218552.5364
7 | 2723497.5407 | 1218539.678
8 | 2723559.8676 | 1218486.8843
9 | 2723547.8033 | 1218490.1812
10 | 2723563.3824 | 1218477.0273
11 | 2723601.7648 | 1218509.0484
12 | 2723598.0304 | 1218505.3458
13 | 2723619.3905 | 1218501.2435
14 | 2723366.368 | 1218686.6979
15 | 2723435.354 | 1218680.7866
16 | 2723654.7689 | 1218454.094
17 | 2723603.3903 | 1218428.9194
18 | 2723690.265 | 1218471.5444
19 | 2723648.8366 | 1218467.5026
20 | 2723671.2297 | 1218559.6961
21 | 2723629.9733 | 1218669.0367
22 | 2723672.2998 | 1218557.877
23 | 2723497.7324 | 1218522.7471
24 | 2723686.4026 | 1218524.0721
25 | 2723684.3857 | 1218484.0181
26 | 2723598.003 | 1218441.6021
27 | 2723514.7139 | 1218483.7012
28 | 2723545.4297 | 1218484.9279
29 | 2723639.601 | 1218488.3839
30 | 2723448.344 | 1218686.4623
31 | 2723644.3172 | 1218477.7179
32 | 2723622.6472 | 1218630.81
33 | 2723596.2853 | 1218445.6459
34 | 2723657.0066 | 1218494.3242
35 | 2723653.8479 | 1218482.7196
36 | 2723596.3774 | 1218574.7326

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99461 | -0.10246 | 0.070945 | 0.017781
1 | 0.99731 | -0.050968 | 0 | 0
2 | 0.99291 | -0.13491 | 0 | 0
3 | 1 | 0 | -0.51514 | -0.13143
4 | 0.9968 | -0.060839 | 0 | 0
5 | 0.99099 | -0.17162 | 0.074032 | 0.018554
6 | 0.99543 | -0.087257 | 0.060101 | 0.015063
7 | 0.98817 | -0.22576 | 0 | 0
8 | 0.98193 | -0.34666 | 0 | 0
9 | 0.98257 | -0.33409 | 0 | 0
10 | 0.98163 | -0.3525 | 0.021706 | 0.0054401
11 | 0.97899 | -0.40401 | 0 | 0
12 | 0.97886 | -0.40657 | 0.026799 | 0.0067164
13 | 0.97821 | -0.41917 | 0.017777 | 0.0044553
14 | 0.98683 | -0.25183 | 0 | 0
15 | 0.98639 | -0.26055 | 0.004899 | 0.0012278
16 | 0.97645 | -0.4538 | 0 | 0
17 | 0.97539 | -0.4746 | 0 | 0
18 | 0.97578 | -0.46703 | 0 | 0
19 | 0.97677 | -0.44756 | 0.0095909 | 0.0024037
20 | 0.97428 | -0.49657 | 0 | 0
21 | 0.97315 | -0.51877 | 0 | 0
22 | 0.97428 | -0.49645 | 0.050916 | 0.012761
23 | 0.98698 | -0.24866 | 0.049638 | 0.012441
24 | 0.97483 | -0.48576 | 0 | 0
25 | 0.97565 | -0.46946 | 0.009625 | 0.0024123
26 | 0.97514 | -0.47963 | 0.0093958 | 0.0023548
27 | 0.98455 | -0.29567 | 0 | 0
28 | 0.98242 | -0.33698 | 0.024738 | 0.0062
29 | 0.97735 | -0.43614 | 0 | 0
30 | 0.98638 | -0.26073 | 0.00071271 | 0.00017862
31 | 0.97703 | -0.44233 | 0 | 0
32 | 0.9725 | -0.53159 | 0.012573 | 0.0031512
33 | 0.97509 | -0.48048 | 0.010521 | 0.0026368
34 | 0.97669 | -0.44918 | 0.03882 | 0.0097292
35 | 0.9769 | -0.44498 | 0.013549 | 0.0033957
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.4509 | -0.11478 | 0.45202 | 0.11549 | 0.0011224 | 0.000717 | 0.67521 | 0.67521 | 0.67521 | 0.99461 | -0.10246 | 0.99731 | -0.050968 | 46.3742
1 | 0.37995 | 0.096996 | -0.37936 | -0.096617 | 0.00059477 | 0.00037964 | 0.56907 | 0.56907 | 0.56907 | 0.99461 | -0.10246 | 0.99291 | -0.13491 | 39.0845
2 | -0.51222 | -0.13062 | 0.51349 | 0.13143 | 0.0012639 | 0.0008077 | 0.76505 | 0.76505 | 0.76505 | 0.99731 | -0.050968 | 1 | 0 | 52.5446
3 | 0.060205 | 0.015129 | -0.060177 | -0.015111 | 2.8352e-05 | 1.8023e-05 | 0.089842 | 0.089842 | 0.089842 | 0.99731 | -0.050968 | 0.9968 | -0.060839 | 24.6817
4 | 0.37936 | 0.096617 | -0.37869 | -0.096189 | 0.00067048 | 0.00042797 | 0.56907 | 0.56907 | 0.56907 | 0.99291 | -0.13491 | 0.99099 | -0.17162 | 39.0845
5 | 0.060177 | 0.015111 | -0.060101 | -0.015063 | 7.5743e-05 | 4.815e-05 | 0.089842 | 0.089842 | 0.089842 | 0.9968 | -0.060839 | 0.99543 | -0.087257 | 24.6818
6 | 0.30465 | 0.077634 | -0.30386 | -0.077129 | 0.0007936 | 0.00050583 | 0.45791 | 0.45791 | 0.45791 | 0.99099 | -0.17162 | 0.98817 | -0.22576 | 31.4498
7 | 0.29824 | 0.075721 | -0.29791 | -0.075512 | 0.00032821 | 0.00020917 | 0.44944 | 0.44945 | 0.44945 | 0.98817 | -0.22576 | 0.98698 | -0.24866 | 30.8685
8 | 0.005621 | 0.0014078 | -0.0056141 | -0.0014066 | 6.9758e-06 | 1.143e-06 | 0.008464 | 0.0084652 | 0.0084652 | 0.98817 | -0.22576 | 0.98683 | -0.25183 | 2.3256
9 | -0.22238 | -0.056137 | 0.22251 | 0.056222 | 0.00013405 | 8.5156e-05 | 0.33714 | 0.33714 | 0.33714 | 0.98193 | -0.34666 | 0.98257 | -0.33409 | 23.1553
10 | 0.021712 | 0.0054438 | -0.021706 | -0.0054401 | 6.0393e-06 | 3.677e-06 | 0.032904 | 0.032904 | 0.032904 | 0.98193 | -0.34666 | 0.98163 | -0.3525 | 9.0395
11 | 0.20067 | 0.050693 | -0.20012 | -0.050345 | 0.0005499 | 0.00034874 | 0.30424 | 0.30424 | 0.30424 | 0.98193 | -0.34666 | 0.97899 | -0.40401 | 20.8955
12 | 0.024742 | 0.0062021 | -0.024738 | -0.0062 | 3.4117e-06 | 2.1014e-06 | 0.03747 | 0.03747 | 0.03747 | 0.98257 | -0.33409 | 0.98242 | -0.33698 | 10.2939
13 | -0.24726 | -0.062424 | 0.24771 | 0.062714 | 0.00045595 | 0.00029005 | 0.37461 | 0.37461 | 0.37461 | 0.98257 | -0.33409 | 0.98455 | -0.29567 | 25.7287
14 | 0.026802 | 0.0067185 | -0.026799 | -0.0067164 | 3.268e-06 | 2.0255e-06 | 0.040738 | 0.040739 | 0.040739 | 0.97899 | -0.40401 | 0.97886 | -0.40657 | 11.1919
15 | 0.17332 | 0.043626 | -0.17319 | -0.043547 | 0.0001255 | 7.9348e-05 | 0.2635 | 0.2635 | 0.2635 | 0.97899 | -0.40401 | 0.97821 | -0.41917 | 18.0975
16 | 0.15541 | 0.039091 | -0.15529 | -0.039012 | 0.00012592 | 7.9381e-05 | 0.23646 | 0.23646 | 0.23646 | 0.97821 | -0.41917 | 0.97735 | -0.43614 | 16.2403
17 | 0.0056141 | 0.0014066 | -0.0056117 | -0.0014063 | 2.3293e-06 | 3.8386e-07 | 0.0084652 | 0.0084656 | 0.0084656 | 0.98683 | -0.25183 | 0.98639 | -0.26055 | 2.3257
18 | 0.00071272 | 0.00017845 | -0.00071271 | -0.00017862 | 6.1449e-09 | -1.7701e-07 | 0.0010751 | 0.0010752 | 0.0010752 | 0.98639 | -0.26055 | 0.98638 | -0.26073 | 0.29538
19 | 0.019942 | 0.0050067 | -0.019922 | -0.0049947 | 1.9772e-05 | 1.1941e-05 | 0.030393 | 0.030393 | 0.030393 | 0.97645 | -0.4538 | 0.97539 | -0.4746 | 8.3497
20 | 0.073272 | 0.018406 | -0.073226 | -0.018379 | 4.6247e-05 | 2.762e-05 | 0.11168 | 0.11168 | 0.11168 | 0.97645 | -0.4538 | 0.97578 | -0.46703 | 7.67
21 | -0.093214 | -0.023413 | 0.093242 | 0.02343 | 2.7744e-05 | 1.7022e-05 | 0.14207 | 0.14207 | 0.14207 | 0.97645 | -0.4538 | 0.97677 | -0.44756 | 9.7574
22 | 0.019922 | 0.0049947 | -0.019917 | -0.0049919 | 4.7732e-06 | 2.8829e-06 | 0.030393 | 0.030393 | 0.030393 | 0.97539 | -0.4746 | 0.97514 | -0.47963 | 8.3497
23 | 0.0636 | 0.015966 | -0.063543 | -0.015933 | 5.677e-05 | 3.312e-05 | 0.096996 | 0.096997 | 0.096997 | 0.97578 | -0.46703 | 0.97483 | -0.48576 | 6.6619
24 | 0.0096261 | 0.0024128 | -0.009625 | -0.0024123 | 1.1143e-06 | 5.4094e-07 | 0.01468 | 0.01468 | 0.01468 | 0.97578 | -0.46703 | 0.97565 | -0.46946 | 4.0329
25 | -0.10283 | -0.025834 | 0.10286 | 0.02585 | 2.5707e-05 | 1.5893e-05 | 0.15668 | 0.15668 | 0.15668 | 0.97677 | -0.44756 | 0.97703 | -0.44233 | 10.7609
26 | 0.012594 | 0.0031532 | -0.012581 | -0.0031554 | 1.3311e-05 | -2.22e-06 | 0.019234 | 0.019238 | 0.019238 | 0.97428 | -0.49657 | 0.97315 | -0.51877 | 1.7617
27 | -0.012594 | -0.0031532 | 0.012594 | 0.0031531 | 7.32e-08 | -5.8284e-08 | 0.019234 | 0.019234 | 0.019234 | 0.97428 | -0.49657 | 0.97428 | -0.49645 | 1.321
28 | 0.012581 | 0.0031554 | -0.012573 | -0.0031512 | 7.6842e-06 | 4.2304e-06 | 0.019238 | 0.019238 | 0.019238 | 0.97315 | -0.51877 | 0.9725 | -0.53159 | 5.2852
29 | -0.063511 | -0.015914 | 0.063543 | 0.015933 | 3.2335e-05 | 1.8867e-05 | 0.096998 | 0.096997 | 0.096998 | 0.97428 | -0.49645 | 0.97483 | -0.48576 | 6.662
30 | 0.24827 | 0.063071 | -0.24771 | -0.062714 | 0.00056054 | 0.00035658 | 0.37461 | 0.37461 | 0.37461 | 0.98698 | -0.24866 | 0.98455 | -0.29567 | 25.7287
31 | 0.010522 | 0.0026371 | -0.010521 | -0.0026368 | 4.247e-07 | 2.17e-07 | 0.016055 | 0.016055 | 0.016055 | 0.97514 | -0.47963 | 0.97509 | -0.48048 | 4.4108
32 | 0.11644 | 0.029268 | -0.11641 | -0.029246 | 3.4366e-05 | 2.141e-05 | 0.17732 | 0.17732 | 0.17732 | 0.97735 | -0.43614 | 0.97703 | -0.44233 | 12.1783
33 | 0.038844 | 0.0097444 | -0.03882 | -0.0097292 | 2.4124e-05 | 1.5209e-05 | 0.059143 | 0.059143 | 0.059143 | 0.97735 | -0.43614 | 0.97669 | -0.44918 | 16.2482
34 | 0.013551 | 0.0033966 | -0.013549 | -0.0033957 | 1.7152e-06 | 9.6327e-07 | 0.020638 | 0.020638 | 0.020638 | 0.97703 | -0.44233 | 0.9769 | -0.44498 | 5.6697

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.56644 | 0.14429

## res_load
| p_mw | q_mvar
0 | 0.070945 | 0.017781
1 | 0.051304 | 0.012858
2 | 0.074032 | 0.018554
3 | 0.060101 | 0.015063
4 | 0.021706 | 0.0054401
5 | 0.026799 | 0.0067164
6 | 0.017777 | 0.0044553
7 | 0.004899 | 0.0012278
8 | 0.0095909 | 0.0024037
9 | 0.050916 | 0.012761
10 | 0.049638 | 0.012441
11 | 0.009625 | 0.0024123
12 | 0.0093958 | 0.0023548
13 | 0.024738 | 0.0062
14 | 0.00071271 | 0.00017862
15 | 0.012573 | 0.0031512
16 | 0.010521 | 0.0026368
17 | 0.03882 | 0.0097292
18 | 0.013549 | 0.0033957

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1