## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-79_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-79_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-79_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-79_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-79_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1630-79_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1630-79_0_4_node_53 | 0.4 | n |  | TRUE
7 | bus_LV_1630-79_0_4_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_1630-79_0_4_node_46 | 0.4 | n |  | TRUE
9 | bus_LV_1630-79_0_4_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_1630-79_0_4_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_1630-79_0_4_node_38 | 0.4 | n |  | TRUE
12 | bus_LV_1630-79_0_4_node_35 | 0.4 | n |  | TRUE
13 | bus_LV_1630-79_0_4_node_47 | 0.4 | n |  | TRUE
14 | bus_LV_1630-79_0_4_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_1630-79_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1630-79_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1630-79_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1630-79_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1630-79_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1630-79_0_4_node_37 | 0.4 | n |  | TRUE
21 | bus_LV_1630-79_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1630-79_0_4_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_1630-79_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1630-79_0_4_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_1630-79_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_1630-79_0_4_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_1630-79_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_1630-79_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1630-79_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_1630-79_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_1630-79_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_1630-79_0_4_node_52 | 0.4 | n |  | TRUE
33 | bus_LV_1630-79_0_4_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_1630-79_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1630-79_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_1630-79_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1630-79_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_1630-79_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_1630-79_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_1630-79_0_4_node_50 | 0.4 | n |  | TRUE
41 | bus_LV_1630-79_0_4_node_49 | 0.4 | n |  | TRUE
42 | bus_LV_1630-79_0_4_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_1630-79_0_4_node_55 | 0.4 | n |  | TRUE
44 | bus_LV_1630-79_0_4_node_54 | 0.4 | n |  | TRUE
45 | bus_LV_1630-79_0_4_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_1630-79_0_4_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_1630-79_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_1630-79_0_4_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1630-79_0_4_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_1630-79_0_4_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_1630-79_0_4_node_57 | 0.4 | n |  | TRUE
52 | bus_LV_1630-79_0_4_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_1630-79_0_4_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_1630-79_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_1630-79_0_4_node_56 | 0.4 | n |  | TRUE
56 | bus_MV_152_0_node_99 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-79_0_4_load_0 | 0 | 0.013105 | 0.0032845 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-79_0_4_load_1 | 1 | 0.012388 | 0.0031047 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-79_0_4_load_3 | 3 | 0.012381 | 0.003103 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-79_0_4_load_4 | 4 | 0.029296 | 0.0073422 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-79_0_4_load_53 | 6 | 0.010394 | 0.0026049 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-79_0_4_load_46 | 8 | 0.0023892 | 0.0005988 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-79_0_4_load_23 | 9 | 0.0027131 | 0.00067997 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-79_0_4_load_20 | 10 | 0.0105 | 0.0026316 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-79_0_4_load_35 | 12 | 0.0036241 | 0.00090829 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-79_0_4_load_47 | 13 | 0.0025268 | 0.00063326 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-79_0_4_load_6 | 15 | 0.012459 | 0.0031226 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-79_0_4_load_7 | 16 | 0.013835 | 0.0034673 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-79_0_4_load_10 | 18 | 0.012397 | 0.0031069 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-79_0_4_load_9 | 19 | 0.037806 | 0.009475 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-79_0_4_load_18 | 21 | 0.007685 | 0.001926 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-79_0_4_load_39 | 22 | 0.0076858 | 0.0019262 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-79_0_4_load_19 | 23 | 0.01236 | 0.0030977 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-79_0_4_load_11 | 24 | 0.010264 | 0.0025725 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-79_0_4_load_12 | 25 | 0.0059994 | 0.0015036 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-79_0_4_load_13 | 26 | 0.010728 | 0.0026887 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-79_0_4_load_14 | 27 | 0.019941 | 0.0049977 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-79_0_4_load_15 | 29 | 0.044743 | 0.011214 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-79_0_4_load_16 | 30 | 0.010002 | 0.0025069 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-79_0_4_load_52 | 32 | 0.0065487 | 0.0016413 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-79_0_4_load_51 | 33 | 0.0057603 | 0.0014437 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-79_0_4_load_24 | 34 | 0.0071781 | 0.001799 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-79_0_4_load_29 | 38 | 0.0071897 | 0.0018019 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-79_0_4_load_28 | 39 | 0.0072085 | 0.0018066 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-79_0_4_load_49 | 41 | 0.0072076 | 0.0018064 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-79_0_4_load_54 | 44 | 0.0071972 | 0.0018038 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-79_0_4_load_30 | 47 | 0.0083543 | 0.0020938 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1630-79_0_4_load_31 | 48 | 0.0027763 | 0.00069581 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1630-79_0_4_load_33 | 49 | 0.0027994 | 0.0007016 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1630-79_0_4_load_57 | 51 | 0.007313 | 0.0018328 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1630-79_0_4_load_40 | 52 | 0.0032626 | 0.00081769 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1630-79_0_4_load_44 | 53 | 0.014415 | 0.0036127 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1630-79_0_4_load_41 | 54 | 0.003626 | 0.00090876 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1630-79_0_4_load_56 | 55 | 0.024966 | 0.0062571 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-79_0_4_line_0 |  | 0 | 1 | 0.0095141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_1630-79_0_4_line_1 |  | 0 | 2 | 0.03383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_1630-79_0_4_line_2 |  | 1 | 3 | 0.010316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_1630-79_0_4_line_3 |  | 2 | 4 | 0.019808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1630-79_0_4_line_4 |  | 2 | 5 | 0.001413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-79_0_4_line_5 |  | 3 | 6 | 0.007195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-79_0_4_line_6 |  | 4 | 7 | 0.018332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_1630-79_0_4_line_7 |  | 4 | 8 | 0.018279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-79_0_4_line_8 |  | 5 | 9 | 0.0089165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-79_0_4_line_9 |  | 6 | 10 | 0.014178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-79_0_4_line_10 |  | 7 | 11 | 0.006329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-79_0_4_line_11 |  | 7 | 12 | 0.015771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-79_0_4_line_12 |  | 8 | 13 | 0.026644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-79_0_4_line_13 |  | 9 | 14 | 0.019851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-79_0_4_line_14 |  | 10 | 23 | 0.0077598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-79_0_4_line_15 |  | 11 | 52 | 0.019981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-79_0_4_line_16 |  | 11 | 50 | 0.022459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-79_0_4_line_17 |  | 12 | 20 | 0.028737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-79_0_4_line_18 |  | 14 | 28 | 0.008277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-79_0_4_line_19 |  | 14 | 27 | 0.017955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-79_0_4_line_20 |  | 15 | 16 | 0.029512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-79_0_4_line_21 |  | 15 | 17 | 0.015806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-79_0_4_line_22 |  | 17 | 18 | 0.020598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-79_0_4_line_23 |  | 18 | 21 | 0.00096262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-79_0_4_line_24 |  | 19 | 20 | 0.032029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-79_0_4_line_25 |  | 20 | 22 | 0.021207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-79_0_4_line_26 |  | 21 | 23 | 0.009332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-79_0_4_line_27 |  | 22 | 53 | 0.0068131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-79_0_4_line_28 |  | 24 | 25 | 0.018916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-79_0_4_line_29 |  | 24 | 26 | 0.015563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-79_0_4_line_30 |  | 25 | 27 | 0.012902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-79_0_4_line_31 |  | 28 | 31 | 0.0131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-79_0_4_line_32 |  | 28 | 30 | 0.012187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-79_0_4_line_33 |  | 29 | 30 | 0.025188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-79_0_4_line_34 |  | 31 | 32 | 0.007564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1630-79_0_4_line_35 |  | 32 | 33 | 0.0045813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1630-79_0_4_line_36 |  | 34 | 35 | 0.008563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-79_0_4_line_37 |  | 35 | 36 | 0.007757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-79_0_4_line_38 |  | 35 | 37 | 0.012964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-79_0_4_line_39 |  | 36 | 38 | 0.006632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-79_0_4_line_40 |  | 36 | 39 | 0.010201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-79_0_4_line_41 |  | 37 | 40 | 0.007547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-79_0_4_line_42 |  | 37 | 41 | 0.011397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-79_0_4_line_43 |  | 38 | 42 | 0.014123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-79_0_4_line_44 |  | 40 | 43 | 0.011015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1630-79_0_4_line_45 |  | 40 | 44 | 0.0084121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1630-79_0_4_line_46 |  | 42 | 45 | 0.004833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1630-79_0_4_line_47 |  | 42 | 46 | 0.009856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1630-79_0_4_line_48 |  | 43 | 55 | 0.037598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1630-79_0_4_line_49 |  | 45 | 53 | 0.029007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1630-79_0_4_line_50 |  | 46 | 49 | 0.0079177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1630-79_0_4_line_51 |  | 47 | 48 | 0.0077933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1630-79_0_4_line_52 |  | 48 | 49 | 0.0066999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1630-79_0_4_line_53 |  | 50 | 51 | 0.018526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1630-79_0_4_line_54 |  | 52 | 54 | 0.0094368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-79_0_4_trafo_3 | 0.63 MVA 20/0.4 kV | 56 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2723229.1268 | 1217272.722 | 2723237.8886 | 1217269.0139
1 | 2723198.1443 | 1217286.3022 | 2723215.5519 | 1217278.4671 | 2723229.1268 | 1217272.722
2 | 2723247.3888 | 1217264.9933 | 2723237.8886 | 1217269.0139
3 | 2723188.7703 | 1217268.8393 | 2723192.5943 | 1217275.9683 | 2723198.1443 | 1217286.3022
4 | 2723198.8095 | 1217287.5502 | 2723198.1443 | 1217286.3022
5 | 2723254.1037 | 1217262.4229 | 2723250.9223 | 1217263.4979 | 2723247.3888 | 1217264.9933
6 | 2723188.7703 | 1217268.8393 | 2723180.0906 | 1217252.6806
7 | 2723188.7703 | 1217268.8393 | 2723172.247 | 1217276.6568
8 | 2723198.8095 | 1217287.5502 | 2723203.0272 | 1217295.4061
9 | 2723254.1037 | 1217262.4229 | 2723259.3879 | 1217260.6374 | 2723267.7592 | 1217258.6646 | 2723267.7592 | 1217258.6646
10 | 2723180.0906 | 1217252.6806 | 2723177.0925 | 1217247.1032
11 | 2723180.0906 | 1217252.6806 | 2723194.1309 | 1217245.4986
12 | 2723172.247 | 1217276.6568 | 2723162.2437 | 1217281.3897 | 2723159.7673 | 1217282.1613 | 2723150.833 | 1217283.0885 | 2723148.1805 | 1217283.9344 | 2723147.1353 | 1217284.5581
13 | 2723212.4171 | 1217312.8957 | 2723203.0272 | 1217295.4061
14 | 2723267.7592 | 1217258.6646 | 2723275.3895 | 1217257.2527
15 | 2723177.0925 | 1217247.1032 | 2723159.3117 | 1217256.2173
16 | 2723166.4682 | 1217227.3015 | 2723177.0925 | 1217247.1032
17 | 2723216.7837 | 1217229.2097 | 2723212.4334 | 1217236.1363 | 2723194.1309 | 1217245.4986
18 | 2723216.1676 | 1217320.279 | 2723212.4171 | 1217312.8957
19 | 2723212.4171 | 1217312.8957 | 2723228.4256 | 1217304.7641
20 | 2723301.7209 | 1217236.9279 | 2723296.0974 | 1217216.2177 | 2723293.2357 | 1217213.5898 | 2723289.4521 | 1217211.8435 | 2723289.4521 | 1217211.8435
21 | 2723305.8626 | 1217252.1811 | 2723301.7209 | 1217236.9279
22 | 2723305.8626 | 1217252.1811 | 2723302.7694 | 1217252.673 | 2723285.5376 | 1217255.5241
23 | 2723285.5376 | 1217255.5241 | 2723284.5879 | 1217255.6813
24 | 2723216.7837 | 1217229.2097 | 2723232.3684 | 1217230.9444 | 2723247.9133 | 1217225.8827
25 | 2723216.7837 | 1217229.2097 | 2723210.3198 | 1217209.0123
26 | 2723275.3895 | 1217257.2527 | 2723277.9207 | 1217256.7844 | 2723284.5879 | 1217255.6813
27 | 2723208.2431 | 1217202.5234 | 2723210.3198 | 1217209.0123
28 | 2723256.8353 | 1217290.4387 | 2723252.424 | 1217292.5738 | 2723239.9287 | 1217298.921
29 | 2723256.8353 | 1217290.4387 | 2723270.8433 | 1217283.6587
30 | 2723239.9287 | 1217298.921 | 2723228.4256 | 1217304.7641
31 | 2723216.1676 | 1217320.279 | 2723222.0994 | 1217331.9663
32 | 2723216.1676 | 1217320.279 | 2723227.2524 | 1217315.2135
33 | 2723252.2128 | 1217313.9518 | 2723229.5298 | 1217314.1728 | 2723227.2524 | 1217315.2135
34 | 2723222.0994 | 1217331.9663 | 2723225.525 | 1217338.7102
35 | 2723227.5998 | 1217342.7947 | 2723225.525 | 1217338.7102
36 | 2723224.6313 | 1217161.1634 | 2723221.4075 | 1217153.2304
37 | 2723224.6313 | 1217161.1634 | 2723217.4901 | 1217164.2404
38 | 2723236.6631 | 1217156.2528 | 2723224.6313 | 1217161.1634
39 | 2723217.4901 | 1217164.2404 | 2723211.1549 | 1217166.2022
40 | 2723217.4901 | 1217164.2404 | 2723219.8636 | 1217174.1609
41 | 2723236.6631 | 1217156.2528 | 2723243.6633 | 1217153.3842
42 | 2723236.6631 | 1217156.2528 | 2723239.4014 | 1217167.3158
43 | 2723197.6644 | 1217170.3798 | 2723211.1549 | 1217166.2022
44 | 2723253.8876 | 1217149.2146 | 2723243.6633 | 1217153.3842
45 | 2723243.6633 | 1217153.3842 | 2723240.3771 | 1217145.6406
46 | 2723197.6644 | 1217170.3798 | 2723199.2099 | 1217174.9597
47 | 2723197.6644 | 1217170.3798 | 2723193.6895 | 1217161.3572
48 | 2723253.8876 | 1217149.2146 | 2723259.3213 | 1217170.6659 | 2723274.6647 | 1217168.7007
49 | 2723199.2099 | 1217174.9597 | 2723203.2813 | 1217187.0199 | 2723208.2431 | 1217202.5234
50 | 2723193.6895 | 1217161.3572 | 2723189.989 | 1217163.6714 | 2723187.733 | 1217166.4164
51 | 2723179.2542 | 1217178.1706 | 2723183.8123 | 1217171.8493
52 | 2723187.733 | 1217166.4164 | 2723187.7065 | 1217166.4486 | 2723183.8123 | 1217171.8493
53 | 2723166.4682 | 1217227.3015 | 2723182.7663 | 1217218.4092
54 | 2723159.3117 | 1217256.2173 | 2723150.9138 | 1217260.5219

## bus_geodata
| x | y | coords
0 | 2723229.1268 | 1217272.722
1 | 2723237.8886 | 1217269.0139
2 | 2723198.1443 | 1217286.3022
3 | 2723247.3888 | 1217264.9933
4 | 2723188.7703 | 1217268.8393
5 | 2723198.8095 | 1217287.5502
6 | 2723254.1037 | 1217262.4229
7 | 2723180.0906 | 1217252.6806
8 | 2723172.247 | 1217276.6568
9 | 2723203.0272 | 1217295.4061
10 | 2723267.7592 | 1217258.6646
11 | 2723177.0925 | 1217247.1032
12 | 2723194.1309 | 1217245.4986
13 | 2723147.1353 | 1217284.5581
14 | 2723212.4171 | 1217312.8957
15 | 2723301.7209 | 1217236.9279
16 | 2723289.4521 | 1217211.8435
17 | 2723305.8626 | 1217252.1811
18 | 2723285.5376 | 1217255.5241
19 | 2723247.9133 | 1217225.8827
20 | 2723216.7837 | 1217229.2097
21 | 2723284.5879 | 1217255.6813
22 | 2723210.3198 | 1217209.0123
23 | 2723275.3895 | 1217257.2527
24 | 2723256.8353 | 1217290.4387
25 | 2723239.9287 | 1217298.921
26 | 2723270.8433 | 1217283.6587
27 | 2723228.4256 | 1217304.7641
28 | 2723216.1676 | 1217320.279
29 | 2723252.2128 | 1217313.9518
30 | 2723227.2524 | 1217315.2135
31 | 2723222.0994 | 1217331.9663
32 | 2723225.525 | 1217338.7102
33 | 2723227.5998 | 1217342.7947
34 | 2723221.4075 | 1217153.2304
35 | 2723224.6313 | 1217161.1634
36 | 2723217.4901 | 1217164.2404
37 | 2723236.6631 | 1217156.2528
38 | 2723211.1549 | 1217166.2022
39 | 2723219.8636 | 1217174.1609
40 | 2723243.6633 | 1217153.3842
41 | 2723239.4014 | 1217167.3158
42 | 2723197.6644 | 1217170.3798
43 | 2723253.8876 | 1217149.2146
44 | 2723240.3771 | 1217145.6406
45 | 2723199.2099 | 1217174.9597
46 | 2723193.6895 | 1217161.3572
47 | 2723179.2542 | 1217178.1706
48 | 2723183.8123 | 1217171.8493
49 | 2723187.733 | 1217166.4164
50 | 2723166.4682 | 1217227.3015
51 | 2723182.7663 | 1217218.4092
52 | 2723159.3117 | 1217256.2173
53 | 2723208.2431 | 1217202.5234
54 | 2723150.9138 | 1217260.5219
55 | 2723274.6647 | 1217168.7007
56 | 2723198.1443 | 1217286.3022

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99804 | -0.037297 | 0.013105 | 0.0032845
1 | 0.99896 | -0.019741 | 0.012388 | 0.0031047
2 | 0.99489 | -0.097382 | 0 | 0
3 | 1 | 0 | -0.41407 | -0.10482
4 | 0.99376 | -0.11913 | 0.029296 | 0.0073422
5 | 0.99474 | -0.10029 | 0 | 0
6 | 0.99948 | -0.0099916 | 0.010394 | 0.0026049
7 | 0.99247 | -0.14385 | 0 | 0
8 | 0.99367 | -0.12072 | 0.0023892 | 0.0005988
9 | 0.99379 | -0.11863 | 0.0027131 | 0.00067997
10 | 0.99859 | -0.027135 | 0.0105 | 0.0026316
11 | 0.99238 | -0.14544 | 0 | 0
12 | 0.99045 | -0.18256 | 0.0036241 | 0.00090829
13 | 0.99361 | -0.1219 | 0.0025268 | 0.00063326
14 | 0.99172 | -0.15865 | 0 | 0
15 | 0.99687 | -0.060106 | 0.012459 | 0.0031226
16 | 0.9965 | -0.06727 | 0.013835 | 0.0034673
17 | 0.99725 | -0.052819 | 0 | 0
18 | 0.99775 | -0.043332 | 0.012397 | 0.0031069
19 | 0.98576 | -0.27332 | 0.037806 | 0.009475
20 | 0.98687 | -0.25163 | 0 | 0
21 | 0.99778 | -0.042679 | 0.007685 | 0.001926
22 | 0.98497 | -0.28851 | 0.0076858 | 0.0019262
23 | 0.99817 | -0.035105 | 0.01236 | 0.0030977
24 | 0.99026 | -0.18684 | 0.010264 | 0.0025725
25 | 0.99063 | -0.17978 | 0.0059994 | 0.0015036
26 | 0.99011 | -0.1898 | 0.010728 | 0.0026887
27 | 0.99094 | -0.1736 | 0.019941 | 0.0049977
28 | 0.99121 | -0.16849 | 0 | 0
29 | 0.98956 | -0.20037 | 0.044743 | 0.011214
30 | 0.9906 | -0.18034 | 0.010002 | 0.0025069
31 | 0.99106 | -0.17135 | 0 | 0
32 | 0.99097 | -0.17301 | 0.0065487 | 0.0016413
33 | 0.99095 | -0.17347 | 0.0057603 | 0.0014437
34 | 0.98055 | -0.37481 | 0.0071781 | 0.001799
35 | 0.9806 | -0.3737 | 0 | 0
36 | 0.98094 | -0.36715 | 0 | 0
37 | 0.98013 | -0.38295 | 0 | 0
38 | 0.98127 | -0.3607 | 0.0071897 | 0.0018019
39 | 0.98087 | -0.36849 | 0.0072085 | 0.0018066
40 | 0.97991 | -0.38736 | 0 | 0
41 | 0.98006 | -0.38444 | 0.0072076 | 0.0018064
42 | 0.98206 | -0.34513 | 0 | 0
43 | 0.97965 | -0.39235 | 0 | 0
44 | 0.97985 | -0.38846 | 0.0071972 | 0.0018038
45 | 0.9824 | -0.33859 | 0 | 0
46 | 0.98194 | -0.34761 | 0 | 0
47 | 0.98171 | -0.35213 | 0.0083543 | 0.0020938
48 | 0.98177 | -0.35095 | 0.0027763 | 0.00069581
49 | 0.98184 | -0.34961 | 0.0027994 | 0.0007016
50 | 0.99223 | -0.14835 | 0 | 0
51 | 0.99211 | -0.15075 | 0.007313 | 0.0018328
52 | 0.99226 | -0.14788 | 0.0032626 | 0.00081769
53 | 0.98441 | -0.29944 | 0.014415 | 0.0036127
54 | 0.99223 | -0.14848 | 0.003626 | 0.00090876
55 | 0.97878 | -0.40942 | 0.024966 | 0.0062571
56 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.31966 | -0.081282 | 0.31993 | 0.081455 | 0.00027059 | 0.00017281 | 0.477 | 0.477 | 0.477 | 0.99804 | -0.037297 | 0.99896 | -0.019741 | 43.6814
1 | 0.30655 | 0.077998 | -0.30566 | -0.077433 | 0.00088496 | 0.00056505 | 0.45746 | 0.45746 | 0.45746 | 0.99804 | -0.037297 | 0.99489 | -0.097382 | 41.8922
2 | -0.33231 | -0.08456 | 0.33263 | 0.084762 | 0.00031654 | 0.00020218 | 0.49545 | 0.49545 | 0.49545 | 0.99896 | -0.019741 | 1 | 0 | 45.3712
3 | 0.18847 | 0.04787 | -0.18827 | -0.047745 | 0.00019706 | 0.00012535 | 0.28211 | 0.28211 | 0.28211 | 0.99489 | -0.097382 | 0.99376 | -0.11913 | 25.8343
4 | 0.1172 | 0.029563 | -0.11718 | -0.029552 | 1.6293e-05 | 1.0409e-05 | 0.17535 | 0.17535 | 0.17535 | 0.99489 | -0.097382 | 0.99474 | -0.10029 | 48.1736
5 | 0.079791 | 0.020059 | -0.079753 | -0.020034 | 3.8049e-05 | 2.4257e-05 | 0.11875 | 0.11875 | 0.11875 | 1 | 0 | 0.99948 | -0.0099916 | 32.6241
6 | 0.15406 | 0.039171 | -0.15388 | -0.039054 | 0.00018323 | 0.00011679 | 0.23088 | 0.23088 | 0.23088 | 0.99376 | -0.11913 | 0.99247 | -0.14385 | 31.7147
7 | 0.0049165 | 0.0012318 | -0.0049161 | -0.0012318 | 3.7149e-07 | 9.4618e-10 | 0.0073616 | 0.0073617 | 0.0073617 | 0.99376 | -0.11913 | 0.99367 | -0.12072 | 2.0225
8 | 0.11718 | 0.029552 | -0.11708 | -0.029487 | 0.00010281 | 6.5685e-05 | 0.17535 | 0.17535 | 0.17535 | 0.99474 | -0.10029 | 0.99379 | -0.11863 | 48.1736
9 | 0.069359 | 0.01743 | -0.069302 | -0.017393 | 5.6711e-05 | 3.611e-05 | 0.10328 | 0.10328 | 0.10328 | 0.99948 | -0.0099916 | 0.99859 | -0.027135 | 28.373
10 | 0.014205 | 0.0035607 | -0.014204 | -0.0035601 | 1.0766e-06 | 6.0727e-07 | 0.021299 | 0.021299 | 0.021299 | 0.99247 | -0.14385 | 0.99238 | -0.14544 | 5.8513
11 | 0.13967 | 0.035493 | -0.13941 | -0.035327 | 0.00025978 | 0.00016605 | 0.20958 | 0.20958 | 0.20958 | 0.99247 | -0.14385 | 0.99045 | -0.18256 | 57.5782
12 | 0.0025269 | 0.00063301 | -0.0025268 | -0.00063326 | 1.4306e-07 | -2.5356e-07 | 0.0037839 | 0.003784 | 0.003784 | 0.99367 | -0.12072 | 0.99361 | -0.1219 | 1.0396
13 | 0.11436 | 0.028807 | -0.11415 | -0.028667 | 0.00021841 | 0.00013953 | 0.17129 | 0.17129 | 0.17129 | 0.99379 | -0.11863 | 0.99172 | -0.15865 | 47.0576
14 | 0.058802 | 0.014762 | -0.05878 | -0.014748 | 2.2346e-05 | 1.42e-05 | 0.087631 | 0.087631 | 0.087631 | 0.99859 | -0.027135 | 0.99817 | -0.035105 | 24.0744
15 | 0.0068895 | 0.0017266 | -0.0068887 | -0.0017264 | 7.9961e-07 | 2.5363e-07 | 0.01033 | 0.01033 | 0.01033 | 0.99238 | -0.14544 | 0.99226 | -0.14788 | 2.838
16 | 0.0073149 | 0.0018335 | -0.0073139 | -0.0018331 | 1.0132e-06 | 3.5833e-07 | 0.010968 | 0.010968 | 0.010968 | 0.99238 | -0.14544 | 0.99223 | -0.14835 | 3.0133
17 | 0.13579 | 0.034419 | -0.13534 | -0.034132 | 0.00044909 | 0.00028705 | 0.20414 | 0.20414 | 0.20414 | 0.99045 | -0.18256 | 0.98687 | -0.25163 | 56.0825
18 | 0.067162 | 0.016874 | -0.067131 | -0.016854 | 3.153e-05 | 2.0072e-05 | 0.10079 | 0.10079 | 0.10079 | 0.99172 | -0.15865 | 0.99121 | -0.16849 | 27.689
19 | 0.046983 | 0.011794 | -0.046949 | -0.011772 | 3.3468e-05 | 2.1188e-05 | 0.070502 | 0.070502 | 0.070502 | 0.99172 | -0.15865 | 0.99094 | -0.1736 | 19.3687
20 | 0.01384 | 0.00347 | -0.013835 | -0.0034673 | 4.7232e-06 | 2.6382e-06 | 0.020658 | 0.020659 | 0.020659 | 0.99687 | -0.060106 | 0.9965 | -0.06727 | 5.6754
21 | -0.026299 | -0.0065925 | 0.026308 | 0.0065982 | 9.1339e-06 | 5.6395e-06 | 0.039256 | 0.039256 | 0.039256 | 0.99687 | -0.060106 | 0.99725 | -0.052819 | 10.7847
22 | -0.026308 | -0.0065982 | 0.02632 | 0.0066055 | 1.1903e-05 | 7.3493e-06 | 0.039256 | 0.039256 | 0.039256 | 0.99725 | -0.052819 | 0.99775 | -0.043332 | 10.7846
23 | -0.038717 | -0.0097125 | 0.038718 | 0.0097132 | 1.2037e-06 | 7.5777e-07 | 0.057744 | 0.057744 | 0.057744 | 0.99775 | -0.043332 | 0.99778 | -0.042679 | 15.8638
24 | -0.037806 | -0.009475 | 0.037845 | 0.0094996 | 3.9117e-05 | 2.4626e-05 | 0.057068 | 0.057068 | 0.057068 | 0.98576 | -0.27332 | 0.98687 | -0.25163 | 15.678
25 | 0.097494 | 0.024632 | -0.097322 | -0.024522 | 0.00017201 | 0.00010982 | 0.14707 | 0.14707 | 0.14707 | 0.98687 | -0.25163 | 0.98497 | -0.28851 | 40.4045
26 | -0.046403 | -0.011639 | 0.04642 | 0.01165 | 1.676e-05 | 1.0605e-05 | 0.069205 | 0.069205 | 0.069205 | 0.99778 | -0.042679 | 0.99817 | -0.035105 | 19.0124
27 | 0.089636 | 0.022596 | -0.089589 | -0.022566 | 4.6882e-05 | 2.9918e-05 | 0.13546 | 0.13546 | 0.13546 | 0.98497 | -0.28851 | 0.98441 | -0.29944 | 37.2147
28 | -0.020994 | -0.005262 | 0.021001 | 0.0052663 | 7.0594e-06 | 4.2746e-06 | 0.031547 | 0.031547 | 0.031547 | 0.99026 | -0.18684 | 0.99063 | -0.17978 | 8.6667
29 | 0.01073 | 0.0026895 | -0.010728 | -0.0026887 | 1.5171e-06 | 7.7076e-07 | 0.016123 | 0.016123 | 0.016123 | 0.99026 | -0.18684 | 0.99011 | -0.1898 | 4.4295
30 | -0.027001 | -0.0067699 | 0.027008 | 0.0067748 | 7.9589e-06 | 4.9275e-06 | 0.040558 | 0.040558 | 0.040558 | 0.99063 | -0.17978 | 0.99094 | -0.1736 | 11.1424
31 | 0.012312 | 0.0030864 | -0.01231 | -0.0030855 | 1.6782e-06 | 9.0522e-07 | 0.018483 | 0.018483 | 0.018483 | 0.99121 | -0.16849 | 0.99106 | -0.17135 | 5.0777
32 | 0.054819 | 0.013767 | -0.054788 | -0.013747 | 3.096e-05 | 1.9657e-05 | 0.082305 | 0.082305 | 0.082305 | 0.99121 | -0.16849 | 0.9906 | -0.18034 | 22.6113
33 | -0.044743 | -0.011214 | 0.044786 | 0.011241 | 4.2756e-05 | 2.704e-05 | 0.06728 | 0.06728 | 0.06728 | 0.98956 | -0.20037 | 0.9906 | -0.18034 | 18.4836
34 | 0.01231 | 0.0030855 | -0.012309 | -0.0030849 | 9.69e-07 | 5.227e-07 | 0.018483 | 0.018483 | 0.018483 | 0.99106 | -0.17135 | 0.99097 | -0.17301 | 5.0777
35 | 0.0057604 | 0.0014437 | -0.0057603 | -0.0014437 | 1.2853e-07 | 2.3239e-08 | 0.0086496 | 0.0086497 | 0.0086497 | 0.99097 | -0.17301 | 0.99095 | -0.17347 | 2.3763
36 | -0.0071781 | -0.001799 | 0.0071785 | 0.0017991 | 3.8103e-07 | 1.3584e-07 | 0.010893 | 0.010893 | 0.010893 | 0.98055 | -0.37481 | 0.9806 | -0.3737 | 2.9926
37 | -0.046601 | -0.011698 | 0.046615 | 0.011707 | 1.4549e-05 | 9.2132e-06 | 0.070721 | 0.070721 | 0.070721 | 0.9806 | -0.3737 | 0.98094 | -0.36715 | 19.4288
38 | 0.039422 | 0.009899 | -0.039405 | -0.009888 | 1.7401e-05 | 1.0973e-05 | 0.059828 | 0.059828 | 0.059828 | 0.9806 | -0.3737 | 0.98013 | -0.38295 | 16.4362
39 | -0.053824 | -0.013514 | 0.053841 | 0.013525 | 1.6583e-05 | 1.0529e-05 | 0.081656 | 0.081656 | 0.081656 | 0.98094 | -0.36715 | 0.98127 | -0.3607 | 22.4331
40 | 0.007209 | 0.0018068 | -0.0072085 | -0.0018066 | 4.5744e-07 | 1.64e-07 | 0.010936 | 0.010936 | 0.010936 | 0.98094 | -0.36715 | 0.98087 | -0.36849 | 3.0043
41 | 0.032197 | 0.0080814 | -0.03219 | -0.0080772 | 6.7632e-06 | 4.2333e-06 | 0.048885 | 0.048885 | 0.048885 | 0.98013 | -0.38295 | 0.97991 | -0.38736 | 13.4299
42 | 0.0072081 | 0.0018066 | -0.0072076 | -0.0018064 | 5.1182e-07 | 1.8394e-07 | 0.010943 | 0.010943 | 0.010943 | 0.98013 | -0.38295 | 0.98006 | -0.38444 | 3.0064
43 | -0.06103 | -0.015327 | 0.061076 | 0.015355 | 4.5371e-05 | 2.8859e-05 | 0.092559 | 0.092559 | 0.092559 | 0.98127 | -0.3607 | 0.98206 | -0.34513 | 25.4283
44 | 0.024992 | 0.0062733 | -0.024986 | -0.0062696 | 5.9505e-06 | 3.6696e-06 | 0.037955 | 0.037955 | 0.037955 | 0.97991 | -0.38736 | 0.97965 | -0.39235 | 10.4272
45 | 0.0071975 | 0.0018039 | -0.0071972 | -0.0018038 | 3.7684e-07 | 1.3521e-07 | 0.01093 | 0.01093 | 0.01093 | 0.97991 | -0.38736 | 0.97985 | -0.38846 | 3.0027
46 | -0.07501 | -0.018849 | 0.075034 | 0.018864 | 2.3418e-05 | 1.4927e-05 | 0.11367 | 0.11367 | 0.11367 | 0.98206 | -0.34513 | 0.9824 | -0.33859 | 31.2287
47 | 0.013934 | 0.0034935 | -0.013933 | -0.0034925 | 1.6476e-06 | 9.2978e-07 | 0.021113 | 0.021114 | 0.021114 | 0.98206 | -0.34513 | 0.98194 | -0.34761 | 5.8004
48 | 0.024986 | 0.0062696 | -0.024966 | -0.0062571 | 2.0311e-05 | 1.2526e-05 | 0.037955 | 0.037955 | 0.037955 | 0.97965 | -0.39235 | 0.97878 | -0.40942 | 10.4273
49 | -0.075034 | -0.018864 | 0.075174 | 0.018953 | 0.00014055 | 8.9587e-05 | 0.11367 | 0.11367 | 0.11367 | 0.9824 | -0.33859 | 0.98441 | -0.29944 | 31.2287
50 | 0.013933 | 0.0034925 | -0.013931 | -0.0034918 | 1.3236e-06 | 7.4695e-07 | 0.021114 | 0.021114 | 0.021114 | 0.98194 | -0.34761 | 0.98184 | -0.34961 | 5.8004
51 | -0.0083543 | -0.0020938 | 0.0083548 | 0.002094 | 4.6862e-07 | 2.0138e-07 | 0.012663 | 0.012663 | 0.012663 | 0.98171 | -0.35213 | 0.98177 | -0.35095 | 3.4789
52 | -0.011131 | -0.0027898 | 0.011132 | 0.0027902 | 7.1512e-07 | 3.7295e-07 | 0.016871 | 0.016871 | 0.016871 | 0.98177 | -0.35095 | 0.98184 | -0.34961 | 4.6349
53 | 0.0073139 | 0.0018331 | -0.007313 | -0.0018328 | 8.358e-07 | 2.9565e-07 | 0.010968 | 0.010968 | 0.010968 | 0.99223 | -0.14835 | 0.99211 | -0.15075 | 3.0133
54 | 0.0036261 | 0.00090871 | -0.003626 | -0.00090876 | 1.0464e-07 | -5.492e-08 | 0.0054378 | 0.0054378 | 0.0054378 | 0.99226 | -0.14788 | 0.99223 | -0.14848 | 1.4939

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42645 | 0.10792

## res_load
| p_mw | q_mvar
0 | 0.013105 | 0.0032845
1 | 0.012388 | 0.0031047
2 | 0.012381 | 0.003103
3 | 0.029296 | 0.0073422
4 | 0.010394 | 0.0026049
5 | 0.0023892 | 0.0005988
6 | 0.0027131 | 0.00067997
7 | 0.0105 | 0.0026316
8 | 0.0036241 | 0.00090829
9 | 0.0025268 | 0.00063326
10 | 0.012459 | 0.0031226
11 | 0.013835 | 0.0034673
12 | 0.012397 | 0.0031069
13 | 0.037806 | 0.009475
14 | 0.007685 | 0.001926
15 | 0.0076858 | 0.0019262
16 | 0.01236 | 0.0030977
17 | 0.010264 | 0.0025725
18 | 0.0059994 | 0.0015036
19 | 0.010728 | 0.0026887
20 | 0.019941 | 0.0049977
21 | 0.044743 | 0.011214
22 | 0.010002 | 0.0025069
23 | 0.0065487 | 0.0016413
24 | 0.0057603 | 0.0014437
25 | 0.0071781 | 0.001799
26 | 0.0071897 | 0.0018019
27 | 0.0072085 | 0.0018066
28 | 0.0072076 | 0.0018064
29 | 0.0071972 | 0.0018038
30 | 0.0083543 | 0.0020938
31 | 0.0027763 | 0.00069581
32 | 0.0027994 | 0.0007016
33 | 0.007313 | 0.0018328
34 | 0.0032626 | 0.00081769
35 | 0.014415 | 0.0036127
36 | 0.003626 | 0.00090876
37 | 0.024966 | 0.0062571

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1