## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-80_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-80_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-80_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-80_0_4_node_16 | 0.4 | n |  | TRUE
4 | bus_LV_1630-80_0_4_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_1630-80_0_4_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_1630-80_0_4_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_1630-80_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_1630-80_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1630-80_0_4_node_3 | 0.4 | n |  | TRUE
10 | bus_LV_1630-80_0_4_node_4 | 0.4 | n |  | TRUE
11 | bus_LV_1630-80_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1630-80_0_4_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_1630-80_0_4_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_1630-80_0_4_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_1630-80_0_4_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_1630-80_0_4_node_33 | 0.4 | n |  | TRUE
17 | bus_LV_1630-80_0_4_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_1630-80_0_4_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1630-80_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1630-80_0_4_node_40 | 0.4 | n |  | TRUE
21 | bus_LV_1630-80_0_4_node_7 | 0.4 | n |  | TRUE
22 | bus_LV_1630-80_0_4_node_8 | 0.4 | n |  | TRUE
23 | bus_LV_1630-80_0_4_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_1630-80_0_4_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_1630-80_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1630-80_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1630-80_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1630-80_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_1630-80_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_1630-80_0_4_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_1630-80_0_4_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_1630-80_0_4_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_1630-80_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1630-80_0_4_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_1630-80_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_1630-80_0_4_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_1630-80_0_4_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1630-80_0_4_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_1630-80_0_4_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_1630-80_0_4_node_41 | 0.4 | n |  | TRUE
41 | bus_MV_152_0_node_100 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-80_0_4_load_0 | 0 | 0.0064489 | 0.0016162 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-80_0_4_load_1 | 1 | 0.006552 | 0.0016421 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-80_0_4_load_12 | 4 | 0.0070606 | 0.0017695 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-80_0_4_load_29 | 6 | 0.0045967 | 0.001152 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-80_0_4_load_13 | 8 | 0.0057981 | 0.0014531 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-80_0_4_load_3 | 9 | 0.0033106 | 0.00082971 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-80_0_4_load_4 | 10 | 0.0031245 | 0.00078308 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-80_0_4_load_21 | 12 | 0.066996 | 0.016791 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-80_0_4_load_31 | 13 | 0.048035 | 0.012039 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-80_0_4_load_27 | 15 | 0.0026128 | 0.00065484 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-80_0_4_load_33 | 16 | 0.0039484 | 0.00098956 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-80_0_4_load_34 | 18 | 0.002431 | 0.00060927 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-80_0_4_load_15 | 19 | 0.0054031 | 0.0013542 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-80_0_4_load_40 | 20 | 0.0039501 | 0.00098999 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-80_0_4_load_7 | 21 | 0.0049078 | 0.00123 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-80_0_4_load_8 | 22 | 0.0051845 | 0.0012994 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-80_0_4_load_10 | 23 | 0.0072465 | 0.0018162 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-80_0_4_load_11 | 24 | 0.0039035 | 0.00097832 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-80_0_4_load_22 | 25 | 0.006428 | 0.001611 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-80_0_4_load_24 | 27 | 0.004593 | 0.0011511 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-80_0_4_load_25 | 28 | 0.005202 | 0.0013037 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-80_0_4_load_35 | 29 | 0.0041557 | 0.0010415 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-80_0_4_load_32 | 30 | 0.048025 | 0.012036 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-80_0_4_load_39 | 31 | 0.057932 | 0.014519 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-80_0_4_load_38 | 32 | 0.048048 | 0.012042 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-80_0_4_load_28 | 33 | 0.0094961 | 0.0023799 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-80_0_4_load_17 | 34 | 0.052989 | 0.01328 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-80_0_4_load_23 | 35 | 0.0063128 | 0.0015821 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-80_0_4_load_30 | 37 | 0.048852 | 0.012244 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-80_0_4_load_37 | 38 | 0.0092617 | 0.0023212 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-80_0_4_load_41 | 40 | 0.0084353 | 0.0021141 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-80_0_4_line_0 |  | 0 | 1 | 0.012188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-80_0_4_line_1 |  | 1 | 2 | 0.010601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-80_0_4_line_2 |  | 2 | 3 | 0.024915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-80_0_4_line_3 |  | 2 | 4 | 0.0202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-80_0_4_line_4 |  | 2 | 5 | 0.033545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-80_0_4_line_5 |  | 3 | 6 | 0.013084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-80_0_4_line_6 |  | 4 | 7 | 0.011558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-80_0_4_line_7 |  | 5 | 8 | 0.0068292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-80_0_4_line_8 |  | 6 | 33 | 0.017121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-80_0_4_line_9 |  | 7 | 24 | 0.0033604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-80_0_4_line_10 |  | 7 | 21 | 0.012043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-80_0_4_line_11 |  | 8 | 19 | 0.016531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-80_0_4_line_12 |  | 9 | 10 | 0.0073282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-80_0_4_line_13 |  | 10 | 11 | 0.0171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-80_0_4_line_14 |  | 11 | 15 | 0.015863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-80_0_4_line_15 |  | 11 | 16 | 0.0097043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-80_0_4_line_16 |  | 12 | 13 | 0.036552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-80_0_4_line_17 |  | 12 | 14 | 0.016043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-80_0_4_line_18 |  | 13 | 30 | 0.0054647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_1630-80_0_4_line_19 |  | 13 | 37 | 0.0065029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-80_0_4_line_20 |  | 14 | 34 | 0.028665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-80_0_4_line_21 |  | 15 | 17 | 0.0095272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-80_0_4_line_22 |  | 16 | 18 | 0.0018992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-80_0_4_line_23 |  | 17 | 27 | 0.012065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-80_0_4_line_24 |  | 18 | 29 | 0.00058876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-80_0_4_line_25 |  | 19 | 20 | 0.033629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-80_0_4_line_26 |  | 20 | 31 | 0.0025848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-80_0_4_line_27 |  | 21 | 22 | 0.010927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-80_0_4_line_28 |  | 22 | 23 | 0.012603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-80_0_4_line_29 |  | 24 | 25 | 0.016691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-80_0_4_line_30 |  | 25 | 26 | 0.01295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-80_0_4_line_31 |  | 26 | 35 | 0.027901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-80_0_4_line_32 |  | 27 | 28 | 0.020138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-80_0_4_line_33 |  | 29 | 30 | 0.015272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-80_0_4_line_34 |  | 30 | 32 | 0.0075565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1630-80_0_4_line_35 |  | 31 | 32 | 0.0071745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1630-80_0_4_line_36 |  | 35 | 36 | 0.023599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1630-80_0_4_line_37 |  | 36 | 38 | 0.006951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-80_0_4_line_38 |  | 38 | 39 | 0.050443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1630-80_0_4_line_39 |  | 39 | 40 | 0.02002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-80_0_4_trafo_39 | 0.63 MVA 20/0.4 kV | 41 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2723468.5568 | 1217198.8759 | 2723456.3799 | 1217198.3551
1 | 2723445.7883 | 1217197.9021 | 2723456.3799 | 1217198.3551
2 | 2723429.1735 | 1217208.8554 | 2723446.2094 | 1217205.4278 | 2723445.7883 | 1217197.9021
3 | 2723445.7883 | 1217197.9021 | 2723444.6413 | 1217177.7351
4 | 2723453.8204 | 1217229.1484 | 2723448.566 | 1217223.2572 | 2723447.2398 | 1217219.827 | 2723446.2094 | 1217205.4278 | 2723445.7883 | 1217197.9021
5 | 2723429.1735 | 1217208.8554 | 2723417.8492 | 1217209.6771 | 2723416.1635 | 1217210.0655
6 | 2723443.9851 | 1217166.1956 | 2723444.6413 | 1217177.7351
7 | 2723453.8204 | 1217229.1484 | 2723459.4334 | 1217226.1623 | 2723459.9043 | 1217226.182
8 | 2723399.5091 | 1217214.0188 | 2723400.803 | 1217213.605 | 2723416.1635 | 1217210.0655
9 | 2723443.9851 | 1217166.1956 | 2723444.2028 | 1217162.8422
10 | 2723443.9851 | 1217166.1956 | 2723453.0398 | 1217167.5286 | 2723455.7487 | 1217168.5363
11 | 2723476.4214 | 1217226.8704 | 2723459.9043 | 1217226.182
12 | 2723551.3635 | 1217219.1347 | 2723544.3707 | 1217221.3262
13 | 2723528.0537 | 1217226.44 | 2723544.3707 | 1217221.3262
14 | 2723528.0537 | 1217226.44 | 2723528.6643 | 1217232.513 | 2723531.5372 | 1217241.8399
15 | 2723528.0537 | 1217226.44 | 2723524.8014 | 1217217.2969
16 | 2723511.3808 | 1217164.6792 | 2723524.169 | 1217198.921
17 | 2723506.0847 | 1217149.5358 | 2723511.3808 | 1217164.6792
18 | 2723518.9468 | 1217200.5311 | 2723524.169 | 1217198.921
19 | 2723530.3832 | 1217197.005 | 2723524.169 | 1217198.921
20 | 2723506.0847 | 1217149.5358 | 2723532.3719 | 1217138.1041
21 | 2723534.3418 | 1217250.945 | 2723531.5372 | 1217241.8399
22 | 2723524.8014 | 1217217.2969 | 2723524.1649 | 1217215.5075
23 | 2723534.3418 | 1217250.945 | 2723522.8626 | 1217254.6592
24 | 2723523.9676 | 1217214.9528 | 2723524.1649 | 1217215.5075
25 | 2723476.4214 | 1217226.8704 | 2723502.3433 | 1217205.4464
26 | 2723502.3433 | 1217205.4464 | 2723504.8217 | 1217204.7126
27 | 2723465.9898 | 1217172.3457 | 2723455.7487 | 1217168.5363
28 | 2723478.2018 | 1217174.6999 | 2723471.7815 | 1217174.5001 | 2723465.9898 | 1217172.3457
29 | 2723445.2842 | 1217146.1865 | 2723444.2028 | 1217162.8422
30 | 2723447.1713 | 1217133.3805 | 2723445.3795 | 1217144.7188 | 2723445.2842 | 1217146.1865
31 | 2723447.1713 | 1217133.3805 | 2723422.6595 | 1217120.0527
32 | 2723522.8626 | 1217254.6592 | 2723503.7024 | 1217260.8586
33 | 2723518.9468 | 1217200.5311 | 2723520.096 | 1217204.0687 | 2723523.9676 | 1217214.9528
34 | 2723518.9468 | 1217200.5311 | 2723511.7011 | 1217202.6761
35 | 2723511.7011 | 1217202.6761 | 2723504.8217 | 1217204.7126
36 | 2723401.9272 | 1217108.7799 | 2723422.6595 | 1217120.0527
37 | 2723401.9272 | 1217108.7799 | 2723398.6786 | 1217114.9285
38 | 2723398.6786 | 1217114.9285 | 2723355.2925 | 1217140.6615
39 | 2723368.4046 | 1217155.8225 | 2723355.2925 | 1217140.6615

## bus_geodata
| x | y | coords
0 | 2723468.5568 | 1217198.8759
1 | 2723456.3799 | 1217198.3551
2 | 2723445.7883 | 1217197.9021
3 | 2723429.1735 | 1217208.8554
4 | 2723444.6413 | 1217177.7351
5 | 2723453.8204 | 1217229.1484
6 | 2723416.1635 | 1217210.0655
7 | 2723443.9851 | 1217166.1956
8 | 2723459.9043 | 1217226.182
9 | 2723551.3635 | 1217219.1347
10 | 2723544.3707 | 1217221.3262
11 | 2723528.0537 | 1217226.44
12 | 2723511.3807 | 1217164.6792
13 | 2723524.169 | 1217198.921
14 | 2723506.0847 | 1217149.5358
15 | 2723531.5372 | 1217241.8399
16 | 2723524.8014 | 1217217.2969
17 | 2723534.3418 | 1217250.945
18 | 2723524.1649 | 1217215.5075
19 | 2723476.4214 | 1217226.8704
20 | 2723502.3433 | 1217205.4463
21 | 2723455.7487 | 1217168.5363
22 | 2723465.9898 | 1217172.3457
23 | 2723478.2018 | 1217174.6999
24 | 2723444.2028 | 1217162.8422
25 | 2723445.2842 | 1217146.1865
26 | 2723447.1713 | 1217133.3805
27 | 2723522.8626 | 1217254.6592
28 | 2723503.7024 | 1217260.8586
29 | 2723523.9676 | 1217214.9528
30 | 2723518.9468 | 1217200.5311
31 | 2723504.8217 | 1217204.7126
32 | 2723511.7011 | 1217202.6761
33 | 2723399.5091 | 1217214.0188
34 | 2723532.3719 | 1217138.1041
35 | 2723422.6595 | 1217120.0527
36 | 2723401.9272 | 1217108.7799
37 | 2723530.3832 | 1217197.005
38 | 2723398.6786 | 1217114.9285
39 | 2723355.2925 | 1217140.6615
40 | 2723368.4046 | 1217155.8225
41 | 2723502.3433 | 1217205.4463

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99202 | -0.15324 | 0.0064489 | 0.0016162
1 | 0.99209 | -0.15185 | 0.006552 | 0.0016421
2 | 0.99221 | -0.14941 | 0 | 0
3 | 0.99189 | -0.15563 | 0 | 0
4 | 0.99113 | -0.17044 | 0.0070606 | 0.0017695
5 | 0.99485 | -0.098565 | 0 | 0
6 | 0.99172 | -0.1589 | 0.0045967 | 0.001152
7 | 0.99058 | -0.18105 | 0 | 0
8 | 0.99539 | -0.088247 | 0.0057981 | 0.0014531
9 | 0.99783 | -0.041642 | 0.0033106 | 0.00082971
10 | 0.99785 | -0.041217 | 0.0031245 | 0.00078308
11 | 0.99795 | -0.039291 | 0 | 0
12 | 0.99404 | -0.11464 | 0.066996 | 0.016791
13 | 0.99804 | -0.037591 | 0.048035 | 0.012039
14 | 0.99326 | -0.12965 | 0 | 0
15 | 0.99777 | -0.042737 | 0.0026128 | 0.00065484
16 | 0.99812 | -0.036091 | 0.0039484 | 0.00098956
17 | 0.99769 | -0.044371 | 0 | 0
18 | 0.99816 | -0.035333 | 0.002431 | 0.00060927
19 | 0.99677 | -0.061633 | 0.0054031 | 0.0013542
20 | 0.99976 | -0.0045512 | 0.0039501 | 0.00098999
21 | 0.99039 | -0.18476 | 0.0049078 | 0.00123
22 | 0.99026 | -0.18717 | 0.0051845 | 0.0012994
23 | 0.99018 | -0.1888 | 0.0072465 | 0.0018162
24 | 0.99047 | -0.1831 | 0.0039035 | 0.00097832
25 | 0.99001 | -0.19213 | 0.006428 | 0.001611
26 | 0.98972 | -0.19766 | 0 | 0
27 | 0.99758 | -0.046441 | 0.004593 | 0.0011511
28 | 0.99749 | -0.048276 | 0.005202 | 0.0013037
29 | 0.99817 | -0.035074 | 0.0041557 | 0.0010415
30 | 0.99858 | -0.027227 | 0.048025 | 0.012036
31 | 1 | 0 | -0.44687 | -0.11232
32 | 0.99925 | -0.01428 | 0.048048 | 0.012042
33 | 0.99157 | -0.16178 | 0.0094961 | 0.0023799
34 | 0.99187 | -0.15652 | 0.052989 | 0.01328
35 | 0.98911 | -0.20959 | 0.0063128 | 0.0015821
36 | 0.98872 | -0.21704 | 0 | 0
37 | 0.99775 | -0.043151 | 0.048852 | 0.012244
38 | 0.98861 | -0.21923 | 0.0092617 | 0.0023212
39 | 0.98822 | -0.22682 | 0 | 0
40 | 0.98807 | -0.22984 | 0.0084353 | 0.0021141
41 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0064489 | -0.0016162 | 0.0064493 | 0.0016164 | 4.2767e-07 | 1.1634e-07 | 0.0096733 | 0.0096732 | 0.0096733 | 0.99202 | -0.15324 | 0.99209 | -0.15185 | 2.6575
1 | -0.013001 | -0.0032584 | 0.013003 | 0.0032593 | 1.5117e-06 | 8.3061e-07 | 0.0195 | 0.0195 | 0.0195 | 0.99209 | -0.15185 | 0.99221 | -0.14941 | 5.3573
2 | 0.0141 | 0.0035362 | -0.014096 | -0.0035338 | 4.1783e-06 | 2.3524e-06 | 0.021147 | 0.021147 | 0.021147 | 0.99221 | -0.14941 | 0.99189 | -0.15563 | 5.8097
3 | 0.05888 | 0.014808 | -0.058821 | -0.01477 | 5.9087e-05 | 3.7555e-05 | 0.08832 | 0.08832 | 0.08832 | 0.99221 | -0.14941 | 0.99113 | -0.17044 | 24.2638
4 | -0.085983 | -0.021603 | 0.086193 | 0.021737 | 0.00020923 | 0.00013347 | 0.12897 | 0.12897 | 0.12897 | 0.99221 | -0.14941 | 0.99485 | -0.098565 | 35.4307
5 | 0.014096 | 0.0035338 | -0.014094 | -0.0035326 | 2.1942e-06 | 1.2355e-06 | 0.021147 | 0.021147 | 0.021147 | 0.99189 | -0.15563 | 0.99172 | -0.1589 | 5.8097
6 | 0.05176 | 0.013001 | -0.051734 | -0.012984 | 2.6181e-05 | 1.6607e-05 | 0.07772 | 0.07772 | 0.07772 | 0.99113 | -0.17044 | 0.99058 | -0.18105 | 21.3517
7 | -0.086193 | -0.021737 | 0.086235 | 0.021764 | 4.2596e-05 | 2.7172e-05 | 0.12897 | 0.12897 | 0.12897 | 0.99485 | -0.098565 | 0.99539 | -0.088247 | 35.4307
8 | 0.0094974 | 0.0023806 | -0.0094961 | -0.0023799 | 1.3038e-06 | 6.1357e-07 | 0.01425 | 0.01425 | 0.01425 | 0.99172 | -0.1589 | 0.99157 | -0.16178 | 3.9149
9 | 0.03439 | 0.008636 | -0.034387 | -0.0086339 | 3.3638e-06 | 2.1096e-06 | 0.051666 | 0.051666 | 0.051666 | 0.99058 | -0.18105 | 0.99047 | -0.1831 | 14.1939
10 | 0.017344 | 0.0043483 | -0.017341 | -0.0043465 | 3.0655e-06 | 1.8069e-06 | 0.026054 | 0.026054 | 0.026054 | 0.99058 | -0.18105 | 0.99039 | -0.18476 | 7.1577
11 | -0.092033 | -0.023217 | 0.092151 | 0.023292 | 0.00011744 | 7.4944e-05 | 0.13764 | 0.13764 | 0.13764 | 0.99539 | -0.088247 | 0.99677 | -0.061633 | 37.8119
12 | -0.0033106 | -0.00082971 | 0.0033106 | 0.00082965 | 6.6978e-08 | -5.286e-08 | 0.0049369 | 0.0049368 | 0.0049369 | 0.99783 | -0.041642 | 0.99785 | -0.041217 | 1.3563
13 | -0.0064351 | -0.0016127 | 0.0064357 | 0.0016129 | 5.9048e-07 | 1.5452e-07 | 0.0095962 | 0.0095961 | 0.0095962 | 0.99785 | -0.041217 | 0.99795 | -0.039291 | 2.6363
14 | 0.012412 | 0.0031117 | -0.01241 | -0.0031106 | 2.0376e-06 | 1.0968e-06 | 0.018508 | 0.018508 | 0.018508 | 0.99795 | -0.039291 | 0.99777 | -0.042737 | 5.0845
15 | -0.018848 | -0.0047245 | 0.018851 | 0.0047263 | 2.8742e-06 | 1.7127e-06 | 0.028104 | 0.028104 | 0.028104 | 0.99795 | -0.039291 | 0.99812 | -0.036091 | 7.7208
16 | -0.12009 | -0.030138 | 0.12053 | 0.030421 | 0.00044304 | 0.00028307 | 0.17978 | 0.17978 | 0.17978 | 0.99404 | -0.11464 | 0.99804 | -0.037591 | 49.3914
17 | 0.053095 | 0.013348 | -0.053057 | -0.013323 | 3.8018e-05 | 2.4124e-05 | 0.079495 | 0.079495 | 0.079495 | 0.99404 | -0.11464 | 0.99326 | -0.12965 | 21.8393
18 | -0.21744 | -0.054712 | 0.21754 | 0.054781 | 0.00010773 | 6.8807e-05 | 0.32426 | 0.32426 | 0.32426 | 0.99804 | -0.037591 | 0.99858 | -0.027227 | 44.541
19 | 0.048865 | 0.012252 | -0.048852 | -0.012244 | 1.2944e-05 | 8.1993e-06 | 0.072857 | 0.072857 | 0.072857 | 0.99804 | -0.037591 | 0.99775 | -0.043151 | 20.0156
20 | 0.053057 | 0.013323 | -0.052989 | -0.01328 | 6.7931e-05 | 4.3105e-05 | 0.079495 | 0.079495 | 0.079495 | 0.99326 | -0.12965 | 0.99187 | -0.15652 | 21.8393
21 | 0.0097972 | 0.0024557 | -0.0097965 | -0.0024554 | 7.6272e-07 | 3.6372e-07 | 0.014611 | 0.014611 | 0.014611 | 0.99777 | -0.042737 | 0.99769 | -0.044371 | 4.014
22 | -0.022799 | -0.0057158 | 0.0228 | 0.0057163 | 8.2282e-07 | 5.0178e-07 | 0.03399 | 0.03399 | 0.03399 | 0.99812 | -0.036091 | 0.99816 | -0.035333 | 9.3379
23 | 0.0097965 | 0.0024554 | -0.0097955 | -0.0024549 | 9.659e-07 | 4.6064e-07 | 0.014611 | 0.014611 | 0.014611 | 0.99769 | -0.044371 | 0.99758 | -0.046441 | 4.0141
24 | -0.025231 | -0.0063256 | 0.025231 | 0.0063258 | 3.1237e-07 | 1.9222e-07 | 0.037614 | 0.037614 | 0.037614 | 0.99816 | -0.035333 | 0.99817 | -0.035074 | 10.3335
25 | -0.097554 | -0.024646 | 0.097822 | 0.024817 | 0.00026772 | 0.0001709 | 0.1457 | 0.1457 | 0.1457 | 0.99677 | -0.061633 | 0.99976 | -0.0045512 | 40.0278
26 | -0.10177 | -0.025807 | 0.10179 | 0.025821 | 2.2271e-05 | 1.422e-05 | 0.15158 | 0.15158 | 0.15158 | 0.99976 | -0.0045512 | 1 | 0 | 41.6429
27 | 0.012433 | 0.0031165 | -0.012432 | -0.0031157 | 1.4298e-06 | 7.7451e-07 | 0.01868 | 0.01868 | 0.01868 | 0.99039 | -0.18476 | 0.99026 | -0.18717 | 5.132
28 | 0.0072471 | 0.0018164 | -0.0072465 | -0.0018162 | 5.6046e-07 | 1.9657e-07 | 0.01089 | 0.01089 | 0.01089 | 0.99026 | -0.18717 | 0.99018 | -0.1888 | 2.9917
29 | 0.030483 | 0.0076555 | -0.03047 | -0.0076473 | 1.313e-05 | 8.1886e-06 | 0.045802 | 0.045802 | 0.045802 | 0.99047 | -0.1831 | 0.99001 | -0.19213 | 12.5829
30 | 0.024042 | 0.0060363 | -0.024036 | -0.0060324 | 6.3427e-06 | 3.8929e-06 | 0.03614 | 0.03614 | 0.03614 | 0.99001 | -0.19213 | 0.98972 | -0.19766 | 9.9286
31 | 0.024036 | 0.0060324 | -0.024022 | -0.0060241 | 1.3666e-05 | 8.3877e-06 | 0.03614 | 0.03614 | 0.03614 | 0.98972 | -0.19766 | 0.98911 | -0.20959 | 9.9287
32 | 0.0052025 | 0.0013038 | -0.005202 | -0.0013037 | 4.5477e-07 | 2.8155e-08 | 0.0077601 | 0.0077602 | 0.0077602 | 0.99758 | -0.046441 | 0.99749 | -0.048276 | 2.1319
33 | -0.029387 | -0.0073673 | 0.029398 | 0.0073741 | 1.0991e-05 | 6.8347e-06 | 0.043809 | 0.043809 | 0.043809 | 0.99817 | -0.035074 | 0.99858 | -0.027227 | 12.0355
34 | -0.29497 | -0.074191 | 0.29515 | 0.074308 | 0.00018256 | 0.00011654 | 0.43963 | 0.43963 | 0.43963 | 0.99858 | -0.027227 | 0.99925 | -0.01428 | 40.2593
35 | 0.34343 | 0.086499 | -0.3432 | -0.08635 | 0.00023434 | 0.0001497 | 0.51118 | 0.51118 | 0.51118 | 1 | 0 | 0.99925 | -0.01428 | 46.8114
36 | 0.017709 | 0.0044419 | -0.017703 | -0.0044382 | 6.282e-06 | 3.7177e-06 | 0.026643 | 0.026643 | 0.026643 | 0.98911 | -0.20959 | 0.98872 | -0.21704 | 7.3196
37 | 0.017703 | 0.0044382 | -0.017701 | -0.0044371 | 1.8504e-06 | 1.0951e-06 | 0.026643 | 0.026643 | 0.026643 | 0.98872 | -0.21704 | 0.98861 | -0.21923 | 7.3196
38 | 0.0084395 | 0.0021159 | -0.0084365 | -0.0021146 | 3.0526e-06 | 1.3071e-06 | 0.012703 | 0.012703 | 0.012703 | 0.98861 | -0.21923 | 0.98822 | -0.22682 | 3.4899
39 | 0.0084365 | 0.0021146 | -0.0084353 | -0.0021141 | 1.2115e-06 | 5.1892e-07 | 0.012703 | 0.012703 | 0.012703 | 0.98822 | -0.22682 | 0.98807 | -0.22984 | 3.4899

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50481 | 0.12684

## res_load
| p_mw | q_mvar
0 | 0.0064489 | 0.0016162
1 | 0.006552 | 0.0016421
2 | 0.0070606 | 0.0017695
3 | 0.0045967 | 0.001152
4 | 0.0057981 | 0.0014531
5 | 0.0033106 | 0.00082971
6 | 0.0031245 | 0.00078308
7 | 0.066996 | 0.016791
8 | 0.048035 | 0.012039
9 | 0.0026128 | 0.00065484
10 | 0.0039484 | 0.00098956
11 | 0.002431 | 0.00060927
12 | 0.0054031 | 0.0013542
13 | 0.0039501 | 0.00098999
14 | 0.0049078 | 0.00123
15 | 0.0051845 | 0.0012994
16 | 0.0072465 | 0.0018162
17 | 0.0039035 | 0.00097832
18 | 0.006428 | 0.001611
19 | 0.004593 | 0.0011511
20 | 0.005202 | 0.0013037
21 | 0.0041557 | 0.0010415
22 | 0.048025 | 0.012036
23 | 0.057932 | 0.014519
24 | 0.048048 | 0.012042
25 | 0.0094961 | 0.0023799
26 | 0.052989 | 0.01328
27 | 0.0063128 | 0.0015821
28 | 0.048852 | 0.012244
29 | 0.0092617 | 0.0023212
30 | 0.0084353 | 0.0021141

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1