## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1630-84_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1630-84_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1630-84_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1630-84_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1630-84_0_6_node_145 | 0.4 | n |  | TRUE
5 | bus_LV_1630-84_0_6_node_156 | 0.4 | n |  | TRUE
6 | bus_LV_1630-84_0_6_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_1630-84_0_6_node_144 | 0.4 | n |  | TRUE
8 | bus_LV_1630-84_0_6_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_1630-84_0_6_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1630-84_0_6_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1630-84_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1630-84_0_6_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1630-84_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1630-84_0_6_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_1630-84_0_6_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1630-84_0_6_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1630-84_0_6_node_37 | 0.4 | n |  | TRUE
18 | bus_LV_1630-84_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1630-84_0_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1630-84_0_6_node_84 | 0.4 | n |  | TRUE
21 | bus_LV_1630-84_0_6_node_81 | 0.4 | n |  | TRUE
22 | bus_LV_1630-84_0_6_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_1630-84_0_6_node_154 | 0.4 | n |  | TRUE
24 | bus_LV_1630-84_0_6_node_155 | 0.4 | n |  | TRUE
25 | bus_LV_1630-84_0_6_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1630-84_0_6_node_153 | 0.4 | n |  | TRUE
27 | bus_LV_1630-84_0_6_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1630-84_0_6_node_140 | 0.4 | n |  | TRUE
29 | bus_LV_1630-84_0_6_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1630-84_0_6_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1630-84_0_6_node_108 | 0.4 | n |  | TRUE
32 | bus_LV_1630-84_0_6_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1630-84_0_6_node_55 | 0.4 | n |  | TRUE
34 | bus_LV_1630-84_0_6_node_138 | 0.4 | n |  | TRUE
35 | bus_LV_1630-84_0_6_node_80 | 0.4 | n |  | TRUE
36 | bus_LV_1630-84_0_6_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_1630-84_0_6_node_157 | 0.4 | n |  | TRUE
38 | bus_LV_1630-84_0_6_node_123 | 0.4 | n |  | TRUE
39 | bus_LV_1630-84_0_6_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_1630-84_0_6_node_92 | 0.4 | n |  | TRUE
41 | bus_LV_1630-84_0_6_node_116 | 0.4 | n |  | TRUE
42 | bus_LV_1630-84_0_6_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_1630-84_0_6_node_152 | 0.4 | n |  | TRUE
44 | bus_LV_1630-84_0_6_node_147 | 0.4 | n |  | TRUE
45 | bus_LV_1630-84_0_6_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_1630-84_0_6_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_1630-84_0_6_node_86 | 0.4 | n |  | TRUE
48 | bus_LV_1630-84_0_6_node_82 | 0.4 | n |  | TRUE
49 | bus_LV_1630-84_0_6_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_1630-84_0_6_node_139 | 0.4 | n |  | TRUE
51 | bus_LV_1630-84_0_6_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_1630-84_0_6_node_67 | 0.4 | n |  | TRUE
53 | bus_LV_1630-84_0_6_node_94 | 0.4 | n |  | TRUE
54 | bus_LV_1630-84_0_6_node_95 | 0.4 | n |  | TRUE
55 | bus_LV_1630-84_0_6_node_105 | 0.4 | n |  | TRUE
56 | bus_LV_1630-84_0_6_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_1630-84_0_6_node_137 | 0.4 | n |  | TRUE
58 | bus_LV_1630-84_0_6_node_79 | 0.4 | n |  | TRUE
59 | bus_LV_1630-84_0_6_node_124 | 0.4 | n |  | TRUE
60 | bus_LV_1630-84_0_6_node_121 | 0.4 | n |  | TRUE
61 | bus_LV_1630-84_0_6_node_90 | 0.4 | n |  | TRUE
62 | bus_LV_1630-84_0_6_node_131 | 0.4 | n |  | TRUE
63 | bus_LV_1630-84_0_6_node_114 | 0.4 | n |  | TRUE
64 | bus_LV_1630-84_0_6_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_1630-84_0_6_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_1630-84_0_6_node_150 | 0.4 | n |  | TRUE
67 | bus_LV_1630-84_0_6_node_158 | 0.4 | n |  | TRUE
68 | bus_LV_1630-84_0_6_node_149 | 0.4 | n |  | TRUE
69 | bus_LV_1630-84_0_6_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_1630-84_0_6_node_30 | 0.4 | n |  | TRUE
71 | bus_LV_1630-84_0_6_node_31 | 0.4 | n |  | TRUE
72 | bus_LV_1630-84_0_6_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_1630-84_0_6_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_1630-84_0_6_node_73 | 0.4 | n |  | TRUE
75 | bus_LV_1630-84_0_6_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_1630-84_0_6_node_32 | 0.4 | n |  | TRUE
77 | bus_LV_1630-84_0_6_node_33 | 0.4 | n |  | TRUE
78 | bus_LV_1630-84_0_6_node_36 | 0.4 | n |  | TRUE
79 | bus_LV_1630-84_0_6_node_74 | 0.4 | n |  | TRUE
80 | bus_LV_1630-84_0_6_node_126 | 0.4 | n |  | TRUE
81 | bus_LV_1630-84_0_6_node_41 | 0.4 | n |  | TRUE
82 | bus_LV_1630-84_0_6_node_127 | 0.4 | n |  | TRUE
83 | bus_LV_1630-84_0_6_node_60 | 0.4 | n |  | TRUE
84 | bus_LV_1630-84_0_6_node_38 | 0.4 | n |  | TRUE
85 | bus_LV_1630-84_0_6_node_39 | 0.4 | n |  | TRUE
86 | bus_LV_1630-84_0_6_node_42 | 0.4 | n |  | TRUE
87 | bus_LV_1630-84_0_6_node_40 | 0.4 | n |  | TRUE
88 | bus_LV_1630-84_0_6_node_49 | 0.4 | n |  | TRUE
89 | bus_LV_1630-84_0_6_node_117 | 0.4 | n |  | TRUE
90 | bus_LV_1630-84_0_6_node_133 | 0.4 | n |  | TRUE
91 | bus_LV_1630-84_0_6_node_47 | 0.4 | n |  | TRUE
92 | bus_LV_1630-84_0_6_node_146 | 0.4 | n |  | TRUE
93 | bus_LV_1630-84_0_6_node_45 | 0.4 | n |  | TRUE
94 | bus_LV_1630-84_0_6_node_50 | 0.4 | n |  | TRUE
95 | bus_LV_1630-84_0_6_node_51 | 0.4 | n |  | TRUE
96 | bus_LV_1630-84_0_6_node_87 | 0.4 | n |  | TRUE
97 | bus_LV_1630-84_0_6_node_134 | 0.4 | n |  | TRUE
98 | bus_LV_1630-84_0_6_node_85 | 0.4 | n |  | TRUE
99 | bus_LV_1630-84_0_6_node_135 | 0.4 | n |  | TRUE
100 | bus_LV_1630-84_0_6_node_52 | 0.4 | n |  | TRUE
101 | bus_LV_1630-84_0_6_node_54 | 0.4 | n |  | TRUE
102 | bus_LV_1630-84_0_6_node_56 | 0.4 | n |  | TRUE
103 | bus_LV_1630-84_0_6_node_102 | 0.4 | n |  | TRUE
104 | bus_LV_1630-84_0_6_node_61 | 0.4 | n |  | TRUE
105 | bus_LV_1630-84_0_6_node_62 | 0.4 | n |  | TRUE
106 | bus_LV_1630-84_0_6_node_63 | 0.4 | n |  | TRUE
107 | bus_LV_1630-84_0_6_node_64 | 0.4 | n |  | TRUE
108 | bus_LV_1630-84_0_6_node_66 | 0.4 | n |  | TRUE
109 | bus_LV_1630-84_0_6_node_99 | 0.4 | n |  | TRUE
110 | bus_LV_1630-84_0_6_node_122 | 0.4 | n |  | TRUE
111 | bus_LV_1630-84_0_6_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_1630-84_0_6_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_1630-84_0_6_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_1630-84_0_6_node_68 | 0.4 | n |  | TRUE
115 | bus_LV_1630-84_0_6_node_69 | 0.4 | n |  | TRUE
116 | bus_LV_1630-84_0_6_node_70 | 0.4 | n |  | TRUE
117 | bus_LV_1630-84_0_6_node_71 | 0.4 | n |  | TRUE
118 | bus_LV_1630-84_0_6_node_72 | 0.4 | n |  | TRUE
119 | bus_LV_1630-84_0_6_node_75 | 0.4 | n |  | TRUE
120 | bus_LV_1630-84_0_6_node_76 | 0.4 | n |  | TRUE
121 | bus_LV_1630-84_0_6_node_77 | 0.4 | n |  | TRUE
122 | bus_LV_1630-84_0_6_node_78 | 0.4 | n |  | TRUE
123 | bus_LV_1630-84_0_6_node_109 | 0.4 | n |  | TRUE
124 | bus_LV_1630-84_0_6_node_111 | 0.4 | n |  | TRUE
125 | bus_LV_1630-84_0_6_node_130 | 0.4 | n |  | TRUE
126 | bus_LV_1630-84_0_6_node_112 | 0.4 | n |  | TRUE
127 | bus_LV_1630-84_0_6_node_128 | 0.4 | n |  | TRUE
128 | bus_LV_1630-84_0_6_node_142 | 0.4 | n |  | TRUE
129 | bus_LV_1630-84_0_6_node_110 | 0.4 | n |  | TRUE
130 | bus_LV_1630-84_0_6_node_83 | 0.4 | n |  | TRUE
131 | bus_LV_1630-84_0_6_node_88 | 0.4 | n |  | TRUE
132 | bus_LV_1630-84_0_6_node_89 | 0.4 | n |  | TRUE
133 | bus_LV_1630-84_0_6_node_91 | 0.4 | n |  | TRUE
134 | bus_LV_1630-84_0_6_node_93 | 0.4 | n |  | TRUE
135 | bus_LV_1630-84_0_6_node_141 | 0.4 | n |  | TRUE
136 | bus_LV_1630-84_0_6_node_148 | 0.4 | n |  | TRUE
137 | bus_LV_1630-84_0_6_node_96 | 0.4 | n |  | TRUE
138 | bus_LV_1630-84_0_6_node_136 | 0.4 | n |  | TRUE
139 | bus_LV_1630-84_0_6_node_101 | 0.4 | n |  | TRUE
140 | bus_LV_1630-84_0_6_node_103 | 0.4 | n |  | TRUE
141 | bus_LV_1630-84_0_6_node_106 | 0.4 | n |  | TRUE
142 | bus_LV_1630-84_0_6_node_107 | 0.4 | n |  | TRUE
143 | bus_LV_1630-84_0_6_node_125 | 0.4 | n |  | TRUE
144 | bus_LV_1630-84_0_6_node_115 | 0.4 | n |  | TRUE
145 | bus_LV_1630-84_0_6_node_118 | 0.4 | n |  | TRUE
146 | bus_LV_1630-84_0_6_node_113 | 0.4 | n |  | TRUE
147 | bus_LV_1630-84_0_6_node_119 | 0.4 | n |  | TRUE
148 | bus_LV_1630-84_0_6_node_132 | 0.4 | n |  | TRUE
149 | bus_LV_1630-84_0_6_node_120 | 0.4 | n |  | TRUE
150 | bus_LV_1630-84_0_6_node_129 | 0.4 | n |  | TRUE
151 | bus_LV_1630-84_0_6_node_143 | 0.4 | n |  | TRUE
152 | bus_MV_225_0_node_103 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1630-84_0_6_load_0 | 0 | 0.0071568 | 0.0017937 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1630-84_0_6_load_2 | 2 | 0.0039588 | 0.00099218 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1630-84_0_6_load_145 | 4 | 0.00684 | 0.0017143 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1630-84_0_6_load_156 | 5 | 0.015531 | 0.0038924 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1630-84_0_6_load_144 | 7 | 0.005811 | 0.0014564 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1630-84_0_6_load_27 | 8 | 0.0087315 | 0.0021883 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1630-84_0_6_load_4 | 9 | 0.0048623 | 0.0012186 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1630-84_0_6_load_5 | 10 | 0.0037676 | 0.00094425 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1630-84_0_6_load_7 | 12 | 0.0041768 | 0.0010468 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1630-84_0_6_load_8 | 13 | 0.0043488 | 0.0010899 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1630-84_0_6_load_28 | 14 | 0.0064672 | 0.0016208 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1630-84_0_6_load_37 | 17 | 0.0088376 | 0.0022149 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1630-84_0_6_load_81 | 21 | 0.0060122 | 0.0015068 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1630-84_0_6_load_154 | 23 | 0.0093579 | 0.0023453 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1630-84_0_6_load_155 | 24 | 0.0091089 | 0.0022829 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1630-84_0_6_load_153 | 26 | 0.0031092 | 0.00077924 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1630-84_0_6_load_140 | 28 | 0.0051546 | 0.0012919 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1630-84_0_6_load_108 | 31 | 0.0050866 | 0.0012748 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1630-84_0_6_load_138 | 34 | 0.0058724 | 0.0014718 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1630-84_0_6_load_80 | 35 | 0.0086603 | 0.0021705 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1630-84_0_6_load_157 | 37 | 0.012562 | 0.0031483 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1630-84_0_6_load_92 | 40 | 0.0070423 | 0.001765 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1630-84_0_6_load_152 | 43 | 0.029761 | 0.0074589 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1630-84_0_6_load_86 | 47 | 0.006836 | 0.0017133 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1630-84_0_6_load_82 | 48 | 0.00645 | 0.0016165 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1630-84_0_6_load_139 | 50 | 0.0050383 | 0.0012627 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1630-84_0_6_load_67 | 52 | 0.0078416 | 0.0019653 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1630-84_0_6_load_94 | 53 | 0.0064138 | 0.0016075 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1630-84_0_6_load_95 | 54 | 0.0037626 | 0.00094298 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1630-84_0_6_load_105 | 55 | 0.0043919 | 0.0011007 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1630-84_0_6_load_53 | 56 | 0.0043295 | 0.0010851 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1630-84_0_6_load_137 | 57 | 0.0025444 | 0.0006377 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1630-84_0_6_load_79 | 58 | 0.008768 | 0.0021975 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1630-84_0_6_load_124 | 59 | 0.0066125 | 0.0016572 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1630-84_0_6_load_121 | 60 | 0.012093 | 0.0030307 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1630-84_0_6_load_131 | 62 | 0.0020411 | 0.00051154 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1630-84_0_6_load_48 | 64 | 0.0062264 | 0.0015605 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1630-84_0_6_load_46 | 65 | 0.0067201 | 0.0016842 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1630-84_0_6_load_158 | 67 | 0.0039704 | 0.00099507 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1630-84_0_6_load_149 | 68 | 0.031465 | 0.0078859 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1630-84_0_6_load_31 | 71 | 0.005357 | 0.0013426 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1630-84_0_6_load_57 | 72 | 0.0053681 | 0.0013454 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1630-84_0_6_load_59 | 73 | 0.0027508 | 0.00068942 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1630-84_0_6_load_73 | 74 | 0.0086668 | 0.0021721 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1630-84_0_6_load_32 | 76 | 0.012793 | 0.0032062 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1630-84_0_6_load_126 | 80 | 0.0050307 | 0.0012608 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1630-84_0_6_load_127 | 82 | 0.0040896 | 0.001025 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1630-84_0_6_load_60 | 83 | 0.0042691 | 0.0010699 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1630-84_0_6_load_38 | 84 | 0.0049631 | 0.0012439 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1630-84_0_6_load_42 | 86 | 0.0044406 | 0.0011129 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1630-84_0_6_load_133 | 90 | 0.0031763 | 0.00079606 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1630-84_0_6_load_146 | 92 | 0.0051454 | 0.0012896 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1630-84_0_6_load_45 | 93 | 0.0041832 | 0.0010484 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1630-84_0_6_load_50 | 94 | 0.0037593 | 0.00094217 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1630-84_0_6_load_51 | 95 | 0.0041056 | 0.001029 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1630-84_0_6_load_87 | 96 | 0.0045567 | 0.001142 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1630-84_0_6_load_85 | 98 | 0.005224 | 0.0013093 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1630-84_0_6_load_52 | 100 | 0.0053784 | 0.001348 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1630-84_0_6_load_54 | 101 | 0.0052384 | 0.0013129 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1630-84_0_6_load_56 | 102 | 0.012534 | 0.0031414 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1630-84_0_6_load_61 | 104 | 0.0080431 | 0.0020158 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1630-84_0_6_load_64 | 107 | 0.008672 | 0.0021734 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1630-84_0_6_load_99 | 109 | 0.0079787 | 0.0019997 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1630-84_0_6_load_122 | 110 | 0.0063199 | 0.0015839 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1630-84_0_6_load_97 | 111 | 0.0083059 | 0.0020816 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1630-84_0_6_load_100 | 112 | 0.0063059 | 0.0015804 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1630-84_0_6_load_98 | 113 | 0.0052799 | 0.0013233 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1630-84_0_6_load_68 | 114 | 0.0070763 | 0.0017735 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1630-84_0_6_load_69 | 115 | 0.0085258 | 0.0021368 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1630-84_0_6_load_70 | 116 | 0.0069221 | 0.0017348 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1630-84_0_6_load_71 | 117 | 0.0081596 | 0.002045 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1630-84_0_6_load_72 | 118 | 0.0081105 | 0.0020327 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1630-84_0_6_load_75 | 119 | 0.0099702 | 0.0024988 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1630-84_0_6_load_76 | 120 | 0.0049614 | 0.0012434 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1630-84_0_6_load_77 | 121 | 0.002507 | 0.0006283 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1630-84_0_6_load_109 | 123 | 0.0059416 | 0.0014891 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1630-84_0_6_load_128 | 127 | 0.0014126 | 0.00035404 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1630-84_0_6_load_142 | 128 | 0.0041957 | 0.0010516 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1630-84_0_6_load_110 | 129 | 0.002276 | 0.00057041 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1630-84_0_6_load_83 | 130 | 0.0043948 | 0.0011014 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1630-84_0_6_load_88 | 131 | 0.0045806 | 0.001148 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1630-84_0_6_load_141 | 135 | 0.0068812 | 0.0017246 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1630-84_0_6_load_148 | 136 | 0.0043027 | 0.0010784 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1630-84_0_6_load_136 | 138 | 0.0042743 | 0.0010713 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1630-84_0_6_load_101 | 139 | 0.0033915 | 0.00084999 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1630-84_0_6_load_125 | 143 | 0.00297 | 0.00074435 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1630-84_0_6_load_115 | 144 | 0.0025621 | 0.00064212 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1630-84_0_6_load_118 | 145 | 0.0027105 | 0.00067932 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1630-84_0_6_load_113 | 146 | 0.0015471 | 0.00038774 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1630-84_0_6_load_132 | 148 | 0.00232 | 0.00058144 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1630-84_0_6_load_129 | 150 | 0.005 | 0.0012531 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1630-84_0_6_load_143 | 151 | 0.0025533 | 0.00063991 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1630-84_0_6_line_0 |  | 0 | 1 | 0.010204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1630-84_0_6_line_1 |  | 1 | 2 | 0.011129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1630-84_0_6_line_2 |  | 1 | 3 | 0.007946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1630-84_0_6_line_3 |  | 2 | 4 | 0.0048618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1630-84_0_6_line_4 |  | 3 | 5 | 0.012203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1630-84_0_6_line_5 |  | 3 | 6 | 0.011551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1630-84_0_6_line_6 |  | 4 | 7 | 0.0056486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1630-84_0_6_line_7 |  | 6 | 8 | 0.013326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1630-84_0_6_line_8 |  | 7 | 16 | 0.018578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1630-84_0_6_line_9 |  | 9 | 10 | 0.0299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1630-84_0_6_line_10 |  | 9 | 11 | 0.0065487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1630-84_0_6_line_11 |  | 10 | 12 | 0.010451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1630-84_0_6_line_12 |  | 11 | 13 | 0.0095925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1630-84_0_6_line_13 |  | 12 | 14 | 0.016469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1630-84_0_6_line_14 |  | 14 | 45 | 0.0026686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1630-84_0_6_line_15 |  | 15 | 16 | 0.008464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1630-84_0_6_line_16 |  | 15 | 17 | 0.010552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1630-84_0_6_line_17 |  | 17 | 46 | 0.0034136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1630-84_0_6_line_18 |  | 18 | 19 | 0.014301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1630-84_0_6_line_19 |  | 18 | 20 | 0.025507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1630-84_0_6_line_20 |  | 18 | 21 | 0.0091262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1630-84_0_6_line_21 |  | 19 | 24 | 0.013649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1630-84_0_6_line_22 |  | 19 | 22 | 0.048474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1630-84_0_6_line_23 |  | 20 | 47 | 0.0081843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1630-84_0_6_line_24 |  | 21 | 48 | 9.218e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1630-84_0_6_line_25 |  | 22 | 23 | 0.019706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1630-84_0_6_line_26 |  | 25 | 26 | 0.014304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1630-84_0_6_line_27 |  | 25 | 27 | 0.20637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1630-84_0_6_line_28 |  | 27 | 28 | 0.012047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1630-84_0_6_line_29 |  | 28 | 49 | 0.010237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1630-84_0_6_line_30 |  | 29 | 30 | 0.012726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1630-84_0_6_line_31 |  | 29 | 31 | 0.021341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1630-84_0_6_line_32 |  | 30 | 35 | 0.0046503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1630-84_0_6_line_33 |  | 31 | 52 | 0.014409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1630-84_0_6_line_34 |  | 32 | 33 | 0.013318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1630-84_0_6_line_35 |  | 32 | 34 | 0.0075503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1630-84_0_6_line_36 |  | 33 | 55 | 0.014391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1630-84_0_6_line_37 |  | 33 | 56 | 0.019649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1630-84_0_6_line_38 |  | 34 | 57 | 0.0063312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_1630-84_0_6_line_39 |  | 35 | 58 | 0.0081237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1630-84_0_6_line_40 |  | 36 | 37 | 0.010025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1630-84_0_6_line_41 |  | 36 | 38 | 0.027121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1630-84_0_6_line_42 |  | 38 | 59 | 0.009289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1630-84_0_6_line_43 |  | 38 | 60 | 0.030989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1630-84_0_6_line_44 |  | 39 | 40 | 0.092117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_1630-84_0_6_line_45 |  | 39 | 41 | 0.050145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_1630-84_0_6_line_46 |  | 40 | 61 | 0.068521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_1630-84_0_6_line_47 |  | 41 | 62 | 0.013129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1630-84_0_6_line_48 |  | 41 | 63 | 0.016172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_1630-84_0_6_line_49 |  | 42 | 43 | 0.07079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1630-84_0_6_line_50 |  | 42 | 44 | 0.15177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1630-84_0_6_line_51 |  | 44 | 68 | 0.021105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1630-84_0_6_line_52 |  | 44 | 69 | 0.01927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1630-84_0_6_line_53 |  | 44 | 66 | 0.19101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1630-84_0_6_line_54 |  | 45 | 70 | 0.036558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1630-84_0_6_line_55 |  | 45 | 71 | 0.038782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1630-84_0_6_line_56 |  | 46 | 76 | 0.012676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1630-84_0_6_line_57 |  | 47 | 98 | 0.00089143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1630-84_0_6_line_58 |  | 48 | 130 | 0.0055659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1630-84_0_6_line_59 |  | 49 | 75 | 0.004235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1630-84_0_6_line_60 |  | 49 | 87 | 0.004567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1630-84_0_6_line_61 |  | 50 | 51 | 0.0094013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1630-84_0_6_line_62 |  | 51 | 89 | 0.005562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1630-84_0_6_line_63 |  | 51 | 87 | 0.012999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1630-84_0_6_line_64 |  | 53 | 54 | 0.0014359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1630-84_0_6_line_65 |  | 54 | 137 | 0.0083082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1630-84_0_6_line_66 |  | 55 | 103 | 0.020132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_1630-84_0_6_line_67 |  | 56 | 100 | 0.0099389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1630-84_0_6_line_68 |  | 57 | 138 | 0.0077622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_1630-84_0_6_line_69 |  | 58 | 118 | 0.0078643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1630-84_0_6_line_70 |  | 60 | 110 | 0.0046105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1630-84_0_6_line_71 |  | 61 | 134 | 0.004037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_1630-84_0_6_line_72 |  | 61 | 131 | 0.05566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1630-84_0_6_line_73 |  | 62 | 125 | 0.0087106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1630-84_0_6_line_74 |  | 63 | 144 | 0.014383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_1630-84_0_6_line_75 |  | 63 | 146 | 0.0053531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1630-84_0_6_line_76 |  | 64 | 65 | 0.0045061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1630-84_0_6_line_77 |  | 65 | 93 | 0.0095443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1630-84_0_6_line_78 |  | 66 | 67 | 0.002536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1630-84_0_6_line_79 |  | 69 | 110 | 0.018199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1630-84_0_6_line_80 |  | 69 | 105 | 0.017617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1630-84_0_6_line_81 |  | 70 | 72 | 0.0040953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1630-84_0_6_line_82 |  | 72 | 75 | 0.013648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1630-84_0_6_line_83 |  | 73 | 74 | 0.0025938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1630-84_0_6_line_84 |  | 74 | 78 | 0.005031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1630-84_0_6_line_85 |  | 75 | 83 | 0.023192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1630-84_0_6_line_86 |  | 76 | 77 | 0.013998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1630-84_0_6_line_87 |  | 77 | 78 | 0.007477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1630-84_0_6_line_88 |  | 78 | 79 | 0.010516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1630-84_0_6_line_89 |  | 79 | 82 | 0.0063811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1630-84_0_6_line_90 |  | 79 | 83 | 0.0075768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1630-84_0_6_line_91 |  | 80 | 81 | 0.0013756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1630-84_0_6_line_92 |  | 81 | 88 | 0.004565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_1630-84_0_6_line_93 |  | 81 | 85 | 0.003711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_1630-84_0_6_line_94 |  | 82 | 86 | 0.011118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_1630-84_0_6_line_95 |  | 84 | 85 | 0.0070453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1630-84_0_6_line_96 |  | 85 | 86 | 0.0064992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_1630-84_0_6_line_97 |  | 88 | 90 | 0.019011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_1630-84_0_6_line_98 |  | 88 | 91 | 0.019577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1630-84_0_6_line_99 |  | 89 | 92 | 0.010028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1630-84_0_6_line_100 |  | 90 | 97 | 0.0088944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_1630-84_0_6_line_101 |  | 91 | 94 | 0.0044486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1630-84_0_6_line_102 |  | 91 | 95 | 0.0073859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1630-84_0_6_line_103 |  | 91 | 93 | 0.012193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1630-84_0_6_line_104 |  | 94 | 96 | 0.01555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1630-84_0_6_line_105 |  | 96 | 98 | 0.010379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1630-84_0_6_line_106 |  | 97 | 99 | 0.00636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_1630-84_0_6_line_107 |  | 99 | 137 | 0.006549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_1630-84_0_6_line_108 |  | 100 | 101 | 0.0084111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1630-84_0_6_line_109 |  | 101 | 102 | 0.0029048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1630-84_0_6_line_110 |  | 103 | 139 | 0.012533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_1630-84_0_6_line_111 |  | 104 | 105 | 0.0049144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
112 | LV_1630-84_0_6_line_112 |  | 104 | 106 | 0.016399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_1630-84_0_6_line_113 |  | 105 | 107 | 0.010829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1630-84_0_6_line_114 |  | 106 | 108 | 0.014153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_1630-84_0_6_line_115 |  | 107 | 109 | 0.0077063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1630-84_0_6_line_116 |  | 108 | 111 | 0.0021706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_1630-84_0_6_line_117 |  | 109 | 112 | 0.0071879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1630-84_0_6_line_118 |  | 111 | 113 | 0.044629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_1630-84_0_6_line_119 |  | 112 | 119 | 0.0011946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1630-84_0_6_line_120 |  | 113 | 134 | 0.025509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_1630-84_0_6_line_121 |  | 114 | 115 | 0.0079703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1630-84_0_6_line_122 |  | 114 | 116 | 0.0074006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1630-84_0_6_line_123 |  | 115 | 117 | 0.0088821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1630-84_0_6_line_124 |  | 116 | 118 | 0.0076328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1630-84_0_6_line_125 |  | 117 | 119 | 0.0087635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1630-84_0_6_line_126 |  | 120 | 121 | 0.0063808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1630-84_0_6_line_127 |  | 121 | 122 | 0.053392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1630-84_0_6_line_128 |  | 122 | 123 | 0.11553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1630-84_0_6_line_129 |  | 123 | 129 | 0.032274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1630-84_0_6_line_130 |  | 124 | 125 | 0.047956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1630-84_0_6_line_131 |  | 124 | 126 | 0.16058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_1630-84_0_6_line_132 |  | 124 | 127 | 0.01468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_1630-84_0_6_line_133 |  | 125 | 148 | 0.010556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1630-84_0_6_line_134 |  | 126 | 128 | 0.038571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_1630-84_0_6_line_135 |  | 129 | 133 | 0.071756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1630-84_0_6_line_136 |  | 131 | 132 | 0.036203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1630-84_0_6_line_137 |  | 132 | 133 | 0.022743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1630-84_0_6_line_138 |  | 133 | 135 | 0.007094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1630-84_0_6_line_139 |  | 134 | 136 | 0.070515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1630-84_0_6_line_140 |  | 137 | 138 | 0.0022853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
141 | LV_1630-84_0_6_line_141 |  | 139 | 140 | 0.010377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
142 | LV_1630-84_0_6_line_142 |  | 140 | 141 | 0.003004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
143 | LV_1630-84_0_6_line_143 |  | 140 | 142 | 0.015459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1630-84_0_6_line_144 |  | 141 | 143 | 0.008941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1630-84_0_6_line_145 |  | 141 | 144 | 0.013944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
146 | LV_1630-84_0_6_line_146 |  | 142 | 145 | 0.015805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1630-84_0_6_line_147 |  | 145 | 147 | 0.028983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_1630-84_0_6_line_148 |  | 147 | 149 | 0.059983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_1630-84_0_6_line_149 |  | 149 | 150 | 0.029735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_1630-84_0_6_line_150 |  | 150 | 151 | 0.0044929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1630-84_0_6_trafo_22 | 0.63 MVA 20/0.4 kV | 152 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19
0 | 2722936.1679 | 1217645.5721 | 2722932.0671 | 1217636.2288
1 | 2722936.1679 | 1217645.5721 | 2722945.4328 | 1217644.0509 | 2722947.1479 | 1217644.3442
2 | 2722928.3049 | 1217646.8664 | 2722936.1679 | 1217645.5721
3 | 2722951.9401 | 1217645.1638 | 2722947.1479 | 1217644.3442
4 | 2722928.3049 | 1217646.8664 | 2722927.7457 | 1217655.1947 | 2722928.7395 | 1217658.9181
5 | 2722928.3049 | 1217646.8664 | 2722925.4096 | 1217647.3404 | 2722917.6045 | 1217643.621
6 | 2722956.4281 | 1217648.5571 | 2722953.4188 | 1217645.995 | 2722951.9401 | 1217645.1638 | 2722951.9401 | 1217645.1638
7 | 2722917.6045 | 1217643.621 | 2722914.8147 | 1217636.0464 | 2722915.4421 | 1217630.8303
8 | 2722973.5897 | 1217655.4074 | 2722962.6502 | 1217651.979 | 2722960.4566 | 1217650.8328 | 2722956.8589 | 1217648.9238 | 2722956.4281 | 1217648.5571
9 | 2722867.769 | 1217624.9053 | 2722883.8931 | 1217650.0846
10 | 2722864.2374 | 1217619.3905 | 2722867.769 | 1217624.9053
11 | 2722883.8931 | 1217650.0846 | 2722889.5288 | 1217658.8854
12 | 2722864.2374 | 1217619.3905 | 2722869.0666 | 1217620.869 | 2722873.185 | 1217622.7844
13 | 2722889.5288 | 1217658.8854 | 2722898.41 | 1217672.7541
14 | 2722899.8491 | 1217675.0014 | 2722898.41 | 1217672.7541
15 | 2722971.0161 | 1217663.4717 | 2722973.5897 | 1217655.4074
16 | 2722971.0161 | 1217663.4717 | 2722965.0815 | 1217672.1961
17 | 2722963.1616 | 1217675.0186 | 2722965.0815 | 1217672.1961
18 | 2723004.1232 | 1217674.1188 | 2723008.0686 | 1217678.6815 | 2723010.296 | 1217686.6448
19 | 2723018.9119 | 1217710.6525 | 2723015.3675 | 1217701.0163 | 2723010.296 | 1217686.6448
20 | 2723010.296 | 1217686.6448 | 2723001.7417 | 1217689.8247
21 | 2723004.1232 | 1217674.1188 | 2722991.4209 | 1217679.205
22 | 2723004.1232 | 1217674.1188 | 2723008.0686 | 1217678.6815 | 2723007.2408 | 1217664.3533 | 2723014.9311 | 1217662.5995 | 2723030.826 | 1217661.0265 | 2723035.0557 | 1217661.0138
23 | 2723018.9119 | 1217710.6525 | 2723011.3182 | 1217713.705
24 | 2723001.6553 | 1217689.8568 | 2723001.7417 | 1217689.8247
25 | 2723035.0557 | 1217661.0138 | 2723032.8651 | 1217666.3394 | 2723025.3205 | 1217670.598 | 2723025.6972 | 1217675.8877
26 | 2722761.2653 | 1217687.8328 | 2722758.3928 | 1217688.3073 | 2722750.0736 | 1217689.637 | 2722747.1025 | 1217690.1095
27 | 2722761.2653 | 1217687.8328 | 2722760.7937 | 1217684.5538 | 2722759.415 | 1217679.6105 | 2722756.3803 | 1217670.641 | 2722756.3532 | 1217664.5913 | 2722760.2601 | 1217666.2397 | 2722772.2887 | 1217681.6662 | 2722779.2248 | 1217686.2904 | 2722786.1239 | 1217690.1245 | 2722792.3044 | 1217691.6196 | 2722799.6755 | 1217695.3967 | 2722805.4159 | 1217699.0845 | 2722813.7281 | 1217705.4608 | 2722823.2735 | 1217716.0991 | 2722842.3499 | 1217732.9276 | 2722852.9757 | 1217737.9395 | 2722862.1549 | 1217741.665 | 2722878.7962 | 1217744.021 | 2722902.5035 | 1217740.2737 | 2722910.6726 | 1217739.2302
28 | 2722910.6726 | 1217739.2302 | 2722914.1932 | 1217734.9439 | 2722919.6938 | 1217731.4795
29 | 2722928.4079 | 1217726.108 | 2722925.0484 | 1217728.107 | 2722919.6938 | 1217731.4795
30 | 2723101.3583 | 1217855.4234 | 2723093.1313 | 1217865.15
31 | 2723093.1313 | 1217865.15 | 2723098.3136 | 1217868.6375 | 2723110.02 | 1217878.1667
32 | 2723101.3583 | 1217855.4234 | 2723105.1176 | 1217858.1608
33 | 2723121.6978 | 1217886.5855 | 2723113.9279 | 1217881.3478 | 2723110.02 | 1217878.1667
34 | 2722959.8325 | 1217785.8585 | 2722962.2448 | 1217787.8098 | 2722965.3618 | 1217789.4642 | 2722971.5992 | 1217791.8726
35 | 2722971.5992 | 1217791.8726 | 2722973.5425 | 1217787.1201 | 2722973.4596 | 1217784.7057
36 | 2722959.8325 | 1217785.8585 | 2722957.0118 | 1217791.5491 | 2722952.4699 | 1217798.1825
37 | 2722959.8325 | 1217785.8585 | 2722940.7086 | 1217781.3458
38 | 2722973.2424 | 1217778.3782 | 2722973.4596 | 1217784.7057
39 | 2723111.6849 | 1217862.9427 | 2723105.1176 | 1217858.1608
40 | 2723118.7953 | 1217837.2695 | 2723119.9278 | 1217840.5177 | 2723117.0189 | 1217846.4289
41 | 2723139.388 | 1217861.8586 | 2723117.0189 | 1217846.4289
42 | 2723139.388 | 1217861.8586 | 2723144.9857 | 1217854.4352
43 | 2723139.388 | 1217861.8586 | 2723143.2853 | 1217864.33 | 2723166.3891 | 1217877.0494
44 | 2723015.0606 | 1217826.5077 | 2723020.2101 | 1217830.4838 | 2723059.0304 | 1217906.7873
45 | 2722970.972 | 1217848.3481 | 2722999.1908 | 1217837.9113 | 2723007.7923 | 1217834.3082 | 2723010.663 | 1217832.0768 | 2723015.0606 | 1217826.5077
46 | 2723091.2193 | 1217967.1901 | 2723088.5698 | 1217963.8661 | 2723066.201 | 1217920.8817 | 2723059.0304 | 1217906.7873
47 | 2722970.972 | 1217848.3481 | 2722959.6646 | 1217855.0199
48 | 2722970.972 | 1217848.3481 | 2722962.4607 | 1217841.3337 | 2722961.1329 | 1217839.4493 | 2722960.3545 | 1217836.6977
49 | 2723249.5557 | 1217804.6359 | 2723241.3915 | 1217841.0288 | 2723239.7149 | 1217843.5294 | 2723225.264 | 1217844.3201 | 2723211.6619 | 1217852.9011
50 | 2723204.9751 | 1217889.1022 | 2723206.5898 | 1217888.4907 | 2723212.5858 | 1217884.9452 | 2723217.6005 | 1217882.5804 | 2723240.2561 | 1217875.3432 | 2723255.3544 | 1217868.5836 | 2723258.7316 | 1217868.2976 | 2723264.6112 | 1217867.8078 | 2723265.039 | 1217863.6467 | 2723265.5887 | 1217859.4659 | 2723266.8381 | 1217853.3981 | 2723272.6831 | 1217835.1381 | 2723279.5159 | 1217813.1846 | 2723249.5557 | 1217804.6359
51 | 2723204.9751 | 1217889.1022 | 2723212.4098 | 1217908.8602
52 | 2723186.3711 | 1217888.0501 | 2723189.2062 | 1217889.3764 | 2723192.9961 | 1217890.4334 | 2723197.2335 | 1217890.7768 | 2723202.9546 | 1217889.8721 | 2723204.9751 | 1217889.1022
53 | 2723204.9751 | 1217889.1022 | 2723206.5898 | 1217888.4907 | 2723212.5858 | 1217884.9452 | 2723217.6005 | 1217882.5804 | 2723240.2561 | 1217875.3432 | 2723255.3544 | 1217868.5836 | 2723258.7316 | 1217868.2976 | 2723264.6112 | 1217867.8078 | 2723264.432 | 1217872.4299 | 2723264.5579 | 1217878.0813 | 2723265.1032 | 1217884.0195 | 2723266.0845 | 1217890.1668 | 2723267.5495 | 1217897.5251 | 2723274.2663 | 1217931.4127 | 2723275.2907 | 1217936.5823 | 2723238.9982 | 1217935.7532 | 2723217.9303 | 1217935.2616
54 | 2722899.8491 | 1217675.0014 | 2722906.6048 | 1217686.1494 | 2722917.7795 | 1217706.8738
55 | 2722899.8491 | 1217675.0014 | 2722887.7872 | 1217680.3346 | 2722885.1617 | 1217683.1938 | 2722883.6887 | 1217686.1324 | 2722882.9892 | 1217689.4872 | 2722883.2419 | 1217693.0619 | 2722885.7425 | 1217704.199
56 | 2722963.1616 | 1217675.0186 | 2722955.7313 | 1217677.4227 | 2722952.1402 | 1217680.7067
57 | 2723010.4911 | 1217714.0374 | 2723011.3182 | 1217713.705
58 | 2722996.4382 | 1217691.7961 | 2723001.6553 | 1217689.8568
59 | 2722926.1969 | 1217722.493 | 2722928.4079 | 1217726.108
60 | 2722930.7952 | 1217730.0048 | 2722928.4079 | 1217726.108
61 | 2722937.5899 | 1217741.098 | 2722928.2112 | 1217740.4472
62 | 2722937.5899 | 1217741.098 | 2722940.2837 | 1217745.9685
63 | 2722937.5899 | 1217741.098 | 2722930.7952 | 1217730.0048
64 | 2722982.5343 | 1217766.8931 | 2722981.1142 | 1217767.1058
65 | 2722972.8977 | 1217768.3366 | 2722981.1142 | 1217767.1058
66 | 2722943.6865 | 1217816.16 | 2722944.6919 | 1217813.4342 | 2722947.7758 | 1217805.2915 | 2722951.3435 | 1217799.8275 | 2722952.4699 | 1217798.1825
67 | 2722931.1012 | 1217778.8158 | 2722931.1012 | 1217778.8158 | 2722935.5087 | 1217780.1188 | 2722940.7086 | 1217781.3458
68 | 2722972.9761 | 1217770.6206 | 2722973.2424 | 1217778.3782
69 | 2723111.6849 | 1217862.9427 | 2723118.0423 | 1217867.5718
70 | 2723166.3891 | 1217877.0494 | 2723170.428 | 1217879.2729
71 | 2723094.34 | 1217964.6192 | 2723091.2193 | 1217967.1901
72 | 2723091.2193 | 1217967.1901 | 2723090.37 | 1217970.4417 | 2723087.8968 | 1218010.7443 | 2723086.7788 | 1218022.6122
73 | 2722952.1626 | 1217859.4464 | 2722959.6646 | 1217855.0199
74 | 2722960.3545 | 1217836.6977 | 2722946.2109 | 1217834.0821
75 | 2722960.3545 | 1217836.6977 | 2722959.9618 | 1217831.3591
76 | 2723006.364 | 1217731.2658 | 2723009.12 | 1217731.4443 | 2723010.7339 | 1217732.1062
77 | 2722996.8397 | 1217730.6489 | 2723006.364 | 1217731.2658
78 | 2723215.3877 | 1217935.209 | 2723217.9303 | 1217935.2616
79 | 2723186.3711 | 1217888.0501 | 2723170.428 | 1217879.2729
80 | 2723175.8506 | 1217902.1992 | 2723186.3711 | 1217888.0501
81 | 2722917.7795 | 1217706.8738 | 2722919.7224 | 1217710.4789
82 | 2722926.1969 | 1217722.493 | 2722919.7224 | 1217710.4789
83 | 2722944.8616 | 1217697.4939 | 2722942.2688 | 1217697.5675
84 | 2722949.8906 | 1217697.351 | 2722944.8616 | 1217697.4939
85 | 2722926.1969 | 1217722.493 | 2722943.9075 | 1217714.6188 | 2722944.9476 | 1217710.9534
86 | 2722956.505 | 1217694.0071 | 2722952.1402 | 1217680.7067
87 | 2722949.8906 | 1217697.351 | 2722951.5675 | 1217695.9401 | 2722956.505 | 1217694.0071
88 | 2722951.1211 | 1217707.6289 | 2722949.4086 | 1217698.9979 | 2722949.8906 | 1217697.351
89 | 2722951.1211 | 1217707.6289 | 2722955.3865 | 1217707.7281 | 2722957.4341 | 1217708.2561
90 | 2722951.1211 | 1217707.6289 | 2722949.2522 | 1217708.7801 | 2722945.316 | 1217709.6551 | 2722944.9476 | 1217710.9534
91 | 2722964.3682 | 1217723.9594 | 2722964.1513 | 1217722.601
92 | 2722964.3682 | 1217723.9594 | 2722965.0876 | 1217728.4666
93 | 2722964.3682 | 1217723.9594 | 2722960.7791 | 1217724.9416
94 | 2722957.4341 | 1217708.2561 | 2722958.3397 | 1217708.4896 | 2722959.1565 | 1217710.8527 | 2722960.0355 | 1217718.4851
95 | 2722960.7791 | 1217724.9416 | 2722957.5564 | 1217725.8314 | 2722953.878 | 1217726.2489
96 | 2722960.7791 | 1217724.9416 | 2722960.0355 | 1217718.4851
97 | 2722965.0876 | 1217728.4666 | 2722966.3434 | 1217734.2081 | 2722969.9828 | 1217746.8278
98 | 2722984.6721 | 1217729.8607 | 2722965.0876 | 1217728.4666
99 | 2722940.2837 | 1217745.9685 | 2722947.866 | 1217745.3911 | 2722949.3615 | 1217747.2983
100 | 2722972.1007 | 1217755.4546 | 2722971.5019 | 1217752.0952 | 2722969.9828 | 1217746.8278
101 | 2722984.6721 | 1217729.8607 | 2722988.4995 | 1217727.5933
102 | 2722984.6721 | 1217729.8607 | 2722982.5642 | 1217736.9395
103 | 2722984.6721 | 1217729.8607 | 2722996.8397 | 1217730.6489
104 | 2722988.4995 | 1217727.5933 | 2723001.8779 | 1217719.6677
105 | 2723010.4911 | 1217714.0374 | 2723008.1771 | 1217714.9676 | 2723004.3516 | 1217718.2023 | 2723001.8779 | 1217719.6677
106 | 2722972.1007 | 1217755.4546 | 2722972.4936 | 1217761.801
107 | 2722972.8977 | 1217768.3366 | 2722972.4936 | 1217761.801
108 | 2722931.1012 | 1217778.8158 | 2722924.9129 | 1217775.1297 | 2722924.2309 | 1217774.1324
109 | 2722922.5911 | 1217771.7347 | 2722924.2309 | 1217774.1324
110 | 2722943.6865 | 1217816.16 | 2722935.6386 | 1217814.6484 | 2722934.1582 | 1217818.7331
111 | 2723175.8506 | 1217902.1992 | 2723172.1868 | 1217905.4745
112 | 2723159.9607 | 1217916.4041 | 2723172.1868 | 1217905.4745
113 | 2723175.8506 | 1217902.1992 | 2723166.2456 | 1217897.199
114 | 2723159.9607 | 1217916.4041 | 2723155.8368 | 1217920.8557 | 2723153.045 | 1217925.5127 | 2723152.1351 | 1217928.0181
115 | 2723166.2456 | 1217897.199 | 2723159.4101 | 1217893.6404
116 | 2723152.1351 | 1217928.0181 | 2723151.3933 | 1217930.0581
117 | 2723159.4101 | 1217893.6404 | 2723153.0344 | 1217890.3214
118 | 2723151.3933 | 1217930.0581 | 2723149.4542 | 1217935.3907 | 2723143.509 | 1217941.9952 | 2723136.0907 | 1217948.2356 | 2723132.0949 | 1217950.8996 | 2723118.5278 | 1217958.5423
119 | 2723151.9748 | 1217889.7697 | 2723153.0344 | 1217890.3214
120 | 2723094.34 | 1217964.6192 | 2723098.1498 | 1217965.076 | 2723102.6206 | 1217964.7793 | 2723107.2457 | 1217963.6295 | 2723113.1116 | 1217961.5935 | 2723118.5278 | 1217958.5423
121 | 2723130.1953 | 1217876.421 | 2723136.6385 | 1217881.1125
122 | 2723130.1953 | 1217876.421 | 2723124.2127 | 1217872.0647
123 | 2723136.6385 | 1217881.1125 | 2723139.8825 | 1217883.4746 | 2723144.2016 | 1217885.7231
124 | 2723118.0423 | 1217867.5718 | 2723124.2127 | 1217872.0647
125 | 2723151.9748 | 1217889.7697 | 2723144.2016 | 1217885.7231
126 | 2722941.7649 | 1218035.1794 | 2722935.4249 | 1218035.8998
127 | 2722891.5942 | 1218014.6291 | 2722894.4242 | 1218022.4602 | 2722899.6764 | 1218027.339 | 2722906.6777 | 1218031.7202 | 2722913.345 | 1218034.6266 | 2722918.8818 | 1218036.0197 | 2722926.4408 | 1218036.9208 | 2722935.4249 | 1218035.8998
128 | 2722891.5942 | 1218014.6291 | 2722885.1507 | 1218032.8882 | 2722884.6122 | 1218039.8492 | 2722886.0439 | 1218044.7937 | 2722890.6538 | 1218050.2597 | 2722899.6219 | 1218054.6258 | 2722935.2185 | 1218063.378 | 2722940.0739 | 1218066.147 | 2722946.4439 | 1218073.5175 | 2722951.5203 | 1218075.8797 | 2722957.9749 | 1218076.2131 | 2722960.5621 | 1218074.9912
129 | 2722960.5621 | 1218074.9912 | 2722968.8705 | 1218071.0673 | 2722974.5921 | 1218065.3475 | 2722980.4842 | 1218062.4002 | 2722988.8835 | 1218062.0322
130 | 2722913.1838 | 1217887.2084 | 2722922.2672 | 1217878.6446 | 2722930.0479 | 1217872.8673 | 2722952.1626 | 1217859.4464
131 | 2722913.1838 | 1217887.2084 | 2722909.1497 | 1217894.6755 | 2722905.423 | 1217902.6937 | 2722902.137 | 1217905.1835 | 2722896.7245 | 1217911.0097 | 2722893.4913 | 1217916.0914 | 2722886.8089 | 1217933.4116 | 2722879.4473 | 1217957.8899 | 2722874.6379 | 1217977.9064 | 2722867.6831 | 1218008.4312 | 2722862.8673 | 1218026.9241 | 2722860.0947 | 1218036.5522
132 | 2722913.1838 | 1217887.2084 | 2722904.0416 | 1217892.3683 | 2722900.9209 | 1217893.4715 | 2722900.0599 | 1217893.6091
133 | 2722947.468 | 1217849.9866 | 2722952.1626 | 1217859.4464
134 | 2722860.0947 | 1218036.5522 | 2722850.3243 | 1218039.0527 | 2722842.3668 | 1218039.8004 | 2722835.2481 | 1218041.8441 | 2722836.8431 | 1218046.9699 | 2722833.2966 | 1218052.8903 | 2722833.3439 | 1218053.7058
135 | 2723060.5795 | 1218059.1512 | 2723048.0986 | 1218059.4381 | 2722988.8835 | 1218062.0322
136 | 2723083.3834 | 1218058.6551 | 2723086.7788 | 1218022.6122
137 | 2723083.3834 | 1218058.6551 | 2723068.0391 | 1218058.9829 | 2723060.5795 | 1218059.1512
138 | 2723060.5795 | 1218059.1512 | 2723060.995 | 1218066.232
139 | 2723099.5664 | 1217906.4707 | 2723096.5519 | 1217907.5759 | 2723092.3797 | 1217910.3252 | 2723087.5663 | 1217914.707 | 2723083.636 | 1217920.0745 | 2723080.6037 | 1217926.8171 | 2723079.4815 | 1217932.2537 | 2723079.989 | 1217937.8241 | 2723081.645 | 1217943.6628 | 2723091.0329 | 1217960.7812 | 2723094.34 | 1217964.6192
140 | 2722972.8977 | 1217768.3366 | 2722972.9761 | 1217770.6206
141 | 2722930.6224 | 1217828.489 | 2722934.1582 | 1217818.7331
142 | 2722930.6224 | 1217828.489 | 2722933.0535 | 1217830.2628
143 | 2722919.4767 | 1217818.5069 | 2722922.6086 | 1217823.4865 | 2722924.9204 | 1217825.8916 | 2722930.6224 | 1217828.489
144 | 2722933.0535 | 1217830.2628 | 2722931.7699 | 1217839.1099
145 | 2722933.0535 | 1217830.2628 | 2722935.5817 | 1217832.1164 | 2722946.2109 | 1217834.0821
146 | 2722919.4767 | 1217818.5069 | 2722910.9865 | 1217818.5652 | 2722905.0779 | 1217814.2537
147 | 2722876.9705 | 1217810.0459 | 2722894.9381 | 1217810.6725 | 2722900.2471 | 1217811.338 | 2722903.506 | 1217813.1066 | 2722905.0779 | 1217814.2537
148 | 2722883.258 | 1217861.9048 | 2722883.2145 | 1217857.3893 | 2722882.8551 | 1217853.8347 | 2722880.3297 | 1217845.5873 | 2722868.3621 | 1217823.9237 | 2722866.9902 | 1217821.2266 | 2722870.0726 | 1217819.7779 | 2722873.8144 | 1217816.1745 | 2722875.9179 | 1217812.1147 | 2722876.9705 | 1217810.0459
149 | 2722883.258 | 1217861.9048 | 2722896.5433 | 1217841.7965 | 2722898.2425 | 1217836.4245
150 | 2722899.5975 | 1217832.1408 | 2722898.2425 | 1217836.4245

## bus_geodata
| x | y | coords
0 | 2722932.0671 | 1217636.2288
1 | 2722936.1679 | 1217645.5721
2 | 2722947.1479 | 1217644.3442
3 | 2722928.3049 | 1217646.8664
4 | 2722951.9401 | 1217645.1638
5 | 2722928.7395 | 1217658.9181
6 | 2722917.6045 | 1217643.621
7 | 2722956.4281 | 1217648.5571
8 | 2722915.4421 | 1217630.8303
9 | 2722867.769 | 1217624.9053
10 | 2722883.8931 | 1217650.0846
11 | 2722864.2374 | 1217619.3905
12 | 2722889.5288 | 1217658.8854
13 | 2722873.185 | 1217622.7844
14 | 2722898.41 | 1217672.7541
15 | 2722971.0161 | 1217663.4717
16 | 2722973.5897 | 1217655.4074
17 | 2722965.0815 | 1217672.1961
18 | 2723010.296 | 1217686.6448
19 | 2723004.1232 | 1217674.1188
20 | 2723018.9119 | 1217710.6525
21 | 2723001.7417 | 1217689.8247
22 | 2723035.0557 | 1217661.0138
23 | 2723025.6972 | 1217675.8877
24 | 2722991.4209 | 1217679.205
25 | 2722761.2653 | 1217687.8328
26 | 2722747.1025 | 1217690.1095
27 | 2722910.6726 | 1217739.2302
28 | 2722919.6938 | 1217731.4795
29 | 2723093.1313 | 1217865.15
30 | 2723101.3583 | 1217855.4234
31 | 2723110.02 | 1217878.1667
32 | 2722971.5992 | 1217791.8726
33 | 2722959.8325 | 1217785.8585
34 | 2722973.4596 | 1217784.7057
35 | 2723105.1176 | 1217858.1608
36 | 2723117.0189 | 1217846.4289
37 | 2723118.7953 | 1217837.2695
38 | 2723139.388 | 1217861.8586
39 | 2723015.0606 | 1217826.5077
40 | 2723059.0304 | 1217906.7873
41 | 2722970.972 | 1217848.3481
42 | 2723249.5557 | 1217804.6359
43 | 2723211.6619 | 1217852.9011
44 | 2723204.9751 | 1217889.1022
45 | 2722899.8491 | 1217675.0014
46 | 2722963.1616 | 1217675.0186
47 | 2723011.3182 | 1217713.705
48 | 2723001.6553 | 1217689.8568
49 | 2722928.4079 | 1217726.108
50 | 2722928.2112 | 1217740.4472
51 | 2722937.5899 | 1217741.098
52 | 2723121.6978 | 1217886.5855
53 | 2722982.5343 | 1217766.8931
54 | 2722981.1142 | 1217767.1058
55 | 2722952.4699 | 1217798.1825
56 | 2722940.7086 | 1217781.3458
57 | 2722973.2424 | 1217778.3782
58 | 2723111.6849 | 1217862.9427
59 | 2723144.9857 | 1217854.4352
60 | 2723166.3891 | 1217877.0494
61 | 2723091.2193 | 1217967.1901
62 | 2722959.6646 | 1217855.0199
63 | 2722960.3545 | 1217836.6977
64 | 2723010.7339 | 1217732.1062
65 | 2723006.364 | 1217731.2658
66 | 2723217.9303 | 1217935.2616
67 | 2723215.3877 | 1217935.209
68 | 2723212.4098 | 1217908.8602
69 | 2723186.3711 | 1217888.0501
70 | 2722917.7795 | 1217706.8738
71 | 2722885.7425 | 1217704.199
72 | 2722919.7224 | 1217710.4789
73 | 2722942.2688 | 1217697.5675
74 | 2722944.8616 | 1217697.4939
75 | 2722926.1969 | 1217722.4929
76 | 2722952.1402 | 1217680.7067
77 | 2722956.505 | 1217694.0071
78 | 2722949.8906 | 1217697.351
79 | 2722951.1211 | 1217707.6289
80 | 2722964.1513 | 1217722.601
81 | 2722964.3682 | 1217723.9594
82 | 2722957.4341 | 1217708.2561
83 | 2722944.9476 | 1217710.9534
84 | 2722953.878 | 1217726.2489
85 | 2722960.7791 | 1217724.9416
86 | 2722960.0355 | 1217718.4851
87 | 2722930.7952 | 1217730.0048
88 | 2722965.0876 | 1217728.4666
89 | 2722940.2837 | 1217745.9685
90 | 2722969.9828 | 1217746.8278
91 | 2722984.6721 | 1217729.8607
92 | 2722949.3615 | 1217747.2983
93 | 2722996.8397 | 1217730.6489
94 | 2722988.4995 | 1217727.5933
95 | 2722982.5642 | 1217736.9395
96 | 2723001.8779 | 1217719.6677
97 | 2722972.1007 | 1217755.4546
98 | 2723010.4911 | 1217714.0374
99 | 2722972.4936 | 1217761.801
100 | 2722931.1012 | 1217778.8158
101 | 2722924.2309 | 1217774.1324
102 | 2722922.5911 | 1217771.7347
103 | 2722943.6865 | 1217816.16
104 | 2723172.1868 | 1217905.4745
105 | 2723175.8506 | 1217902.1992
106 | 2723159.9607 | 1217916.4041
107 | 2723166.2456 | 1217897.199
108 | 2723152.1351 | 1217928.0181
109 | 2723159.41 | 1217893.6404
110 | 2723170.428 | 1217879.2729
111 | 2723151.3933 | 1217930.0581
112 | 2723153.0344 | 1217890.3213
113 | 2723118.5278 | 1217958.5423
114 | 2723130.1953 | 1217876.421
115 | 2723136.6385 | 1217881.1125
116 | 2723124.2127 | 1217872.0647
117 | 2723144.2016 | 1217885.7231
118 | 2723118.0423 | 1217867.5718
119 | 2723151.9748 | 1217889.7697
120 | 2722941.7649 | 1218035.1794
121 | 2722935.4249 | 1218035.8998
122 | 2722891.5942 | 1218014.6291
123 | 2722960.5621 | 1218074.9912
124 | 2722913.1838 | 1217887.2084
125 | 2722952.1626 | 1217859.4464
126 | 2722860.0947 | 1218036.5522
127 | 2722900.0599 | 1217893.6091
128 | 2722833.3439 | 1218053.7058
129 | 2722988.8835 | 1218062.0322
130 | 2722996.4382 | 1217691.7961
131 | 2723086.7788 | 1218022.6122
132 | 2723083.3834 | 1218058.6551
133 | 2723060.5795 | 1218059.1512
134 | 2723094.34 | 1217964.6192
135 | 2723060.995 | 1218066.232
136 | 2723099.5664 | 1217906.4707
137 | 2722972.8977 | 1217768.3366
138 | 2722972.9761 | 1217770.6206
139 | 2722934.1582 | 1217818.7331
140 | 2722930.6224 | 1217828.489
141 | 2722933.0535 | 1217830.2628
142 | 2722919.4767 | 1217818.5069
143 | 2722931.7699 | 1217839.1099
144 | 2722946.2109 | 1217834.0821
145 | 2722905.0779 | 1217814.2537
146 | 2722959.9618 | 1217831.3591
147 | 2722876.9705 | 1217810.0459
148 | 2722947.468 | 1217849.9866
149 | 2722883.258 | 1217861.9048
150 | 2722898.2425 | 1217836.4245
151 | 2722899.5975 | 1217832.1408
152 | 2723020.8695 | 1217818.0433

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97156 | -0.54843 | 0.0071568 | 0.0017937
1 | 0.97163 | -0.54708 | 0 | 0
2 | 0.97196 | -0.54063 | 0.0039588 | 0.00099218
3 | 0.97145 | -0.55064 | 0 | 0
4 | 0.97212 | -0.53745 | 0.00684 | 0.0017143
5 | 0.97128 | -0.55414 | 0.015531 | 0.0038924
6 | 0.97136 | -0.5525 | 0 | 0
7 | 0.97234 | -0.53306 | 0.005811 | 0.0014564
8 | 0.97125 | -0.55465 | 0.0087315 | 0.0021883
9 | 0.97329 | -0.51449 | 0.0048623 | 0.0012186
10 | 0.97355 | -0.50942 | 0.0037676 | 0.00094425
11 | 0.97326 | -0.51501 | 0 | 0
12 | 0.97367 | -0.50693 | 0.0041768 | 0.0010468
13 | 0.97322 | -0.51578 | 0.0043488 | 0.0010899
14 | 0.97394 | -0.50173 | 0.0064672 | 0.0016208
15 | 0.97355 | -0.50914 | 0 | 0
16 | 0.97317 | -0.51662 | 0 | 0
17 | 0.97403 | -0.49983 | 0.0088376 | 0.0022149
18 | 0.97534 | -0.47417 | 0 | 0
19 | 0.9751 | -0.47901 | 0 | 0
20 | 0.97618 | -0.45767 | 0 | 0
21 | 0.9752 | -0.47699 | 0.0060122 | 0.0015068
22 | 0.97467 | -0.48733 | 0 | 0
23 | 0.9745 | -0.49071 | 0.0093579 | 0.0023453
24 | 0.97498 | -0.48129 | 0.0091089 | 0.0022829
25 | 0.97475 | -0.48581 | 0 | 0
26 | 0.9747 | -0.48662 | 0.0031092 | 0.00077924
27 | 0.97534 | -0.47403 | 0 | 0
28 | 0.97538 | -0.47334 | 0.0051546 | 0.0012919
29 | 0.9742 | -0.49653 | 0 | 0
30 | 0.97435 | -0.49351 | 0 | 0
31 | 0.97394 | -0.5016 | 0.0050866 | 0.0012748
32 | 0.98418 | -0.30148 | 0 | 0
33 | 0.98526 | -0.28076 | 0 | 0
34 | 0.98358 | -0.31325 | 0.0058724 | 0.0014718
35 | 0.97441 | -0.49241 | 0.0086603 | 0.0021705
36 | 0.97587 | -0.46364 | 0 | 0
37 | 0.97575 | -0.46595 | 0.012562 | 0.0031483
38 | 0.97618 | -0.45741 | 0 | 0
39 | 1 | 0 | -0.60117 | -0.155
40 | 0.99243 | -0.14293 | 0.0070423 | 0.001765
41 | 0.995 | -0.094365 | 0 | 0
42 | 0.97211 | -0.53733 | 0 | 0
43 | 0.97014 | -0.57627 | 0.029761 | 0.0074589
44 | 0.97633 | -0.45437 | 0 | 0
45 | 0.97399 | -0.50057 | 0 | 0
46 | 0.97421 | -0.49626 | 0 | 0
47 | 0.97645 | -0.45239 | 0.006836 | 0.0017133
48 | 0.9752 | -0.47701 | 0.00645 | 0.0016165
49 | 0.97546 | -0.47179 | 0 | 0
50 | 0.97525 | -0.47594 | 0.0050383 | 0.0012627
51 | 0.97529 | -0.47507 | 0 | 0
52 | 0.97383 | -0.50368 | 0.0078416 | 0.0019653
53 | 0.98221 | -0.33973 | 0.0064138 | 0.0016075
54 | 0.98222 | -0.33956 | 0.0037626 | 0.00094298
55 | 0.98654 | -0.25606 | 0.0043919 | 0.0011007
56 | 0.98476 | -0.29046 | 0.0043295 | 0.0010851
57 | 0.98308 | -0.3229 | 0.0025444 | 0.0006377
58 | 0.97457 | -0.48919 | 0.008768 | 0.0021975
59 | 0.97612 | -0.45853 | 0.0066125 | 0.0016572
60 | 0.97673 | -0.44655 | 0.012093 | 0.0030307
61 | 0.98696 | -0.24778 | 0 | 0
62 | 0.99488 | -0.096672 | 0.0020411 | 0.00051154
63 | 0.99343 | -0.12405 | 0 | 0
64 | 0.97759 | -0.43003 | 0.0062264 | 0.0015605
65 | 0.97761 | -0.42952 | 0.0067201 | 0.0016842
66 | 0.97563 | -0.46826 | 0 | 0
67 | 0.97562 | -0.46845 | 0.0039704 | 0.00099507
68 | 0.97571 | -0.46653 | 0.031465 | 0.0078859
69 | 0.9775 | -0.43143 | 0 | 0
70 | 0.97498 | -0.48113 | 0 | 0
71 | 0.9738 | -0.50439 | 0.005357 | 0.0013426
72 | 0.97509 | -0.47895 | 0.0053681 | 0.0013454
73 | 0.97622 | -0.45682 | 0.0027508 | 0.00068942
74 | 0.97622 | -0.45669 | 0.0086668 | 0.0021721
75 | 0.97553 | -0.47036 | 0 | 0
76 | 0.97488 | -0.48303 | 0.012793 | 0.0032062
77 | 0.97579 | -0.46516 | 0 | 0
78 | 0.97628 | -0.45563 | 0 | 0
79 | 0.97707 | -0.44005 | 0 | 0
80 | 0.97909 | -0.4005 | 0.0050307 | 0.0012608
81 | 0.9791 | -0.40038 | 0 | 0
82 | 0.97789 | -0.42397 | 0.0040896 | 0.001025
83 | 0.97667 | -0.44795 | 0.0042691 | 0.0010699
84 | 0.97889 | -0.40442 | 0.0049631 | 0.0012439
85 | 0.97892 | -0.40379 | 0 | 0
86 | 0.97863 | -0.40957 | 0.0044406 | 0.0011129
87 | 0.97541 | -0.47264 | 0 | 0
88 | 0.97932 | -0.39604 | 0 | 0
89 | 0.97526 | -0.47559 | 0 | 0
90 | 0.9807 | -0.36917 | 0.0031763 | 0.00079606
91 | 0.97792 | -0.42346 | 0 | 0
92 | 0.97521 | -0.47654 | 0.0051454 | 0.0012896
93 | 0.97773 | -0.42726 | 0.0041832 | 0.0010484
94 | 0.97769 | -0.42797 | 0.0037593 | 0.00094217
95 | 0.97789 | -0.42401 | 0.0041056 | 0.001029
96 | 0.97694 | -0.44271 | 0.0045567 | 0.001142
97 | 0.98135 | -0.35646 | 0 | 0
98 | 0.97648 | -0.4517 | 0.005224 | 0.0013093
99 | 0.98182 | -0.34738 | 0 | 0
100 | 0.98455 | -0.2946 | 0.0053784 | 0.001348
101 | 0.98441 | -0.29729 | 0.0052384 | 0.0013129
102 | 0.98438 | -0.29794 | 0.012534 | 0.0031414
103 | 0.98835 | -0.22109 | 0 | 0
104 | 0.97966 | -0.3893 | 0.0080431 | 0.0020158
105 | 0.97919 | -0.39845 | 0 | 0
106 | 0.98074 | -0.36818 | 0 | 0
107 | 0.97816 | -0.41856 | 0.008672 | 0.0021734
108 | 0.98167 | -0.35 | 0 | 0
109 | 0.97749 | -0.43168 | 0.0079787 | 0.0019997
110 | 0.97687 | -0.44391 | 0.0063199 | 0.0015839
111 | 0.98182 | -0.34721 | 0.0083059 | 0.0020816
112 | 0.97692 | -0.44289 | 0.0063059 | 0.0015804
113 | 0.98488 | -0.28789 | 0.0052799 | 0.0013233
114 | 0.97538 | -0.47327 | 0.0070763 | 0.0017735
115 | 0.97577 | -0.46561 | 0.0085258 | 0.0021368
116 | 0.97506 | -0.47942 | 0.0069221 | 0.0017348
117 | 0.97627 | -0.45569 | 0.0081596 | 0.002045
118 | 0.97479 | -0.48481 | 0.0081105 | 0.0020327
119 | 0.97683 | -0.44462 | 0.0099702 | 0.0024988
120 | 0.98171 | -0.35024 | 0.0049614 | 0.0012434
121 | 0.98173 | -0.34966 | 0.002507 | 0.0006283
122 | 0.9821 | -0.34245 | 0 | 0
123 | 0.9829 | -0.32687 | 0.0059416 | 0.0014891
124 | 0.99457 | -0.10263 | 0 | 0
125 | 0.99481 | -0.097889 | 0 | 0
126 | 0.99396 | -0.11452 | 0 | 0
127 | 0.99455 | -0.103 | 0.0014126 | 0.00035404
128 | 0.99381 | -0.11738 | 0.0041957 | 0.0010516
129 | 0.9833 | -0.31906 | 0.002276 | 0.00057041
130 | 0.97517 | -0.47745 | 0.0043948 | 0.0011014
131 | 0.98556 | -0.27487 | 0.0045806 | 0.001148
132 | 0.98481 | -0.28955 | 0 | 0
133 | 0.98434 | -0.29878 | 0 | 0
134 | 0.98667 | -0.25334 | 0 | 0
135 | 0.98429 | -0.29966 | 0.0068812 | 0.0017246
136 | 0.98639 | -0.25878 | 0.0043027 | 0.0010784
137 | 0.9823 | -0.33803 | 0 | 0
138 | 0.98247 | -0.33464 | 0.0042743 | 0.0010713
139 | 0.98949 | -0.19938 | 0.0033915 | 0.00084999
140 | 0.99043 | -0.18123 | 0 | 0
141 | 0.99072 | -0.1758 | 0 | 0
142 | 0.99029 | -0.18405 | 0 | 0
143 | 0.99069 | -0.17628 | 0.00297 | 0.00074435
144 | 0.99205 | -0.1504 | 0.0025621 | 0.00064212
145 | 0.99014 | -0.18694 | 0.0027105 | 0.00067932
146 | 0.99343 | -0.1242 | 0.0015471 | 0.00038774
147 | 0.98994 | -0.19083 | 0 | 0
148 | 0.99479 | -0.098321 | 0.00232 | 0.00058144
149 | 0.98952 | -0.1989 | 0 | 0
150 | 0.98932 | -0.2029 | 0.005 | 0.0012531
151 | 0.98931 | -0.2031 | 0.0025533 | 0.00063991
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0071568 | -0.0017937 | 0.0071572 | 0.0017938 | 4.5971e-07 | 1.6785e-07 | 0.010961 | 0.010961 | 0.010961 | 0.97156 | -0.54843 | 0.97163 | -0.54708 | 3.0113
1 | -0.031428 | -0.0078794 | 0.031438 | 0.0078854 | 9.6683e-06 | 6.0498e-06 | 0.048132 | 0.048132 | 0.048132 | 0.97163 | -0.54708 | 0.97196 | -0.54063 | 13.223
2 | 0.024271 | 0.0060856 | -0.024267 | -0.006083 | 4.117e-06 | 2.5365e-06 | 0.037171 | 0.037171 | 0.037171 | 0.97163 | -0.54708 | 0.97145 | -0.55064 | 10.2118
3 | -0.035397 | -0.0088776 | 0.035402 | 0.008881 | 5.3544e-06 | 3.3665e-06 | 0.054193 | 0.054193 | 0.054193 | 0.97196 | -0.54063 | 0.97212 | -0.53745 | 14.8881
4 | 0.015534 | 0.003894 | -0.015531 | -0.0038924 | 2.5908e-06 | 1.507e-06 | 0.023794 | 0.023794 | 0.023794 | 0.97145 | -0.55064 | 0.97128 | -0.55414 | 6.5368
5 | 0.0087331 | 0.0021891 | -0.0087324 | -0.0021887 | 7.7513e-07 | 3.5308e-07 | 0.013377 | 0.013377 | 0.013377 | 0.97145 | -0.55064 | 0.97136 | -0.5525 | 3.675
6 | -0.042242 | -0.010595 | 0.042251 | 0.010601 | 8.8567e-06 | 5.5983e-06 | 0.064662 | 0.064662 | 0.064662 | 0.97212 | -0.53745 | 0.97234 | -0.53306 | 17.7644
7 | 0.0087324 | 0.0021887 | -0.0087315 | -0.0021883 | 8.9422e-07 | 4.0737e-07 | 0.013377 | 0.013377 | 0.013377 | 0.97136 | -0.5525 | 0.97125 | -0.55465 | 3.675
8 | -0.048062 | -0.012057 | 0.048099 | 0.012081 | 3.7692e-05 | 2.3892e-05 | 0.073555 | 0.073555 | 0.073555 | 0.97234 | -0.53306 | 0.97317 | -0.51662 | 20.2075
9 | -0.0092114 | -0.0023085 | 0.0092136 | 0.0023096 | 2.2237e-06 | 1.0515e-06 | 0.014083 | 0.014083 | 0.014083 | 0.97329 | -0.51449 | 0.97355 | -0.50942 | 3.8689
10 | 0.0043491 | 0.0010899 | -0.004349 | -0.0010899 | 1.0857e-07 | -1.1899e-08 | 0.0066491 | 0.0066491 | 0.0066491 | 0.97329 | -0.51449 | 0.97326 | -0.51501 | 1.8267
11 | -0.012981 | -0.0032538 | 0.012983 | 0.0032547 | 1.5428e-06 | 8.5744e-07 | 0.019841 | 0.019841 | 0.019841 | 0.97355 | -0.50942 | 0.97367 | -0.50693 | 5.4509
12 | 0.004349 | 0.0010899 | -0.0043488 | -0.0010899 | 1.5904e-07 | -1.742e-08 | 0.0066491 | 0.0066492 | 0.0066492 | 0.97326 | -0.51501 | 0.97322 | -0.51578 | 1.8267
13 | -0.01716 | -0.0043015 | 0.017164 | 0.004304 | 4.2472e-06 | 2.5133e-06 | 0.026225 | 0.026224 | 0.026225 | 0.97367 | -0.50693 | 0.97394 | -0.50173 | 7.2045
14 | -0.023631 | -0.0059248 | 0.023632 | 0.0059256 | 1.3045e-06 | 8.017e-07 | 0.036105 | 0.036105 | 0.036105 | 0.97394 | -0.50173 | 0.97399 | -0.50057 | 9.919
15 | 0.048117 | 0.012092 | -0.048099 | -0.012081 | 1.7172e-05 | 1.0885e-05 | 0.073555 | 0.073555 | 0.073555 | 0.97355 | -0.50914 | 0.97317 | -0.51662 | 20.2074
16 | -0.048117 | -0.012092 | 0.048138 | 0.012106 | 2.1408e-05 | 1.357e-05 | 0.073555 | 0.073555 | 0.073555 | 0.97355 | -0.50914 | 0.97403 | -0.49983 | 20.2074
17 | -0.056976 | -0.01432 | 0.056985 | 0.014327 | 9.7015e-06 | 6.1665e-06 | 0.087056 | 0.087056 | 0.087056 | 0.97403 | -0.49983 | 0.97421 | -0.49626 | 23.9165
18 | 0.018477 | 0.0046337 | -0.018473 | -0.0046312 | 4.2619e-06 | 2.5492e-06 | 0.028191 | 0.028191 | 0.028191 | 0.97534 | -0.47417 | 0.9751 | -0.47901 | 7.7447
19 | -0.035337 | -0.0088598 | 0.035364 | 0.0088773 | 2.7802e-05 | 1.7474e-05 | 0.053912 | 0.053912 | 0.053912 | 0.97534 | -0.47417 | 0.97618 | -0.45767 | 14.811
20 | 0.016859 | 0.0042261 | -0.016857 | -0.0042247 | 2.2642e-06 | 1.3352e-06 | 0.025721 | 0.025721 | 0.025721 | 0.97534 | -0.47417 | 0.9752 | -0.47699 | 7.0663
21 | 0.0091099 | 0.0022834 | -0.0091089 | -0.0022829 | 9.8921e-07 | 4.6286e-07 | 0.013902 | 0.013902 | 0.013902 | 0.9751 | -0.47901 | 0.97498 | -0.48129 | 3.8192
22 | 0.0093631 | 0.0023478 | -0.0093594 | -0.002346 | 3.7114e-06 | 1.7709e-06 | 0.014289 | 0.014289 | 0.014289 | 0.9751 | -0.47901 | 0.97467 | -0.48733 | 3.9255
23 | -0.035364 | -0.0088773 | 0.035373 | 0.0088829 | 8.9203e-06 | 5.6067e-06 | 0.053912 | 0.053912 | 0.053912 | 0.97618 | -0.45767 | 0.97645 | -0.45239 | 14.811
24 | 0.010845 | 0.0027179 | -0.010845 | -0.0027179 | 9.4648e-09 | 4.9075e-09 | 0.016548 | 0.016548 | 0.016548 | 0.9752 | -0.47699 | 0.9752 | -0.47701 | 4.5461
25 | 0.0093594 | 0.002346 | -0.0093579 | -0.0023453 | 1.5088e-06 | 7.2008e-07 | 0.014289 | 0.014289 | 0.014289 | 0.97467 | -0.48733 | 0.9745 | -0.49071 | 3.9256
26 | 0.0031093 | 0.00077914 | -0.0031092 | -0.00077924 | 1.2085e-07 | -1.0095e-07 | 0.0047466 | 0.0047466 | 0.0047466 | 0.97475 | -0.48581 | 0.9747 | -0.48662 | 1.304
27 | -0.0031093 | -0.00077914 | 0.0031111 | 0.00077768 | 1.7432e-06 | -1.4583e-06 | 0.0047466 | 0.0047456 | 0.0047466 | 0.97475 | -0.48581 | 0.97534 | -0.47403 | 1.304
28 | -0.0031111 | -0.00077768 | 0.0031112 | 0.0007776 | 1.0175e-07 | -8.5244e-08 | 0.0047456 | 0.0047456 | 0.0047456 | 0.97534 | -0.47403 | 0.97538 | -0.47334 | 1.3037
29 | -0.0082657 | -0.0020695 | 0.0082664 | 0.0020697 | 6.1038e-07 | 2.6286e-07 | 0.012609 | 0.012609 | 0.012609 | 0.97538 | -0.47334 | 0.97546 | -0.47179 | 3.4641
30 | -0.012932 | -0.0032422 | 0.012934 | 0.0032432 | 1.8621e-06 | 1.0333e-06 | 0.019753 | 0.019753 | 0.019753 | 0.9742 | -0.49653 | 0.97435 | -0.49351 | 5.4268
31 | 0.012932 | 0.0032422 | -0.012929 | -0.0032405 | 3.1227e-06 | 1.7329e-06 | 0.019753 | 0.019753 | 0.019753 | 0.9742 | -0.49653 | 0.97394 | -0.5016 | 5.4268
32 | -0.012934 | -0.0032432 | 0.012935 | 0.0032436 | 6.8045e-07 | 3.7757e-07 | 0.019753 | 0.019753 | 0.019753 | 0.97435 | -0.49351 | 0.97441 | -0.49241 | 5.4267
33 | 0.0078424 | 0.0019656 | -0.0078416 | -0.0019653 | 7.7577e-07 | 3.172e-07 | 0.011982 | 0.011982 | 0.011982 | 0.97394 | -0.5016 | 0.97383 | -0.50368 | 3.2918
34 | -0.26173 | -0.066392 | 0.26199 | 0.066559 | 0.00026106 | 0.00016657 | 0.396 | 0.396 | 0.396 | 0.98418 | -0.30148 | 0.98526 | -0.28076 | 36.2638
35 | 0.26173 | 0.066392 | -0.26158 | -0.066298 | 0.000148 | 9.4433e-05 | 0.396 | 0.396 | 0.396 | 0.98418 | -0.30148 | 0.98358 | -0.31325 | 36.2638
36 | -0.28949 | -0.073458 | 0.28983 | 0.073678 | 0.00034436 | 0.00021984 | 0.43754 | 0.43754 | 0.43754 | 0.98526 | -0.28076 | 0.98654 | -0.25606 | 40.0674
37 | 0.027501 | 0.0068995 | -0.027488 | -0.0068916 | 1.2712e-05 | 7.8858e-06 | 0.041536 | 0.041536 | 0.041536 | 0.98526 | -0.28076 | 0.98476 | -0.29046 | 11.4111
38 | 0.25571 | 0.064826 | -0.25559 | -0.06475 | 0.0001186 | 7.5662e-05 | 0.38712 | 0.38712 | 0.38712 | 0.98358 | -0.31325 | 0.98308 | -0.3229 | 35.4502
39 | -0.021595 | -0.0054141 | 0.021598 | 0.0054161 | 3.3132e-06 | 2.0192e-06 | 0.032978 | 0.032978 | 0.032978 | 0.97441 | -0.49241 | 0.97457 | -0.48919 | 9.06
40 | 0.012563 | 0.003149 | -0.012562 | -0.0031483 | 1.3796e-06 | 7.5771e-07 | 0.019157 | 0.019157 | 0.019157 | 0.97587 | -0.46364 | 0.97575 | -0.46595 | 5.2628
41 | -0.012563 | -0.003149 | 0.012567 | 0.0031511 | 3.7322e-06 | 2.0497e-06 | 0.019157 | 0.019156 | 0.019157 | 0.97587 | -0.46364 | 0.97618 | -0.45741 | 5.2628
42 | 0.0066128 | 0.0016574 | -0.0066125 | -0.0016572 | 3.5394e-07 | 1.104e-07 | 0.01008 | 0.01008 | 0.01008 | 0.97618 | -0.45741 | 0.97612 | -0.45853 | 2.7693
43 | -0.01918 | -0.0048084 | 0.01919 | 0.0048144 | 9.9331e-06 | 5.9695e-06 | 0.029237 | 0.029236 | 0.029237 | 0.97618 | -0.45741 | 0.97673 | -0.44655 | 8.032
44 | 0.27068 | 0.07003 | -0.2688 | -0.068833 | 0.0018752 | 0.0011965 | 0.40355 | 0.40355 | 0.40355 | 1 | 0 | 0.99243 | -0.14293 | 36.9554
45 | 0.32884 | 0.084966 | -0.32734 | -0.084004 | 0.0015064 | 0.00096212 | 0.49023 | 0.49023 | 0.49023 | 1 | 0 | 0.995 | -0.094365 | 44.8929
46 | 0.26176 | 0.067068 | -0.26044 | -0.066224 | 0.0013228 | 0.00084397 | 0.39299 | 0.393 | 0.393 | 0.99243 | -0.14293 | 0.98696 | -0.24778 | 35.9886
47 | 0.0099753 | 0.0024985 | -0.0099742 | -0.002498 | 1.0956e-06 | 5.3068e-07 | 0.014917 | 0.014918 | 0.014918 | 0.995 | -0.094365 | 0.99488 | -0.096672 | 4.0982
48 | 0.31736 | 0.081505 | -0.3169 | -0.081214 | 0.0004567 | 0.00029166 | 0.47531 | 0.47531 | 0.47531 | 0.995 | -0.094365 | 0.99343 | -0.12405 | 43.5269
49 | 0.029817 | 0.0074934 | -0.029761 | -0.0074589 | 5.5316e-05 | 3.4526e-05 | 0.045648 | 0.045648 | 0.045648 | 0.97211 | -0.53733 | 0.97014 | -0.57627 | 12.5407
50 | -0.029817 | -0.0074934 | 0.029935 | 0.0075674 | 0.00011859 | 7.4008e-05 | 0.045648 | 0.045647 | 0.045648 | 0.97211 | -0.53733 | 0.97633 | -0.45437 | 12.5406
51 | 0.031484 | 0.0078973 | -0.031465 | -0.0078859 | 1.8224e-05 | 1.14e-05 | 0.047986 | 0.047986 | 0.047986 | 0.97633 | -0.45437 | 0.97571 | -0.46653 | 13.183
52 | -0.065392 | -0.016459 | 0.065464 | 0.016505 | 7.1813e-05 | 4.5719e-05 | 0.099688 | 0.099688 | 0.099688 | 0.97633 | -0.45437 | 0.9775 | -0.43143 | 27.3869
53 | 0.0039731 | 0.00099436 | -0.0039704 | -0.00099506 | 2.6264e-06 | -7.0615e-07 | 0.0060548 | 0.0060556 | 0.0060556 | 0.97633 | -0.45437 | 0.97563 | -0.46826 | 1.6636
54 | -0.02899 | -0.0072684 | 0.029017 | 0.0072851 | 2.6893e-05 | 1.6756e-05 | 0.044291 | 0.044291 | 0.044291 | 0.97399 | -0.50057 | 0.97498 | -0.48113 | 12.1678
55 | 0.005358 | 0.0013427 | -0.005357 | -0.0013426 | 9.7448e-07 | 1.4109e-07 | 0.0081856 | 0.0081858 | 0.0081858 | 0.97399 | -0.50057 | 0.9738 | -0.50439 | 2.2488
56 | -0.056985 | -0.014327 | 0.057021 | 0.01435 | 3.6025e-05 | 2.2898e-05 | 0.087056 | 0.087056 | 0.087056 | 0.97421 | -0.49626 | 0.97488 | -0.48303 | 23.9165
57 | -0.042209 | -0.010596 | 0.042211 | 0.010597 | 1.3834e-06 | 8.7421e-07 | 0.064329 | 0.064329 | 0.064329 | 0.97645 | -0.45239 | 0.97648 | -0.4517 | 17.6729
58 | 0.0043949 | 0.0011014 | -0.0043948 | -0.0011014 | 9.3862e-08 | -9.3705e-09 | 0.0067059 | 0.006706 | 0.006706 | 0.9752 | -0.47701 | 0.97517 | -0.47745 | 1.8423
59 | -0.018452 | -0.0046229 | 0.018454 | 0.0046236 | 1.2582e-06 | 7.5241e-07 | 0.028148 | 0.028147 | 0.028148 | 0.97546 | -0.47179 | 0.97553 | -0.47036 | 7.7328
60 | 0.010186 | 0.0025531 | -0.010185 | -0.0025529 | 4.1349e-07 | 2.0763e-07 | 0.015538 | 0.015538 | 0.015538 | 0.97546 | -0.47179 | 0.97541 | -0.47264 | 4.2688
61 | -0.0050383 | -0.0012627 | 0.0050385 | 0.0012627 | 2.0834e-07 | 1.6025e-08 | 0.0076874 | 0.0076874 | 0.0076874 | 0.97525 | -0.47594 | 0.97529 | -0.47507 | 2.1119
62 | 0.0051458 | 0.0012896 | -0.0051457 | -0.0012896 | 1.2856e-07 | 1.2874e-08 | 0.007851 | 0.007851 | 0.007851 | 0.97529 | -0.47507 | 0.97526 | -0.47559 | 2.1569
63 | -0.010184 | -0.0025523 | 0.010185 | 0.0025529 | 1.1769e-06 | 5.91e-07 | 0.015538 | 0.015538 | 0.015538 | 0.97529 | -0.47507 | 0.97541 | -0.47264 | 4.2688
64 | -0.0064138 | -0.0016075 | 0.0064139 | 0.0016075 | 5.0839e-08 | 1.4363e-08 | 0.0097167 | 0.0097167 | 0.0097167 | 0.98221 | -0.33973 | 0.98222 | -0.33956 | 2.6694
65 | -0.010176 | -0.0025505 | 0.010177 | 0.0025508 | 7.405e-07 | 3.6875e-07 | 0.015417 | 0.015417 | 0.015417 | 0.98222 | -0.33956 | 0.9823 | -0.33803 | 4.2354
66 | -0.29423 | -0.074779 | 0.29472 | 0.075096 | 0.00049645 | 0.00031695 | 0.44416 | 0.44416 | 0.44416 | 0.98654 | -0.25606 | 0.98835 | -0.22109 | 40.674
67 | 0.023158 | 0.0058066 | -0.023154 | -0.0058038 | 4.5642e-06 | 2.7946e-06 | 0.034994 | 0.034994 | 0.034994 | 0.98476 | -0.29046 | 0.98455 | -0.2946 | 9.6138
68 | 0.25304 | 0.064113 | -0.2529 | -0.064022 | 0.00014253 | 9.0921e-05 | 0.38327 | 0.38327 | 0.38327 | 0.98308 | -0.3229 | 0.98247 | -0.33464 | 35.0975
69 | -0.030366 | -0.0076136 | 0.030373 | 0.0076175 | 6.3399e-06 | 3.9595e-06 | 0.046366 | 0.046366 | 0.046366 | 0.97457 | -0.48919 | 0.97479 | -0.48481 | 12.7379
70 | -0.031282 | -0.0078451 | 0.031286 | 0.0078476 | 3.9271e-06 | 2.4556e-06 | 0.047659 | 0.047659 | 0.047659 | 0.97673 | -0.44655 | 0.97687 | -0.44391 | 13.0932
71 | 0.2332 | 0.059368 | -0.23314 | -0.059328 | 6.2496e-05 | 3.9843e-05 | 0.35192 | 0.35192 | 0.35192 | 0.98696 | -0.24778 | 0.98667 | -0.25334 | 32.2271
72 | 0.027237 | 0.0068562 | -0.027202 | -0.0068344 | 3.5217e-05 | 2.1828e-05 | 0.041076 | 0.041076 | 0.041076 | 0.98696 | -0.24778 | 0.98556 | -0.27487 | 11.2847
73 | 0.0079331 | 0.0019864 | -0.0079326 | -0.0019862 | 4.5983e-07 | 1.8119e-07 | 0.011865 | 0.011865 | 0.011865 | 0.99488 | -0.096672 | 0.99481 | -0.097889 | 3.2596
74 | 0.31536 | 0.080826 | -0.31495 | -0.080569 | 0.00040224 | 0.00025688 | 0.473 | 0.473 | 0.473 | 0.99343 | -0.12405 | 0.99205 | -0.1504 | 43.3147
75 | 0.0015471 | 0.00038768 | -0.0015471 | -0.00038774 | 1.078e-08 | -6.241e-08 | 0.0023173 | 0.0023174 | 0.0023174 | 0.99343 | -0.12405 | 0.99343 | -0.1242 | 0.63664
76 | -0.0062264 | -0.0015605 | 0.0062266 | 0.0015605 | 1.5178e-07 | 4.064e-08 | 0.0094774 | 0.0094774 | 0.0094774 | 0.97759 | -0.43003 | 0.97761 | -0.42952 | 2.6037
77 | -0.012947 | -0.0032447 | 0.012948 | 0.0032455 | 1.3899e-06 | 7.6982e-07 | 0.019706 | 0.019706 | 0.019706 | 0.97761 | -0.42952 | 0.97773 | -0.42726 | 5.4137
78 | 0.0039704 | 0.00099506 | -0.0039704 | -0.00099507 | 3.4874e-08 | -9.3488e-09 | 0.0060556 | 0.0060557 | 0.0060557 | 0.97563 | -0.46826 | 0.97562 | -0.46845 | 1.6636
79 | 0.037629 | 0.0094456 | -0.037606 | -0.0094315 | 2.2397e-05 | 1.4106e-05 | 0.057286 | 0.057286 | 0.057286 | 0.9775 | -0.43143 | 0.97687 | -0.44391 | 15.7379
80 | -0.10309 | -0.02595 | 0.10325 | 0.026054 | 0.00016279 | 0.00010396 | 0.15697 | 0.15697 | 0.15697 | 0.9775 | -0.43143 | 0.97919 | -0.39845 | 43.1247
81 | -0.029017 | -0.0072851 | 0.02902 | 0.007287 | 3.0126e-06 | 1.877e-06 | 0.044291 | 0.044291 | 0.044291 | 0.97498 | -0.48113 | 0.97509 | -0.47895 | 12.1678
82 | -0.034388 | -0.0086324 | 0.034402 | 0.0086412 | 1.4097e-05 | 8.8515e-06 | 0.052483 | 0.052482 | 0.052483 | 0.97509 | -0.47895 | 0.97553 | -0.47036 | 14.4183
83 | -0.0027508 | -0.00068942 | 0.0027508 | 0.0006894 | 1.7101e-08 | -2.1485e-08 | 0.004193 | 0.004193 | 0.004193 | 0.97622 | -0.45682 | 0.97622 | -0.45669 | 1.1519
84 | -0.011418 | -0.0028615 | 0.011418 | 0.0028618 | 5.7143e-07 | 3.0281e-07 | 0.017404 | 0.017404 | 0.017404 | 0.97622 | -0.45669 | 0.97628 | -0.45563 | 4.7812
85 | -0.052856 | -0.013265 | 0.052912 | 0.013301 | 5.6541e-05 | 3.5897e-05 | 0.08063 | 0.08063 | 0.08063 | 0.97553 | -0.47036 | 0.97667 | -0.44795 | 22.1511
86 | -0.069814 | -0.017556 | 0.069874 | 0.017594 | 5.9632e-05 | 3.799e-05 | 0.10658 | 0.10658 | 0.10658 | 0.97488 | -0.48303 | 0.97579 | -0.46516 | 29.2809
87 | -0.069874 | -0.017594 | 0.069906 | 0.017614 | 3.1851e-05 | 2.0291e-05 | 0.10658 | 0.10658 | 0.10658 | 0.97579 | -0.46516 | 0.97628 | -0.45563 | 29.2808
88 | -0.081324 | -0.020476 | 0.081384 | 0.020514 | 6.0621e-05 | 3.8666e-05 | 0.12399 | 0.12399 | 0.12399 | 0.97628 | -0.45563 | 0.97707 | -0.44005 | 34.062
89 | -0.13859 | -0.034899 | 0.13869 | 0.034967 | 0.00010666 | 6.818e-05 | 0.21112 | 0.21112 | 0.21112 | 0.97707 | -0.44005 | 0.97789 | -0.42397 | 58
90 | 0.057203 | 0.014384 | -0.057182 | -0.014371 | 2.1572e-05 | 1.3711e-05 | 0.087134 | 0.087134 | 0.087134 | 0.97707 | -0.44005 | 0.97667 | -0.44795 | 23.938
91 | -0.0050307 | -0.0012608 | 0.0050307 | 0.0012608 | 3.0155e-08 | 1.9986e-09 | 0.0076456 | 0.0076456 | 0.0076456 | 0.97909 | -0.4005 | 0.9791 | -0.40038 | 2.1005
92 | -0.15738 | -0.039714 | 0.15742 | 0.039735 | 3.2672e-05 | 2.0738e-05 | 0.23928 | 0.23928 | 0.23928 | 0.9791 | -0.40038 | 0.97932 | -0.39604 | 21.9125
93 | 0.15235 | 0.038453 | -0.15233 | -0.038437 | 2.489e-05 | 1.579e-05 | 0.23164 | 0.23164 | 0.23164 | 0.9791 | -0.40038 | 0.97892 | -0.40379 | 21.2124
94 | -0.14278 | -0.035992 | 0.14288 | 0.036055 | 9.8477e-05 | 6.2746e-05 | 0.21734 | 0.21734 | 0.21734 | 0.97789 | -0.42397 | 0.97863 | -0.40957 | 29.8548
95 | -0.0049631 | -0.0012439 | 0.0049633 | 0.0012439 | 1.5038e-07 | 7.6717e-09 | 0.0075445 | 0.0075445 | 0.0075445 | 0.97889 | -0.40442 | 0.97892 | -0.40379 | 2.0727
96 | 0.14736 | 0.037193 | -0.14732 | -0.037168 | 4.0797e-05 | 2.5865e-05 | 0.22409 | 0.22409 | 0.22409 | 0.97892 | -0.40379 | 0.97863 | -0.40957 | 20.5215
97 | -0.23458 | -0.059158 | 0.23488 | 0.059351 | 0.00030212 | 0.00019264 | 0.35656 | 0.35656 | 0.35656 | 0.97932 | -0.39604 | 0.9807 | -0.36917 | 32.6516
98 | 0.077161 | 0.019423 | -0.07706 | -0.019359 | 0.00010096 | 6.437e-05 | 0.11727 | 0.11727 | 0.11727 | 0.97932 | -0.39604 | 0.97792 | -0.42346 | 32.2175
99 | 0.0051457 | 0.0012896 | -0.0051454 | -0.0012896 | 2.3179e-07 | 2.3222e-08 | 0.007851 | 0.0078511 | 0.0078511 | 0.97526 | -0.47559 | 0.97521 | -0.47654 | 2.1569
100 | -0.23805 | -0.060147 | 0.2382 | 0.060239 | 0.00014519 | 9.2587e-05 | 0.36138 | 0.36137 | 0.36138 | 0.9807 | -0.36917 | 0.98135 | -0.35646 | 33.093
101 | 0.05582 | 0.014034 | -0.055808 | -0.014027 | 1.2039e-05 | 7.6494e-06 | 0.084952 | 0.084952 | 0.084952 | 0.97792 | -0.42346 | 0.97769 | -0.42797 | 23.3385
102 | 0.0041057 | 0.0010289 | -0.0041056 | -0.001029 | 1.081e-07 | -2.348e-08 | 0.0062473 | 0.0062473 | 0.0062473 | 0.97792 | -0.42346 | 0.97789 | -0.42401 | 1.7163
103 | 0.017134 | 0.0042957 | -0.017131 | -0.0042939 | 3.1082e-06 | 1.8363e-06 | 0.026072 | 0.026072 | 0.026072 | 0.97792 | -0.42346 | 0.97773 | -0.42726 | 7.1627
104 | 0.052048 | 0.013084 | -0.052012 | -0.013061 | 3.6605e-05 | 2.3232e-05 | 0.07923 | 0.079231 | 0.079231 | 0.97769 | -0.42797 | 0.97694 | -0.44271 | 21.7666
105 | 0.047455 | 0.011919 | -0.047435 | -0.011906 | 2.0339e-05 | 1.2887e-05 | 0.07229 | 0.07229 | 0.07229 | 0.97694 | -0.44271 | 0.97648 | -0.4517 | 19.8599
106 | -0.2382 | -0.060239 | 0.2383 | 0.060305 | 0.00010382 | 6.6204e-05 | 0.36137 | 0.36137 | 0.36137 | 0.98135 | -0.35646 | 0.98182 | -0.34738 | 33.0929
107 | -0.2383 | -0.060305 | 0.23841 | 0.060374 | 0.00010691 | 6.8171e-05 | 0.36137 | 0.36137 | 0.36137 | 0.98182 | -0.34738 | 0.9823 | -0.33803 | 33.0929
108 | 0.017775 | 0.0044558 | -0.017773 | -0.0044545 | 2.2765e-06 | 1.35e-06 | 0.026865 | 0.026865 | 0.026865 | 0.98455 | -0.2946 | 0.98441 | -0.29729 | 7.3806
109 | 0.012535 | 0.0031416 | -0.012534 | -0.0031414 | 3.9106e-07 | 2.1335e-07 | 0.018947 | 0.018947 | 0.018947 | 0.98441 | -0.29729 | 0.98438 | -0.29794 | 5.2053
110 | -0.29472 | -0.075096 | 0.29503 | 0.075293 | 0.00030907 | 0.00019732 | 0.44416 | 0.44416 | 0.44416 | 0.98835 | -0.22109 | 0.98949 | -0.19938 | 40.674
111 | 0.20576 | 0.051907 | -0.20567 | -0.051849 | 9.007e-05 | 5.7521e-05 | 0.31265 | 0.31265 | 0.31265 | 0.97966 | -0.3893 | 0.97919 | -0.39845 | 42.9462
112 | -0.2138 | -0.053922 | 0.21402 | 0.05406 | 0.00021634 | 0.00013784 | 0.32487 | 0.32486 | 0.32487 | 0.97966 | -0.3893 | 0.98074 | -0.36818 | 29.7496
113 | 0.10241 | 0.025795 | -0.10231 | -0.025732 | 9.841e-05 | 6.2846e-05 | 0.15567 | 0.15567 | 0.15567 | 0.97919 | -0.39845 | 0.97816 | -0.41856 | 42.7677
114 | -0.21402 | -0.05406 | 0.2142 | 0.054179 | 0.00018671 | 0.00011896 | 0.32486 | 0.32486 | 0.32486 | 0.98074 | -0.36818 | 0.98167 | -0.35 | 29.7495
115 | 0.093641 | 0.023558 | -0.093582 | -0.023521 | 5.8668e-05 | 3.7451e-05 | 0.14248 | 0.14248 | 0.14248 | 0.97816 | -0.41856 | 0.97749 | -0.43168 | 39.1435
116 | -0.2142 | -0.054179 | 0.21423 | 0.054198 | 2.8635e-05 | 1.8244e-05 | 0.32486 | 0.32486 | 0.32486 | 0.98167 | -0.35 | 0.98182 | -0.34721 | 29.7495
117 | 0.085603 | 0.021521 | -0.085558 | -0.021492 | 4.5789e-05 | 2.9215e-05 | 0.13034 | 0.13034 | 0.13034 | 0.97749 | -0.43168 | 0.97692 | -0.44289 | 35.8067
118 | -0.22254 | -0.056279 | 0.22317 | 0.056684 | 0.00063526 | 0.00040486 | 0.33745 | 0.33745 | 0.33745 | 0.98182 | -0.34721 | 0.98488 | -0.28789 | 30.9023
119 | 0.079252 | 0.019912 | -0.079245 | -0.019908 | 6.5296e-06 | 4.164e-06 | 0.12073 | 0.12073 | 0.12073 | 0.97692 | -0.44289 | 0.97683 | -0.44462 | 33.168
120 | -0.22845 | -0.058007 | 0.22883 | 0.05825 | 0.00038048 | 0.00024253 | 0.34543 | 0.34543 | 0.34543 | 0.98488 | -0.28789 | 0.98667 | -0.25334 | 31.6327
121 | -0.052505 | -0.013173 | 0.052524 | 0.013185 | 1.9179e-05 | 1.2175e-05 | 0.080105 | 0.080105 | 0.080105 | 0.97538 | -0.47327 | 0.97577 | -0.46561 | 22.007
122 | 0.045428 | 0.0114 | -0.045415 | -0.011391 | 1.3332e-05 | 8.44e-06 | 0.06931 | 0.06931 | 0.06931 | 0.97538 | -0.47327 | 0.97506 | -0.47942 | 19.0412
123 | -0.06105 | -0.015322 | 0.061079 | 0.01534 | 2.8874e-05 | 1.8369e-05 | 0.093107 | 0.093107 | 0.093107 | 0.97577 | -0.46561 | 0.97627 | -0.45569 | 25.5788
124 | 0.038493 | 0.0096564 | -0.038483 | -0.0096502 | 9.8782e-06 | 6.2268e-06 | 0.058746 | 0.058746 | 0.058746 | 0.97506 | -0.47942 | 0.97479 | -0.48481 | 16.1391
125 | -0.069238 | -0.017385 | 0.069275 | 0.017409 | 3.6608e-05 | 2.3319e-05 | 0.10554 | 0.10554 | 0.10554 | 0.97627 | -0.45569 | 0.97683 | -0.44462 | 28.9955
126 | -0.0049614 | -0.0012434 | 0.0049615 | 0.0012435 | 1.3532e-07 | 5.927e-09 | 0.0075202 | 0.0075202 | 0.0075202 | 0.98171 | -0.35024 | 0.98173 | -0.34966 | 2.066
127 | -0.0074685 | -0.0018718 | 0.0074711 | 0.0018727 | 2.5656e-06 | 9.6663e-07 | 0.01132 | 0.01132 | 0.01132 | 0.98173 | -0.34966 | 0.9821 | -0.34245 | 3.1099
128 | -0.0074711 | -0.0018727 | 0.0074766 | 0.0018748 | 5.5511e-06 | 2.0896e-06 | 0.01132 | 0.011319 | 0.01132 | 0.9821 | -0.34245 | 0.9829 | -0.32687 | 3.1098
129 | -0.013418 | -0.0033639 | 0.013423 | 0.0033667 | 4.9944e-06 | 2.7872e-06 | 0.020314 | 0.020314 | 0.020314 | 0.9829 | -0.32687 | 0.9833 | -0.31906 | 5.5808
130 | -0.0056113 | -0.0014047 | 0.0056126 | 0.0014049 | 1.2673e-06 | 1.8859e-07 | 0.0083948 | 0.0083946 | 0.0083948 | 0.99457 | -0.10263 | 0.99481 | -0.097889 | 2.3063
131 | 0.0041987 | 0.0010509 | -0.0041963 | -0.0010514 | 2.3761e-06 | -5.6184e-07 | 0.0062813 | 0.006282 | 0.006282 | 0.99457 | -0.10263 | 0.99396 | -0.11452 | 1.7258
132 | 0.0014127 | 0.00035387 | -0.0014126 | -0.00035404 | 2.459e-08 | -1.7476e-07 | 0.0021135 | 0.0021135 | 0.0021135 | 0.99457 | -0.10263 | 0.99455 | -0.103 | 0.58065
133 | 0.00232 | 0.00058133 | -0.00232 | -0.00058144 | 4.767e-08 | -1.0654e-07 | 0.0034702 | 0.0034702 | 0.0034702 | 0.99481 | -0.097889 | 0.99479 | -0.098321 | 0.95336
134 | 0.0041963 | 0.0010514 | -0.0041957 | -0.0010516 | 5.7082e-07 | -1.3452e-07 | 0.006282 | 0.0062822 | 0.0062822 | 0.99396 | -0.11452 | 0.99381 | -0.11738 | 1.7259
135 | -0.015699 | -0.0039371 | 0.015714 | 0.0039459 | 1.5189e-05 | 8.8095e-06 | 0.023758 | 0.023758 | 0.023758 | 0.9833 | -0.31906 | 0.98434 | -0.29878 | 6.527
136 | 0.022622 | 0.0056864 | -0.022606 | -0.0056767 | 1.5842e-05 | 9.6781e-06 | 0.03416 | 0.034161 | 0.034161 | 0.98556 | -0.27487 | 0.98481 | -0.28955 | 9.3848
137 | 0.022606 | 0.0056767 | -0.022596 | -0.0056706 | 9.9524e-06 | 6.0803e-06 | 0.034161 | 0.034161 | 0.034161 | 0.98481 | -0.28955 | 0.98434 | -0.29878 | 9.3848
138 | 0.0068814 | 0.0017247 | -0.0068812 | -0.0017246 | 2.8788e-07 | 9.4071e-08 | 0.010403 | 0.010403 | 0.010403 | 0.98434 | -0.29878 | 0.98429 | -0.29966 | 2.8579
139 | 0.0043038 | 0.0010782 | -0.0043027 | -0.0010784 | 1.114e-06 | -1.8737e-07 | 0.0064905 | 0.0064909 | 0.0064909 | 0.98667 | -0.25334 | 0.98639 | -0.25878 | 1.7832
140 | -0.24859 | -0.062924 | 0.24863 | 0.06295 | 4.0556e-05 | 2.5869e-05 | 0.37679 | 0.37679 | 0.37679 | 0.9823 | -0.33803 | 0.98247 | -0.33464 | 34.5047
141 | -0.29842 | -0.076143 | 0.29869 | 0.07631 | 0.0002618 | 0.00016715 | 0.44926 | 0.44926 | 0.44926 | 0.98949 | -0.19938 | 0.99043 | -0.18123 | 41.141
142 | -0.30896 | -0.078886 | 0.30904 | 0.078938 | 8.1085e-05 | 5.1779e-05 | 0.46469 | 0.46469 | 0.46469 | 0.99043 | -0.18123 | 0.99072 | -0.1758 | 42.5543
143 | 0.010272 | 0.0025758 | -0.010271 | -0.0025752 | 1.3808e-06 | 6.8482e-07 | 0.015433 | 0.015434 | 0.015434 | 0.99043 | -0.18123 | 0.99029 | -0.18405 | 4.24
144 | 0.0029701 | 0.00074428 | -0.00297 | -0.00074435 | 6.6721e-08 | -7.2428e-08 | 0.0044609 | 0.0044609 | 0.0044609 | 0.99072 | -0.1758 | 0.99069 | -0.17628 | 1.2255
145 | -0.31201 | -0.079682 | 0.31239 | 0.079927 | 0.00038365 | 0.000245 | 0.46915 | 0.46915 | 0.46915 | 0.99072 | -0.1758 | 0.99205 | -0.1504 | 42.9628
146 | 0.010271 | 0.0025752 | -0.01027 | -0.0025745 | 1.4117e-06 | 7.0021e-07 | 0.015434 | 0.015434 | 0.015434 | 0.99029 | -0.18405 | 0.99014 | -0.18694 | 4.24
147 | 0.007559 | 0.0018951 | -0.0075576 | -0.0018946 | 1.4027e-06 | 5.25e-07 | 0.01136 | 0.01136 | 0.01136 | 0.99014 | -0.18694 | 0.98994 | -0.19083 | 3.121
148 | 0.0075576 | 0.0018946 | -0.0075547 | -0.0018935 | 2.9031e-06 | 1.0871e-06 | 0.01136 | 0.011361 | 0.011361 | 0.98994 | -0.19083 | 0.98952 | -0.1989 | 3.121
149 | 0.0075547 | 0.0018935 | -0.0075533 | -0.001893 | 1.4392e-06 | 5.3917e-07 | 0.011361 | 0.011361 | 0.011361 | 0.98952 | -0.1989 | 0.98932 | -0.2029 | 3.1211
150 | 0.0025533 | 0.00063987 | -0.0025533 | -0.00063991 | 2.4849e-08 | -4.1787e-08 | 0.0038404 | 0.0038404 | 0.0038404 | 0.98932 | -0.2029 | 0.98931 | -0.2031 | 1.0551

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60117 | 0.155

## res_load
| p_mw | q_mvar
0 | 0.0071568 | 0.0017937
1 | 0.0039588 | 0.00099218
2 | 0.00684 | 0.0017143
3 | 0.015531 | 0.0038924
4 | 0.005811 | 0.0014564
5 | 0.0087315 | 0.0021883
6 | 0.0048623 | 0.0012186
7 | 0.0037676 | 0.00094425
8 | 0.0041768 | 0.0010468
9 | 0.0043488 | 0.0010899
10 | 0.0064672 | 0.0016208
11 | 0.0088376 | 0.0022149
12 | 0.0060122 | 0.0015068
13 | 0.0093579 | 0.0023453
14 | 0.0091089 | 0.0022829
15 | 0.0031092 | 0.00077924
16 | 0.0051546 | 0.0012919
17 | 0.0050866 | 0.0012748
18 | 0.0058724 | 0.0014718
19 | 0.0086603 | 0.0021705
20 | 0.012562 | 0.0031483
21 | 0.0070423 | 0.001765
22 | 0.029761 | 0.0074589
23 | 0.006836 | 0.0017133
24 | 0.00645 | 0.0016165
25 | 0.0050383 | 0.0012627
26 | 0.0078416 | 0.0019653
27 | 0.0064138 | 0.0016075
28 | 0.0037626 | 0.00094298
29 | 0.0043919 | 0.0011007
30 | 0.0043295 | 0.0010851
31 | 0.0025444 | 0.0006377
32 | 0.008768 | 0.0021975
33 | 0.0066125 | 0.0016572
34 | 0.012093 | 0.0030307
35 | 0.0020411 | 0.00051154
36 | 0.0062264 | 0.0015605
37 | 0.0067201 | 0.0016842
38 | 0.0039704 | 0.00099507
39 | 0.031465 | 0.0078859
40 | 0.005357 | 0.0013426
41 | 0.0053681 | 0.0013454
42 | 0.0027508 | 0.00068942
43 | 0.0086668 | 0.0021721
44 | 0.012793 | 0.0032062
45 | 0.0050307 | 0.0012608
46 | 0.0040896 | 0.001025
47 | 0.0042691 | 0.0010699
48 | 0.0049631 | 0.0012439
49 | 0.0044406 | 0.0011129
50 | 0.0031763 | 0.00079606
51 | 0.0051454 | 0.0012896
52 | 0.0041832 | 0.0010484
53 | 0.0037593 | 0.00094217
54 | 0.0041056 | 0.001029
55 | 0.0045567 | 0.001142
56 | 0.005224 | 0.0013093
57 | 0.0053784 | 0.001348
58 | 0.0052384 | 0.0013129
59 | 0.012534 | 0.0031414
60 | 0.0080431 | 0.0020158
61 | 0.008672 | 0.0021734
62 | 0.0079787 | 0.0019997
63 | 0.0063199 | 0.0015839
64 | 0.0083059 | 0.0020816
65 | 0.0063059 | 0.0015804
66 | 0.0052799 | 0.0013233
67 | 0.0070763 | 0.0017735
68 | 0.0085258 | 0.0021368
69 | 0.0069221 | 0.0017348
70 | 0.0081596 | 0.002045
71 | 0.0081105 | 0.0020327
72 | 0.0099702 | 0.0024988
73 | 0.0049614 | 0.0012434
74 | 0.002507 | 0.0006283
75 | 0.0059416 | 0.0014891
76 | 0.0014126 | 0.00035404
77 | 0.0041957 | 0.0010516
78 | 0.002276 | 0.00057041
79 | 0.0043948 | 0.0011014
80 | 0.0045806 | 0.001148
81 | 0.0068812 | 0.0017246
82 | 0.0043027 | 0.0010784
83 | 0.0042743 | 0.0010713
84 | 0.0033915 | 0.00084999
85 | 0.00297 | 0.00074435
86 | 0.0025621 | 0.00064212
87 | 0.0027105 | 0.00067932
88 | 0.0015471 | 0.00038774
89 | 0.00232 | 0.00058144
90 | 0.005 | 0.0012531
91 | 0.0025533 | 0.00063991

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1