## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1632-116_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1632-116_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1632-116_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1632-116_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1632-116_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1632-116_0_5_node_34 | 0.4 | n |  | TRUE
6 | bus_LV_1632-116_0_5_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_1632-116_0_5_node_160 | 0.4 | n |  | TRUE
8 | bus_LV_1632-116_0_5_node_42 | 0.4 | n |  | TRUE
9 | bus_LV_1632-116_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1632-116_0_5_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_1632-116_0_5_node_136 | 0.4 | n |  | TRUE
12 | bus_LV_1632-116_0_5_node_139 | 0.4 | n |  | TRUE
13 | bus_LV_1632-116_0_5_node_96 | 0.4 | n |  | TRUE
14 | bus_LV_1632-116_0_5_node_40 | 0.4 | n |  | TRUE
15 | bus_LV_1632-116_0_5_node_155 | 0.4 | n |  | TRUE
16 | bus_LV_1632-116_0_5_node_138 | 0.4 | n |  | TRUE
17 | bus_LV_1632-116_0_5_node_133 | 0.4 | n |  | TRUE
18 | bus_LV_1632-116_0_5_node_137 | 0.4 | n |  | TRUE
19 | bus_LV_1632-116_0_5_node_131 | 0.4 | n |  | TRUE
20 | bus_LV_1632-116_0_5_node_130 | 0.4 | n |  | TRUE
21 | bus_LV_1632-116_0_5_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1632-116_0_5_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_1632-116_0_5_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1632-116_0_5_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1632-116_0_5_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1632-116_0_5_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1632-116_0_5_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1632-116_0_5_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1632-116_0_5_node_158 | 0.4 | n |  | TRUE
30 | bus_LV_1632-116_0_5_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1632-116_0_5_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_1632-116_0_5_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1632-116_0_5_node_15 | 0.4 | n |  | TRUE
34 | bus_LV_1632-116_0_5_node_103 | 0.4 | n |  | TRUE
35 | bus_LV_1632-116_0_5_node_102 | 0.4 | n |  | TRUE
36 | bus_LV_1632-116_0_5_node_17 | 0.4 | n |  | TRUE
37 | bus_LV_1632-116_0_5_node_100 | 0.4 | n |  | TRUE
38 | bus_LV_1632-116_0_5_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_1632-116_0_5_node_123 | 0.4 | n |  | TRUE
40 | bus_LV_1632-116_0_5_node_101 | 0.4 | n |  | TRUE
41 | bus_LV_1632-116_0_5_node_21 | 0.4 | n |  | TRUE
42 | bus_LV_1632-116_0_5_node_78 | 0.4 | n |  | TRUE
43 | bus_LV_1632-116_0_5_node_74 | 0.4 | n |  | TRUE
44 | bus_LV_1632-116_0_5_node_24 | 0.4 | n |  | TRUE
45 | bus_LV_1632-116_0_5_node_134 | 0.4 | n |  | TRUE
46 | bus_LV_1632-116_0_5_node_153 | 0.4 | n |  | TRUE
47 | bus_LV_1632-116_0_5_node_156 | 0.4 | n |  | TRUE
48 | bus_LV_1632-116_0_5_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_1632-116_0_5_node_122 | 0.4 | n |  | TRUE
50 | bus_LV_1632-116_0_5_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_1632-116_0_5_node_121 | 0.4 | n |  | TRUE
52 | bus_LV_1632-116_0_5_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_1632-116_0_5_node_89 | 0.4 | n |  | TRUE
54 | bus_LV_1632-116_0_5_node_85 | 0.4 | n |  | TRUE
55 | bus_LV_1632-116_0_5_node_84 | 0.4 | n |  | TRUE
56 | bus_LV_1632-116_0_5_node_81 | 0.4 | n |  | TRUE
57 | bus_LV_1632-116_0_5_node_32 | 0.4 | n |  | TRUE
58 | bus_LV_1632-116_0_5_node_116 | 0.4 | n |  | TRUE
59 | bus_LV_1632-116_0_5_node_110 | 0.4 | n |  | TRUE
60 | bus_LV_1632-116_0_5_node_157 | 0.4 | n |  | TRUE
61 | bus_LV_1632-116_0_5_node_79 | 0.4 | n |  | TRUE
62 | bus_LV_1632-116_0_5_node_80 | 0.4 | n |  | TRUE
63 | bus_LV_1632-116_0_5_node_128 | 0.4 | n |  | TRUE
64 | bus_LV_1632-116_0_5_node_124 | 0.4 | n |  | TRUE
65 | bus_LV_1632-116_0_5_node_75 | 0.4 | n |  | TRUE
66 | bus_LV_1632-116_0_5_node_145 | 0.4 | n |  | TRUE
67 | bus_LV_1632-116_0_5_node_146 | 0.4 | n |  | TRUE
68 | bus_LV_1632-116_0_5_node_135 | 0.4 | n |  | TRUE
69 | bus_LV_1632-116_0_5_node_152 | 0.4 | n |  | TRUE
70 | bus_LV_1632-116_0_5_node_148 | 0.4 | n |  | TRUE
71 | bus_LV_1632-116_0_5_node_149 | 0.4 | n |  | TRUE
72 | bus_LV_1632-116_0_5_node_120 | 0.4 | n |  | TRUE
73 | bus_LV_1632-116_0_5_node_143 | 0.4 | n |  | TRUE
74 | bus_LV_1632-116_0_5_node_86 | 0.4 | n |  | TRUE
75 | bus_LV_1632-116_0_5_node_77 | 0.4 | n |  | TRUE
76 | bus_LV_1632-116_0_5_node_36 | 0.4 | n |  | TRUE
77 | bus_LV_1632-116_0_5_node_37 | 0.4 | n |  | TRUE
78 | bus_LV_1632-116_0_5_node_159 | 0.4 | n |  | TRUE
79 | bus_LV_1632-116_0_5_node_44 | 0.4 | n |  | TRUE
80 | bus_LV_1632-116_0_5_node_43 | 0.4 | n |  | TRUE
81 | bus_LV_1632-116_0_5_node_38 | 0.4 | n |  | TRUE
82 | bus_LV_1632-116_0_5_node_45 | 0.4 | n |  | TRUE
83 | bus_LV_1632-116_0_5_node_39 | 0.4 | n |  | TRUE
84 | bus_LV_1632-116_0_5_node_41 | 0.4 | n |  | TRUE
85 | bus_LV_1632-116_0_5_node_144 | 0.4 | n |  | TRUE
86 | bus_LV_1632-116_0_5_node_47 | 0.4 | n |  | TRUE
87 | bus_LV_1632-116_0_5_node_94 | 0.4 | n |  | TRUE
88 | bus_LV_1632-116_0_5_node_46 | 0.4 | n |  | TRUE
89 | bus_LV_1632-116_0_5_node_48 | 0.4 | n |  | TRUE
90 | bus_LV_1632-116_0_5_node_49 | 0.4 | n |  | TRUE
91 | bus_LV_1632-116_0_5_node_50 | 0.4 | n |  | TRUE
92 | bus_LV_1632-116_0_5_node_51 | 0.4 | n |  | TRUE
93 | bus_LV_1632-116_0_5_node_52 | 0.4 | n |  | TRUE
94 | bus_LV_1632-116_0_5_node_129 | 0.4 | n |  | TRUE
95 | bus_LV_1632-116_0_5_node_126 | 0.4 | n |  | TRUE
96 | bus_LV_1632-116_0_5_node_53 | 0.4 | n |  | TRUE
97 | bus_LV_1632-116_0_5_node_154 | 0.4 | n |  | TRUE
98 | bus_LV_1632-116_0_5_node_151 | 0.4 | n |  | TRUE
99 | bus_LV_1632-116_0_5_node_125 | 0.4 | n |  | TRUE
100 | bus_LV_1632-116_0_5_node_132 | 0.4 | n |  | TRUE
101 | bus_LV_1632-116_0_5_node_54 | 0.4 | n |  | TRUE
102 | bus_LV_1632-116_0_5_node_55 | 0.4 | n |  | TRUE
103 | bus_LV_1632-116_0_5_node_56 | 0.4 | n |  | TRUE
104 | bus_LV_1632-116_0_5_node_57 | 0.4 | n |  | TRUE
105 | bus_LV_1632-116_0_5_node_58 | 0.4 | n |  | TRUE
106 | bus_LV_1632-116_0_5_node_59 | 0.4 | n |  | TRUE
107 | bus_LV_1632-116_0_5_node_61 | 0.4 | n |  | TRUE
108 | bus_LV_1632-116_0_5_node_60 | 0.4 | n |  | TRUE
109 | bus_LV_1632-116_0_5_node_62 | 0.4 | n |  | TRUE
110 | bus_LV_1632-116_0_5_node_63 | 0.4 | n |  | TRUE
111 | bus_LV_1632-116_0_5_node_64 | 0.4 | n |  | TRUE
112 | bus_LV_1632-116_0_5_node_65 | 0.4 | n |  | TRUE
113 | bus_LV_1632-116_0_5_node_72 | 0.4 | n |  | TRUE
114 | bus_LV_1632-116_0_5_node_73 | 0.4 | n |  | TRUE
115 | bus_LV_1632-116_0_5_node_70 | 0.4 | n |  | TRUE
116 | bus_LV_1632-116_0_5_node_66 | 0.4 | n |  | TRUE
117 | bus_LV_1632-116_0_5_node_67 | 0.4 | n |  | TRUE
118 | bus_LV_1632-116_0_5_node_68 | 0.4 | n |  | TRUE
119 | bus_LV_1632-116_0_5_node_69 | 0.4 | n |  | TRUE
120 | bus_LV_1632-116_0_5_node_71 | 0.4 | n |  | TRUE
121 | bus_LV_1632-116_0_5_node_76 | 0.4 | n |  | TRUE
122 | bus_LV_1632-116_0_5_node_82 | 0.4 | n |  | TRUE
123 | bus_LV_1632-116_0_5_node_83 | 0.4 | n |  | TRUE
124 | bus_LV_1632-116_0_5_node_150 | 0.4 | n |  | TRUE
125 | bus_LV_1632-116_0_5_node_87 | 0.4 | n |  | TRUE
126 | bus_LV_1632-116_0_5_node_88 | 0.4 | n |  | TRUE
127 | bus_LV_1632-116_0_5_node_142 | 0.4 | n |  | TRUE
128 | bus_LV_1632-116_0_5_node_90 | 0.4 | n |  | TRUE
129 | bus_LV_1632-116_0_5_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_1632-116_0_5_node_91 | 0.4 | n |  | TRUE
131 | bus_LV_1632-116_0_5_node_92 | 0.4 | n |  | TRUE
132 | bus_LV_1632-116_0_5_node_93 | 0.4 | n |  | TRUE
133 | bus_LV_1632-116_0_5_node_95 | 0.4 | n |  | TRUE
134 | bus_LV_1632-116_0_5_node_97 | 0.4 | n |  | TRUE
135 | bus_LV_1632-116_0_5_node_98 | 0.4 | n |  | TRUE
136 | bus_LV_1632-116_0_5_node_99 | 0.4 | n |  | TRUE
137 | bus_LV_1632-116_0_5_node_119 | 0.4 | n |  | TRUE
138 | bus_LV_1632-116_0_5_node_115 | 0.4 | n |  | TRUE
139 | bus_LV_1632-116_0_5_node_108 | 0.4 | n |  | TRUE
140 | bus_LV_1632-116_0_5_node_104 | 0.4 | n |  | TRUE
141 | bus_LV_1632-116_0_5_node_106 | 0.4 | n |  | TRUE
142 | bus_LV_1632-116_0_5_node_105 | 0.4 | n |  | TRUE
143 | bus_LV_1632-116_0_5_node_107 | 0.4 | n |  | TRUE
144 | bus_LV_1632-116_0_5_node_109 | 0.4 | n |  | TRUE
145 | bus_LV_1632-116_0_5_node_111 | 0.4 | n |  | TRUE
146 | bus_LV_1632-116_0_5_node_112 | 0.4 | n |  | TRUE
147 | bus_LV_1632-116_0_5_node_113 | 0.4 | n |  | TRUE
148 | bus_LV_1632-116_0_5_node_114 | 0.4 | n |  | TRUE
149 | bus_LV_1632-116_0_5_node_118 | 0.4 | n |  | TRUE
150 | bus_LV_1632-116_0_5_node_127 | 0.4 | n |  | TRUE
151 | bus_LV_1632-116_0_5_node_147 | 0.4 | n |  | TRUE
152 | bus_MV_224_0_node_116 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1632-116_0_5_load_0 | 0 | 0.018695 | 0.0046853 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1632-116_0_5_load_2 | 2 | 0.019448 | 0.0048741 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1632-116_0_5_load_34 | 5 | 0.029059 | 0.0072829 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1632-116_0_5_load_160 | 7 | 0.0044587 | 0.0011174 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1632-116_0_5_load_136 | 11 | 0.010178 | 0.0025509 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1632-116_0_5_load_139 | 12 | 0.0025488 | 0.00063879 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1632-116_0_5_load_96 | 13 | 0.0022803 | 0.00057151 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1632-116_0_5_load_155 | 15 | 0.002578 | 0.00064612 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1632-116_0_5_load_133 | 17 | 0.016265 | 0.0040764 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1632-116_0_5_load_131 | 19 | 0.0025586 | 0.00064123 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1632-116_0_5_load_9 | 21 | 0.0076246 | 0.0019109 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1632-116_0_5_load_10 | 22 | 0.0048098 | 0.0012054 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1632-116_0_5_load_30 | 27 | 0.019734 | 0.0049457 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1632-116_0_5_load_158 | 29 | 0.012574 | 0.0031512 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1632-116_0_5_load_33 | 31 | 0.0049116 | 0.001231 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1632-116_0_5_load_31 | 32 | 0.0061109 | 0.0015315 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1632-116_0_5_load_102 | 35 | 0.0085402 | 0.0021404 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1632-116_0_5_load_100 | 37 | 0.0062928 | 0.0015771 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1632-116_0_5_load_123 | 39 | 0.0031366 | 0.0007861 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1632-116_0_5_load_101 | 40 | 0.0037726 | 0.00094549 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1632-116_0_5_load_74 | 43 | 0.0025661 | 0.00064312 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1632-116_0_5_load_153 | 46 | 0.0025528 | 0.00063979 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1632-116_0_5_load_156 | 47 | 0.0048695 | 0.0012204 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1632-116_0_5_load_122 | 49 | 0.011719 | 0.002937 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1632-116_0_5_load_121 | 51 | 0.0048818 | 0.0012235 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1632-116_0_5_load_85 | 54 | 0.0058347 | 0.0014623 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1632-116_0_5_load_84 | 55 | 0.003422 | 0.00085764 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1632-116_0_5_load_81 | 56 | 0.013334 | 0.0033418 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1632-116_0_5_load_32 | 57 | 0.0048903 | 0.0012256 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1632-116_0_5_load_110 | 59 | 0.0036371 | 0.00091155 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1632-116_0_5_load_157 | 60 | 0.0048883 | 0.0012251 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1632-116_0_5_load_79 | 61 | 0.015626 | 0.0039163 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1632-116_0_5_load_80 | 62 | 0.0053655 | 0.0013447 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1632-116_0_5_load_128 | 63 | 0.0021988 | 0.00055107 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1632-116_0_5_load_124 | 64 | 0.002264 | 0.00056741 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1632-116_0_5_load_145 | 66 | 0.0022894 | 0.00057378 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1632-116_0_5_load_146 | 67 | 0.0022019 | 0.00055185 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1632-116_0_5_load_152 | 69 | 0.0024791 | 0.00062131 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1632-116_0_5_load_148 | 70 | 0.002273 | 0.00056968 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1632-116_0_5_load_149 | 71 | 0.0022025 | 0.000552 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1632-116_0_5_load_120 | 72 | 0.0041936 | 0.001051 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1632-116_0_5_load_143 | 73 | 0.0042166 | 0.0010568 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1632-116_0_5_load_37 | 77 | 0.0048868 | 0.0012248 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1632-116_0_5_load_159 | 78 | 0.0046663 | 0.0011695 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1632-116_0_5_load_43 | 80 | 0.0044365 | 0.0011119 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1632-116_0_5_load_38 | 81 | 0.0020418 | 0.00051173 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1632-116_0_5_load_45 | 82 | 0.0024307 | 0.00060918 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1632-116_0_5_load_39 | 83 | 0.0019468 | 0.00048792 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1632-116_0_5_load_41 | 84 | 0.0019569 | 0.00049043 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1632-116_0_5_load_144 | 85 | 0.0020491 | 0.00051356 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1632-116_0_5_load_47 | 86 | 0.0021551 | 0.00054013 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1632-116_0_5_load_46 | 88 | 0.0020182 | 0.00050582 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1632-116_0_5_load_48 | 89 | 0.009597 | 0.0024052 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1632-116_0_5_load_49 | 90 | 0.0050049 | 0.0012543 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1632-116_0_5_load_52 | 93 | 0.0033654 | 0.00084345 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1632-116_0_5_load_129 | 94 | 0.0048386 | 0.0012127 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1632-116_0_5_load_126 | 95 | 0.0022551 | 0.00056518 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1632-116_0_5_load_53 | 96 | 0.0033088 | 0.00082926 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1632-116_0_5_load_154 | 97 | 0.0034105 | 0.00085476 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1632-116_0_5_load_151 | 98 | 0.0048461 | 0.0012146 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1632-116_0_5_load_132 | 100 | 0.0024855 | 0.00062293 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1632-116_0_5_load_54 | 101 | 0.0088707 | 0.0022232 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1632-116_0_5_load_55 | 102 | 0.008409 | 0.0021075 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1632-116_0_5_load_58 | 105 | 0.0049875 | 0.00125 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1632-116_0_5_load_59 | 106 | 0.0032253 | 0.00080833 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1632-116_0_5_load_61 | 107 | 0.0030752 | 0.00077072 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1632-116_0_5_load_60 | 108 | 0.0029001 | 0.00072684 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1632-116_0_5_load_63 | 110 | 0.0059356 | 0.0014876 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1632-116_0_5_load_64 | 111 | 0.0073675 | 0.0018465 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1632-116_0_5_load_65 | 112 | 0.00721 | 0.001807 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1632-116_0_5_load_73 | 114 | 0.0079741 | 0.0019985 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1632-116_0_5_load_70 | 115 | 0.0070643 | 0.0017705 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1632-116_0_5_load_66 | 116 | 0.0096567 | 0.0024202 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1632-116_0_5_load_68 | 118 | 0.0090171 | 0.0022599 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1632-116_0_5_load_69 | 119 | 0.0040603 | 0.0010176 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1632-116_0_5_load_71 | 120 | 0.014079 | 0.0035286 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1632-116_0_5_load_76 | 121 | 0.0032721 | 0.00082007 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1632-116_0_5_load_83 | 123 | 0.013989 | 0.0035061 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1632-116_0_5_load_150 | 124 | 0.0021996 | 0.00055128 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1632-116_0_5_load_88 | 126 | 0.0038361 | 0.00096143 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1632-116_0_5_load_142 | 127 | 0.0049316 | 0.001236 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1632-116_0_5_load_90 | 128 | 0.0022556 | 0.00056532 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1632-116_0_5_load_117 | 129 | 0.0056416 | 0.0014139 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1632-116_0_5_load_91 | 130 | 0.0026928 | 0.00067488 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1632-116_0_5_load_92 | 131 | 0.0045595 | 0.0011427 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1632-116_0_5_load_93 | 132 | 0.0035235 | 0.00088308 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1632-116_0_5_load_95 | 133 | 0.0018107 | 0.00045381 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1632-116_0_5_load_97 | 134 | 0.0029666 | 0.00074349 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1632-116_0_5_load_98 | 135 | 0.0038457 | 0.00096383 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1632-116_0_5_load_99 | 136 | 0.0050634 | 0.001269 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1632-116_0_5_load_119 | 137 | 0.0081228 | 0.0020358 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1632-116_0_5_load_108 | 139 | 0.0056829 | 0.0014243 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1632-116_0_5_load_104 | 140 | 0.0059588 | 0.0014934 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1632-116_0_5_load_105 | 142 | 0.0047612 | 0.0011933 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1632-116_0_5_load_107 | 143 | 0.0055337 | 0.0013869 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1632-116_0_5_load_109 | 144 | 0.0036869 | 0.00092402 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1632-116_0_5_load_111 | 145 | 0.008499 | 0.00213 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1632-116_0_5_load_112 | 146 | 0.0037162 | 0.00093138 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1632-116_0_5_load_113 | 147 | 0.0048715 | 0.0012209 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1632-116_0_5_load_114 | 148 | 0.0036772 | 0.00092159 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1632-116_0_5_load_118 | 149 | 0.0042026 | 0.0010533 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1632-116_0_5_load_127 | 150 | 0.0021993 | 0.0005512 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1632-116_0_5_load_147 | 151 | 0.0021987 | 0.00055106 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 120 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1632-116_0_5_line_0 |  | 0 | 1 | 0.042778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1632-116_0_5_line_1 |  | 1 | 2 | 0.035966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1632-116_0_5_line_2 |  | 2 | 3 | 0.037802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1632-116_0_5_line_3 |  | 3 | 4 | 0.08006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1632-116_0_5_line_4 |  | 4 | 7 | 0.027978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1632-116_0_5_line_5 |  | 4 | 8 | 0.05608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1632-116_0_5_line_6 |  | 5 | 6 | 0.037072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1632-116_0_5_line_7 |  | 6 | 76 | 0.005355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1632-116_0_5_line_8 |  | 6 | 77 | 0.0097327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1632-116_0_5_line_9 |  | 8 | 13 | 0.030344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1632-116_0_5_line_10 |  | 8 | 14 | 0.014492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1632-116_0_5_line_11 |  | 9 | 10 | 0.040719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1632-116_0_5_line_12 |  | 9 | 11 | 0.017216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1632-116_0_5_line_13 |  | 9 | 12 | 0.057457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1632-116_0_5_line_14 |  | 10 | 17 | 0.026567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1632-116_0_5_line_15 |  | 11 | 18 | 0.031622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1632-116_0_5_line_16 |  | 13 | 87 | 0.0090749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1632-116_0_5_line_17 |  | 14 | 80 | 0.012937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1632-116_0_5_line_18 |  | 14 | 81 | 0.012956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1632-116_0_5_line_19 |  | 14 | 76 | 0.031352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1632-116_0_5_line_20 |  | 15 | 16 | 0.011596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1632-116_0_5_line_21 |  | 16 | 18 | 0.017812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1632-116_0_5_line_22 |  | 16 | 100 | 0.018154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1632-116_0_5_line_23 |  | 18 | 68 | 0.016942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1632-116_0_5_line_24 |  | 19 | 20 | 0.014767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1632-116_0_5_line_25 |  | 20 | 100 | 0.01742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1632-116_0_5_line_26 |  | 21 | 22 | 0.00091326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1632-116_0_5_line_27 |  | 21 | 23 | 0.019226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1632-116_0_5_line_28 |  | 22 | 24 | 0.031024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1632-116_0_5_line_29 |  | 23 | 25 | 0.050442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1632-116_0_5_line_30 |  | 23 | 26 | 0.023269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1632-116_0_5_line_31 |  | 24 | 27 | 0.012404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1632-116_0_5_line_32 |  | 24 | 28 | 0.037135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1632-116_0_5_line_33 |  | 25 | 29 | 0.027665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1632-116_0_5_line_34 |  | 25 | 30 | 0.092537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1632-116_0_5_line_35 |  | 26 | 31 | 0.015648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1632-116_0_5_line_36 |  | 26 | 32 | 0.0082561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1632-116_0_5_line_37 |  | 28 | 33 | 0.006698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1632-116_0_5_line_38 |  | 30 | 47 | 0.082209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1632-116_0_5_line_39 |  | 32 | 57 | 0.01525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1632-116_0_5_line_40 |  | 33 | 34 | 0.037438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1632-116_0_5_line_41 |  | 33 | 35 | 0.013732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1632-116_0_5_line_42 |  | 34 | 58 | 0.021523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_1632-116_0_5_line_43 |  | 34 | 59 | 0.019466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1632-116_0_5_line_44 |  | 35 | 36 | 0.01842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1632-116_0_5_line_45 |  | 36 | 37 | 0.011589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1632-116_0_5_line_46 |  | 37 | 40 | 0.039054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1632-116_0_5_line_47 |  | 38 | 39 | 0.084803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1632-116_0_5_line_48 |  | 38 | 40 | 0.12454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1632-116_0_5_line_49 |  | 41 | 42 | 0.013885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1632-116_0_5_line_50 |  | 41 | 43 | 0.03439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1632-116_0_5_line_51 |  | 42 | 63 | 0.015188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1632-116_0_5_line_52 |  | 42 | 64 | 0.01159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1632-116_0_5_line_53 |  | 43 | 65 | 0.015469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1632-116_0_5_line_54 |  | 44 | 45 | 0.014597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1632-116_0_5_line_55 |  | 44 | 46 | 0.011178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1632-116_0_5_line_56 |  | 45 | 68 | 0.019917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1632-116_0_5_line_57 |  | 46 | 69 | 0.0065946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1632-116_0_5_line_58 |  | 47 | 60 | 0.035394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1632-116_0_5_line_59 |  | 48 | 49 | 0.015381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1632-116_0_5_line_60 |  | 48 | 50 | 0.052819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1632-116_0_5_line_61 |  | 48 | 51 | 0.0064097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1632-116_0_5_line_62 |  | 50 | 55 | 0.020763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_1632-116_0_5_line_63 |  | 50 | 56 | 0.021369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1632-116_0_5_line_64 |  | 50 | 52 | 0.01678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_1632-116_0_5_line_65 |  | 52 | 53 | 0.004344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1632-116_0_5_line_66 |  | 52 | 54 | 0.01959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_1632-116_0_5_line_67 |  | 53 | 72 | 0.025223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1632-116_0_5_line_68 |  | 53 | 73 | 0.0025272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1632-116_0_5_line_69 |  | 54 | 74 | 0.0073062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_1632-116_0_5_line_70 |  | 55 | 75 | 0.022233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_1632-116_0_5_line_71 |  | 56 | 62 | 0.023429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1632-116_0_5_line_72 |  | 58 | 137 | 0.018697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1632-116_0_5_line_73 |  | 58 | 138 | 0.007492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_1632-116_0_5_line_74 |  | 59 | 139 | 0.030142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1632-116_0_5_line_75 |  | 61 | 62 | 0.0063517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1632-116_0_5_line_76 |  | 63 | 124 | 0.0064981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1632-116_0_5_line_77 |  | 64 | 99 | 0.024997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1632-116_0_5_line_78 |  | 65 | 121 | 0.017829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1632-116_0_5_line_79 |  | 65 | 75 | 0.005087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1632-116_0_5_line_80 |  | 66 | 67 | 0.0066332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1632-116_0_5_line_81 |  | 67 | 151 | 0.0065025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1632-116_0_5_line_82 |  | 68 | 97 | 0.012336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1632-116_0_5_line_83 |  | 69 | 98 | 0.0065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1632-116_0_5_line_84 |  | 70 | 71 | 0.006606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1632-116_0_5_line_85 |  | 71 | 124 | 0.006499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1632-116_0_5_line_86 |  | 74 | 125 | 0.005958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_1632-116_0_5_line_87 |  | 74 | 126 | 0.037554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_1632-116_0_5_line_88 |  | 75 | 119 | 0.025035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_1632-116_0_5_line_89 |  | 76 | 78 | 0.022319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1632-116_0_5_line_90 |  | 77 | 79 | 0.013748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1632-116_0_5_line_91 |  | 79 | 82 | 0.011947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1632-116_0_5_line_92 |  | 80 | 86 | 0.016846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1632-116_0_5_line_93 |  | 81 | 83 | 0.0069312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1632-116_0_5_line_94 |  | 82 | 88 | 0.015819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1632-116_0_5_line_95 |  | 83 | 84 | 0.0072696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1632-116_0_5_line_96 |  | 84 | 85 | 0.0069516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1632-116_0_5_line_97 |  | 87 | 133 | 0.012404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1632-116_0_5_line_98 |  | 87 | 132 | 0.0086247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1632-116_0_5_line_99 |  | 89 | 90 | 0.017736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1632-116_0_5_line_100 |  | 89 | 91 | 0.0040726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1632-116_0_5_line_101 |  | 90 | 92 | 0.013423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1632-116_0_5_line_102 |  | 91 | 93 | 0.014746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1632-116_0_5_line_103 |  | 92 | 94 | 0.016709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1632-116_0_5_line_104 |  | 92 | 95 | 0.018868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1632-116_0_5_line_105 |  | 94 | 98 | 0.0065003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1632-116_0_5_line_106 |  | 95 | 99 | 0.017826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1632-116_0_5_line_107 |  | 96 | 97 | 0.0087948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1632-116_0_5_line_108 |  | 99 | 150 | 0.021321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1632-116_0_5_line_109 |  | 101 | 102 | 0.0058464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1632-116_0_5_line_110 |  | 101 | 103 | 0.0055059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1632-116_0_5_line_111 |  | 102 | 104 | 0.017834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1632-116_0_5_line_112 |  | 103 | 105 | 0.018575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1632-116_0_5_line_113 |  | 103 | 106 | 0.018046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1632-116_0_5_line_114 |  | 104 | 107 | 0.013315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1632-116_0_5_line_115 |  | 104 | 108 | 0.0048533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1632-116_0_5_line_116 |  | 105 | 109 | 0.010855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1632-116_0_5_line_117 |  | 109 | 110 | 0.025316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1632-116_0_5_line_118 |  | 109 | 111 | 0.015889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1632-116_0_5_line_119 |  | 110 | 112 | 0.0091353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1632-116_0_5_line_120 |  | 111 | 113 | 0.013185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1632-116_0_5_line_121 |  | 113 | 114 | 0.0010773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_1632-116_0_5_line_122 |  | 113 | 115 | 0.02995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_1632-116_0_5_line_123 |  | 114 | 118 | 0.024173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_1632-116_0_5_line_124 |  | 115 | 120 | 0.0076354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_1632-116_0_5_line_125 |  | 116 | 117 | 0.0087744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1632-116_0_5_line_126 |  | 117 | 118 | 0.0033361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
127 | LV_1632-116_0_5_line_127 |  | 117 | 119 | 0.0131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_1632-116_0_5_line_128 |  | 121 | 122 | 0.01357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1632-116_0_5_line_129 |  | 122 | 123 | 0.016709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1632-116_0_5_line_130 |  | 125 | 127 | 0.010388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_1632-116_0_5_line_131 |  | 126 | 128 | 0.00069953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_1632-116_0_5_line_132 |  | 127 | 129 | 0.016628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
133 | LV_1632-116_0_5_line_133 |  | 128 | 130 | 0.0070243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
134 | LV_1632-116_0_5_line_134 |  | 129 | 138 | 0.011186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
135 | LV_1632-116_0_5_line_135 |  | 130 | 131 | 0.0046883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
136 | LV_1632-116_0_5_line_136 |  | 131 | 132 | 0.022173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_1632-116_0_5_line_137 |  | 133 | 134 | 0.011385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1632-116_0_5_line_138 |  | 134 | 135 | 0.022876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1632-116_0_5_line_139 |  | 135 | 136 | 0.0085001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1632-116_0_5_line_140 |  | 137 | 149 | 0.0067395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1632-116_0_5_line_141 |  | 138 | 148 | 0.02514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1632-116_0_5_line_142 |  | 139 | 141 | 0.024074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1632-116_0_5_line_143 |  | 140 | 141 | 0.014992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1632-116_0_5_line_144 |  | 141 | 144 | 0.012574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1632-116_0_5_line_145 |  | 142 | 143 | 0.017748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1632-116_0_5_line_146 |  | 143 | 145 | 0.0021906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1632-116_0_5_line_147 |  | 145 | 146 | 0.0039475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_1632-116_0_5_line_148 |  | 146 | 147 | 0.02168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_1632-116_0_5_line_149 |  | 147 | 148 | 0.0064125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_1632-116_0_5_line_150 |  | 150 | 151 | 0.0065002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1632-116_0_5_trafo_71 | 0.63 MVA 20/0.4 kV | 152 | 120 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2722472.9619 | 1212776.3077 | 2722467.4016 | 1212779.1402 | 2722456.634 | 1212781.6877 | 2722455.2437 | 1212807.1229
1 | 2722472.9619 | 1212776.3077 | 2722476.9804 | 1212783.0399 | 2722472.2141 | 1212804.1915 | 2722471.8115 | 1212810.6223
2 | 2722468.9593 | 1212848.303 | 2722469.8948 | 1212841.239 | 2722471.8115 | 1212810.6223
3 | 2722547.986 | 1212858.2673 | 2722539.5285 | 1212857.126 | 2722516.4022 | 1212852.0136 | 2722489.8137 | 1212847.4862 | 2722468.9593 | 1212848.303
4 | 2722547.986 | 1212858.2673 | 2722546.7768 | 1212864.5917 | 2722546.8132 | 1212867.9951 | 2722547.6006 | 1212869.2456 | 2722551.058 | 1212871.8519 | 2722561.8465 | 1212877.8894
5 | 2722547.986 | 1212858.2673 | 2722556.9041 | 1212858.0726 | 2722566.1002 | 1212857.2943 | 2722603.7792 | 1212851.6978
6 | 2722596.6907 | 1212801.002 | 2722587.8312 | 1212790.9567 | 2722584.4757 | 1212767.5175
7 | 2722596.6907 | 1212801.002 | 2722597.3947 | 1212806.3095
8 | 2722596.6907 | 1212801.002 | 2722595.2508 | 1212791.3764
9 | 2722603.7792 | 1212851.6978 | 2722608.5211 | 1212881.6687
10 | 2722601.5203 | 1212837.3848 | 2722603.7792 | 1212851.6978
11 | 2722407.0405 | 1212961.0851 | 2722415.5278 | 1212929.3238 | 2722418.4812 | 1212922.0566
12 | 2722418.4812 | 1212922.0566 | 2722434.7236 | 1212927.7644
13 | 2722418.4812 | 1212922.0566 | 2722391.0658 | 1212871.5619
14 | 2722407.0405 | 1212961.0851 | 2722433.114 | 1212966.1817
15 | 2722464.5576 | 1212938.2483 | 2722434.7236 | 1212927.7644
16 | 2722609.9393 | 1212890.6321 | 2722608.5211 | 1212881.6687
17 | 2722601.5203 | 1212837.3848 | 2722614.3142 | 1212835.466
18 | 2722601.5203 | 1212837.3848 | 2722588.752 | 1212839.5808
19 | 2722597.3947 | 1212806.3095 | 2722601.5203 | 1212837.3848
20 | 2722463.6768 | 1212920.461 | 2722461.0623 | 1212909.1632
21 | 2722464.5576 | 1212938.2483 | 2722463.6768 | 1212920.461
22 | 2722463.6768 | 1212920.461 | 2722481.6225 | 1212917.7202
23 | 2722464.5576 | 1212938.2483 | 2722469.5137 | 1212954.4514
24 | 2722498.8429 | 1212915.0902 | 2722493.3399 | 1212901.3873
25 | 2722498.8429 | 1212915.0902 | 2722481.6225 | 1212917.7202
26 | 2722700.4308 | 1213042.24 | 2722700.8212 | 1213041.4144
27 | 2722692.2114 | 1213059.6206 | 2722700.4308 | 1213042.24
28 | 2722714.0843 | 1213013.3684 | 2722700.8212 | 1213041.4144
29 | 2722692.2114 | 1213059.6206 | 2722672.0035 | 1213105.8515
30 | 2722713.4501 | 1213069.265 | 2722692.2114 | 1213059.6206
31 | 2722725.1855 | 1213018.9678 | 2722714.0843 | 1213013.3684
32 | 2722714.0843 | 1213013.3684 | 2722709.707 | 1213011.1655 | 2722722.9359 | 1212987.2415 | 2722718.3026 | 1212985.6561
33 | 2722689.2401 | 1213098.3781 | 2722688.8538 | 1213104.9641 | 2722688.1353 | 1213107.7515 | 2722686.7664 | 1213109.647 | 2722684.5641 | 1213110.3133 | 2722682.1662 | 1213110.5197 | 2722672.0035 | 1213105.8515
34 | 2722688.0379 | 1213162.6806 | 2722679.0474 | 1213162.351 | 2722669.3882 | 1213161.2848 | 2722659.6498 | 1213158.8938 | 2722654.6023 | 1213156.7661 | 2722651.2781 | 1213154.7184 | 2722649.9524 | 1213152.3004 | 2722649.8027 | 1213149.6063 | 2722651.665 | 1213145.8862 | 2722659.391 | 1213131.9677 | 2722672.0035 | 1213105.8515
35 | 2722713.4501 | 1213069.265 | 2722715.4497 | 1213072.1639 | 2722715.8937 | 1213075.331 | 2722712.2402 | 1213083.478
36 | 2722713.4501 | 1213069.265 | 2722721.0836 | 1213066.1196
37 | 2722721.7344 | 1212979.9001 | 2722718.3026 | 1212985.6561
38 | 2722688.0379 | 1213162.6806 | 2722719.7191 | 1213113.5613 | 2722733.9431 | 1213094.5305
39 | 2722721.0836 | 1213066.1196 | 2722721.0836 | 1213066.1196 | 2722735.485 | 1213071.1372
40 | 2722693.234 | 1212971.1959 | 2722717.5327 | 1212975.8105 | 2722718.8026 | 1212973.924 | 2722720.3834 | 1212975.0241 | 2722717.8795 | 1212978.8977 | 2722721.7344 | 1212979.9001
41 | 2722721.7344 | 1212979.9001 | 2722728.658 | 1212968.0418
42 | 2722672.0039 | 1212968.1346 | 2722690.224 | 1212971.6009 | 2722693.234 | 1212971.1959
43 | 2722693.234 | 1212971.1959 | 2722695.5555 | 1212969.9093 | 2722697.3219 | 1212967.8997 | 2722704.8279 | 1212955.9211
44 | 2722737.9456 | 1212952.1345 | 2722728.658 | 1212968.0418
45 | 2722737.9456 | 1212952.1345 | 2722744.3602 | 1212942.4827
46 | 2722744.3602 | 1212942.4827 | 2722761.457 | 1212916.7579 | 2722765.6947 | 1212909.7771
47 | 2722747.6855 | 1212792.4901 | 2722815.3908 | 1212796.487 | 2722826.4223 | 1212800.6841 | 2722830.9199 | 1212803.7012
48 | 2722830.9199 | 1212803.7012 | 2722821.4727 | 1212818.1289 | 2722791.6396 | 1212866.3294 | 2722774.0038 | 1212896.0892 | 2722765.6947 | 1212909.7771
49 | 2722551.9976 | 1213046.7723 | 2722552.887 | 1213055.9976 | 2722555.8925 | 1213059.5065
50 | 2722555.8925 | 1213059.5065 | 2722554.6662 | 1213045.604 | 2722554.9885 | 1213041.3851 | 2722555.2521 | 1213038.177 | 2722556.6076 | 1213035.0802 | 2722559.4647 | 1213032.8706 | 2722565.1148 | 1213030.879
51 | 2722551.9976 | 1213046.7723 | 2722536.9632 | 1213048.9254
52 | 2722551.9976 | 1213046.7723 | 2722552.0032 | 1213035.182
53 | 2722579.7037 | 1213025.7366 | 2722565.1148 | 1213030.879
54 | 2722478.7203 | 1212987.5437 | 2722473.2152 | 1212974.0202
55 | 2722478.7203 | 1212987.5437 | 2722489.7678 | 1212985.8442
56 | 2722469.5137 | 1212954.4514 | 2722473.2152 | 1212974.0202
57 | 2722496.2857 | 1212984.8415 | 2722489.7678 | 1212985.8442
58 | 2722733.9431 | 1213094.5305 | 2722755.1327 | 1213066.1801
59 | 2722658.7278 | 1213036.4474 | 2722649.5085 | 1213043.1629 | 2722647.252 | 1213046.4635
60 | 2722622.0097 | 1213011.2729 | 2722625.8269 | 1213010.4174 | 2722629.7454 | 1213021.6288 | 2722634.6755 | 1213032.4274 | 2722640.7498 | 1213044.1169 | 2722644.6041 | 1213050.3231 | 2722647.252 | 1213046.4635
61 | 2722647.252 | 1213046.4635 | 2722650.5177 | 1213051.9789
62 | 2722622.0097 | 1213011.2729 | 2722601.748 | 1213015.807
63 | 2722622.0097 | 1213011.2729 | 2722625.5858 | 1213021.3987 | 2722629.5083 | 1213031.2786
64 | 2722622.9254 | 1212997.4256 | 2722619.3312 | 1212998.5192 | 2722622.0097 | 1213011.2729
65 | 2722622.9254 | 1212997.4256 | 2722627.1846 | 1212996.5125
66 | 2722622.9254 | 1212997.4256 | 2722621.3339 | 1212985.3947 | 2722620.8576 | 1212977.9553
67 | 2722627.1846 | 1212996.5125 | 2722628.6948 | 1213003.9937 | 2722632.2562 | 1213003.7556 | 2722646.0402 | 1213006.3273
68 | 2722627.1846 | 1212996.5125 | 2722626.6842 | 1212994.0353
69 | 2722620.3907 | 1212970.664 | 2722620.8576 | 1212977.9553
70 | 2722580.0513 | 1213020.6621 | 2722601.748 | 1213015.807
71 | 2722640.9436 | 1213051.6917 | 2722639.7758 | 1213050.0903 | 2722634.3571 | 1213040.8829 | 2722629.899 | 1213032.2624 | 2722629.5083 | 1213031.2786
72 | 2722672.0039 | 1212968.1346 | 2722668.3822 | 1212986.4776
73 | 2722664.4902 | 1212968.0355 | 2722672.0039 | 1212968.1346
74 | 2722720.8329 | 1212930.3795 | 2722704.8279 | 1212955.9211
75 | 2722640.9436 | 1213051.6917 | 2722644.686 | 1213056.8238
76 | 2722536.9632 | 1213048.9254 | 2722530.5307 | 1213049.8467
77 | 2722542.5923 | 1213012.6528 | 2722544.487 | 1213020.6645 | 2722550.9964 | 1213029.683 | 2722552.0042 | 1213033.1508 | 2722552.0032 | 1213035.182
78 | 2722579.7037 | 1213025.7366 | 2722583.7871 | 1213043.0921
79 | 2722580.0513 | 1213020.6621 | 2722579.7037 | 1213025.7366
80 | 2722502.1795 | 1213019.3041 | 2722508.7247 | 1213018.2268
81 | 2722508.7247 | 1213018.2268 | 2722515.1409 | 1213017.1709
82 | 2722469.5137 | 1212954.4514 | 2722481.7027 | 1212952.5512
83 | 2722502.7102 | 1212983.8532 | 2722496.2857 | 1212984.8415
84 | 2722517.5581 | 1213051.7046 | 2722524.0974 | 1213050.7681
85 | 2722530.5307 | 1213049.8467 | 2722524.0974 | 1213050.7681
86 | 2722620.3907 | 1212970.664 | 2722626.3559 | 1212970.3086
87 | 2722620.3907 | 1212970.664 | 2722617.4019 | 1212938.2777 | 2722616.8628 | 1212933.2763
88 | 2722580.0513 | 1213020.6621 | 2722576.7611 | 1213021.0169 | 2722573.6482 | 1213020.8862 | 2722570.3127 | 1213020.117 | 2722568.1909 | 1213018.3499 | 2722566.6306 | 1213015.5156 | 2722565.8183 | 1213006.3616
89 | 2722597.3947 | 1212806.3095 | 2722619.5382 | 1212803.0511
90 | 2722593.2167 | 1212777.7795 | 2722595.2508 | 1212791.3764
91 | 2722593.2167 | 1212777.7795 | 2722605.0165 | 1212775.9123
92 | 2722614.3142 | 1212835.466 | 2722630.9739 | 1212832.9673
93 | 2722588.752 | 1212839.5808 | 2722581.9211 | 1212840.7556
94 | 2722620.6415 | 1212773.4399 | 2722605.0165 | 1212775.9123
95 | 2722581.9211 | 1212840.7556 | 2722574.7566 | 1212841.9878
96 | 2722567.9057 | 1212843.166 | 2722574.7566 | 1212841.9878
97 | 2722609.9393 | 1212890.6321 | 2722622.1719 | 1212888.576
98 | 2722609.9393 | 1212890.6321 | 2722611.3744 | 1212899.1366
99 | 2722514.7429 | 1212951.3086 | 2722520.8222 | 1212963.0452 | 2722522.0379 | 1212967.3967
100 | 2722512.8698 | 1212947.6923 | 2722514.7429 | 1212951.3086
101 | 2722525.6496 | 1212980.3243 | 2722522.0379 | 1212967.3967
102 | 2722512.8698 | 1212947.6923 | 2722509.1111 | 1212941.2657 | 2722506.8802 | 1212934.3144
103 | 2722525.6496 | 1212980.3243 | 2722509.1349 | 1212982.8648
104 | 2722525.6496 | 1212980.3243 | 2722529.3541 | 1212989.3851 | 2722532.3397 | 1212996.4519 | 2722533.1552 | 1212997.5988
105 | 2722502.7102 | 1212983.8532 | 2722509.1349 | 1212982.8648
106 | 2722542.5923 | 1213012.6528 | 2722539.9543 | 1213007.161 | 2722533.1552 | 1212997.5988
107 | 2722481.7027 | 1212952.5512 | 2722490.3926 | 1212951.1964
108 | 2722542.5923 | 1213012.6528 | 2722521.5548 | 1213016.1152
109 | 2722527.0622 | 1212910.2077 | 2722525.3192 | 1212904.6272
110 | 2722529.8051 | 1212914.9706 | 2722527.175 | 1212910.5687 | 2722527.0622 | 1212910.2077
111 | 2722520.0022 | 1212887.6038 | 2722525.3192 | 1212904.6272
112 | 2722529.8051 | 1212914.9706 | 2722538.9838 | 1212923.5324 | 2722541.0805 | 1212929.1783
113 | 2722547.0824 | 1212909.5992 | 2722529.8051 | 1212914.9706
114 | 2722520.0022 | 1212887.6038 | 2722507.2499 | 1212891.4341
115 | 2722520.0022 | 1212887.6038 | 2722524.6465 | 1212886.1951
116 | 2722544.8595 | 1212939.3542 | 2722541.0805 | 1212929.1783
117 | 2722544.8595 | 1212939.3542 | 2722569.6629 | 1212934.2834
118 | 2722544.8595 | 1212939.3542 | 2722548.4951 | 1212954.8217
119 | 2722578.6132 | 1212932.4536 | 2722569.6629 | 1212934.2834
120 | 2722551.512 | 1212967.6571 | 2722548.4951 | 1212954.8217
121 | 2722551.512 | 1212967.6571 | 2722551.9319 | 1212968.6491
122 | 2722551.512 | 1212967.6571 | 2722580.8644 | 1212961.7038
123 | 2722551.9319 | 1212968.6491 | 2722557.0199 | 1212980.6691 | 2722561.8135 | 1212990.7031
124 | 2722588.3474 | 1212960.1861 | 2722580.8644 | 1212961.7038
125 | 2722563.5718 | 1212993.5359 | 2722572.157 | 1212991.7238
126 | 2722563.5718 | 1212993.5359 | 2722561.9449 | 1212990.9783 | 2722561.8135 | 1212990.7031
127 | 2722563.5718 | 1212993.5359 | 2722565.0944 | 1212998.2041 | 2722565.8183 | 1213006.3616
128 | 2722590.9036 | 1213053.8773 | 2722586.6999 | 1213050.9887 | 2722584.6724 | 1213046.8549 | 2722583.7871 | 1213043.0921
129 | 2722590.9036 | 1213053.8773 | 2722591.3428 | 1213070.5769
130 | 2722626.3559 | 1212970.3086 | 2722636.7256 | 1212969.6905
131 | 2722616.8628 | 1212933.2763 | 2722616.7878 | 1212932.5808
132 | 2722636.7256 | 1212969.6905 | 2722653.3241 | 1212968.7011
133 | 2722616.7878 | 1212932.5808 | 2722616.3809 | 1212928.805 | 2722615.844 | 1212925.6234
134 | 2722664.4902 | 1212968.0355 | 2722653.3241 | 1212968.7011
135 | 2722615.844 | 1212925.6234 | 2722615.0639 | 1212921.0005
136 | 2722611.3744 | 1212899.1366 | 2722615.0639 | 1212921.0005
137 | 2722622.1719 | 1212888.576 | 2722633.3996 | 1212886.6889
138 | 2722655.9589 | 1212882.8971 | 2722633.3996 | 1212886.6889
139 | 2722664.3414 | 1212881.4882 | 2722655.9589 | 1212882.8971
140 | 2722667.0768 | 1212993.0894 | 2722668.3822 | 1212986.4776
141 | 2722664.4902 | 1212968.0355 | 2722671.692 | 1212943.9495
142 | 2722733.6158 | 1212909.9797 | 2722720.8329 | 1212930.3795
143 | 2722733.6158 | 1212909.9797 | 2722719.2436 | 1212905.7143
144 | 2722733.6158 | 1212909.9797 | 2722735.3053 | 1212907.2791 | 2722737.8495 | 1212902.5611 | 2722738.903 | 1212898.673
145 | 2722681.4982 | 1212911.1532 | 2722686.0684 | 1212895.8684 | 2722687.7889 | 1212896.379
146 | 2722680.8706 | 1212913.252 | 2722681.4982 | 1212911.1532
147 | 2722680.8706 | 1212913.252 | 2722679.7398 | 1212917.0341
148 | 2722673.529 | 1212937.8057 | 2722679.7398 | 1212917.0341
149 | 2722671.692 | 1212943.9495 | 2722673.529 | 1212937.8057
150 | 2722515.1409 | 1213017.1709 | 2722521.5548 | 1213016.1152

## bus_geodata
| x | y | coords
0 | 2722455.2437 | 1212807.1229
1 | 2722472.9619 | 1212776.3077
2 | 2722471.8115 | 1212810.6223
3 | 2722468.9593 | 1212848.303
4 | 2722547.986 | 1212858.2673
5 | 2722584.4757 | 1212767.5175
6 | 2722596.6907 | 1212801.002
7 | 2722561.8465 | 1212877.8894
8 | 2722603.7792 | 1212851.6978
9 | 2722418.4812 | 1212922.0566
10 | 2722407.0405 | 1212961.0851
11 | 2722434.7236 | 1212927.7644
12 | 2722391.0658 | 1212871.5619
13 | 2722608.5211 | 1212881.6687
14 | 2722601.5203 | 1212837.3848
15 | 2722461.0623 | 1212909.1633
16 | 2722463.6768 | 1212920.461
17 | 2722433.114 | 1212966.1817
18 | 2722464.5576 | 1212938.2483
19 | 2722493.3399 | 1212901.3873
20 | 2722498.8429 | 1212915.0902
21 | 2722700.4308 | 1213042.24
22 | 2722700.8212 | 1213041.4144
23 | 2722692.2114 | 1213059.6206
24 | 2722714.0843 | 1213013.3684
25 | 2722672.0035 | 1213105.8515
26 | 2722713.4501 | 1213069.265
27 | 2722725.1855 | 1213018.9678
28 | 2722718.3026 | 1212985.6561
29 | 2722689.2401 | 1213098.3781
30 | 2722688.0379 | 1213162.6806
31 | 2722712.2402 | 1213083.478
32 | 2722721.0836 | 1213066.1196
33 | 2722721.7344 | 1212979.9001
34 | 2722693.234 | 1212971.1959
35 | 2722728.658 | 1212968.0418
36 | 2722737.9456 | 1212952.1345
37 | 2722744.3602 | 1212942.4827
38 | 2722830.9199 | 1212803.7012
39 | 2722747.6855 | 1212792.4901
40 | 2722765.6947 | 1212909.7771
41 | 2722555.8925 | 1213059.5065
42 | 2722551.9976 | 1213046.7723
43 | 2722565.1148 | 1213030.879
44 | 2722478.7203 | 1212987.5437
45 | 2722473.2152 | 1212974.0202
46 | 2722489.7678 | 1212985.8442
47 | 2722733.9431 | 1213094.5305
48 | 2722647.252 | 1213046.4635
49 | 2722658.7277 | 1213036.4474
50 | 2722622.0097 | 1213011.2729
51 | 2722650.5177 | 1213051.9789
52 | 2722622.9254 | 1212997.4256
53 | 2722627.1846 | 1212996.5125
54 | 2722620.8576 | 1212977.9553
55 | 2722601.748 | 1213015.807
56 | 2722629.5083 | 1213031.2786
57 | 2722735.485 | 1213071.1372
58 | 2722672.0039 | 1212968.1346
59 | 2722704.8279 | 1212955.9211
60 | 2722755.1327 | 1213066.1801
61 | 2722644.686 | 1213056.8238
62 | 2722640.9436 | 1213051.6917
63 | 2722536.9632 | 1213048.9254
64 | 2722552.0032 | 1213035.182
65 | 2722579.7037 | 1213025.7366
66 | 2722502.1795 | 1213019.3041
67 | 2722508.7247 | 1213018.2268
68 | 2722469.5137 | 1212954.4514
69 | 2722496.2857 | 1212984.8415
70 | 2722517.5581 | 1213051.7046
71 | 2722524.0974 | 1213050.7681
72 | 2722646.0402 | 1213006.3273
73 | 2722626.6842 | 1212994.0353
74 | 2722620.3907 | 1212970.664
75 | 2722580.0513 | 1213020.6621
76 | 2722597.3947 | 1212806.3095
77 | 2722595.2508 | 1212791.3764
78 | 2722619.5382 | 1212803.0511
79 | 2722593.2167 | 1212777.7795
80 | 2722614.3142 | 1212835.466
81 | 2722588.752 | 1212839.5808
82 | 2722605.0165 | 1212775.9123
83 | 2722581.9211 | 1212840.7556
84 | 2722574.7566 | 1212841.9878
85 | 2722567.9057 | 1212843.166
86 | 2722630.9739 | 1212832.9673
87 | 2722609.9393 | 1212890.6321
88 | 2722620.6415 | 1212773.4399
89 | 2722514.7429 | 1212951.3086
90 | 2722522.0379 | 1212967.3967
91 | 2722512.8698 | 1212947.6923
92 | 2722525.6496 | 1212980.3243
93 | 2722506.8802 | 1212934.3144
94 | 2722509.1349 | 1212982.8648
95 | 2722533.1552 | 1212997.5988
96 | 2722490.3926 | 1212951.1964
97 | 2722481.7027 | 1212952.5512
98 | 2722502.7102 | 1212983.8532
99 | 2722542.5923 | 1213012.6528
100 | 2722481.6225 | 1212917.7202
101 | 2722527.0622 | 1212910.2077
102 | 2722525.3192 | 1212904.6272
103 | 2722529.8051 | 1212914.9706
104 | 2722520.0022 | 1212887.6038
105 | 2722541.0805 | 1212929.1783
106 | 2722547.0824 | 1212909.5992
107 | 2722507.2499 | 1212891.4341
108 | 2722524.6465 | 1212886.1951
109 | 2722544.8595 | 1212939.3542
110 | 2722569.663 | 1212934.2834
111 | 2722548.4951 | 1212954.8217
112 | 2722578.6132 | 1212932.4536
113 | 2722551.512 | 1212967.6571
114 | 2722551.9319 | 1212968.6491
115 | 2722580.8644 | 1212961.7038
116 | 2722572.157 | 1212991.7238
117 | 2722563.5718 | 1212993.5359
118 | 2722561.8135 | 1212990.7031
119 | 2722565.8183 | 1213006.3616
120 | 2722588.3474 | 1212960.1861
121 | 2722583.7871 | 1213043.0921
122 | 2722590.9036 | 1213053.8773
123 | 2722591.3428 | 1213070.577
124 | 2722530.5307 | 1213049.8467
125 | 2722626.3559 | 1212970.3086
126 | 2722616.8628 | 1212933.2763
127 | 2722636.7256 | 1212969.6905
128 | 2722616.7878 | 1212932.5808
129 | 2722653.3241 | 1212968.7011
130 | 2722615.844 | 1212925.6234
131 | 2722615.0639 | 1212921.0005
132 | 2722611.3744 | 1212899.1366
133 | 2722622.1719 | 1212888.576
134 | 2722633.3996 | 1212886.6889
135 | 2722655.9589 | 1212882.8971
136 | 2722664.3414 | 1212881.4882
137 | 2722668.3822 | 1212986.4776
138 | 2722664.4902 | 1212968.0355
139 | 2722720.8329 | 1212930.3795
140 | 2722719.2436 | 1212905.7143
141 | 2722733.6158 | 1212909.9797
142 | 2722687.7889 | 1212896.379
143 | 2722681.4982 | 1212911.1532
144 | 2722738.903 | 1212898.673
145 | 2722680.8706 | 1212913.252
146 | 2722679.7398 | 1212917.0341
147 | 2722673.529 | 1212937.8057
148 | 2722671.692 | 1212943.9495
149 | 2722667.0768 | 1212993.0894
150 | 2722521.5548 | 1213016.1152
151 | 2722515.1409 | 1213017.1709
152 | 2722551.512 | 1212967.6571

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97003 | -0.57915 | 0.018695 | 0.0046853
1 | 0.97077 | -0.56434 | 0 | 0
2 | 0.9714 | -0.55192 | 0.019448 | 0.0048741
3 | 0.97275 | -0.52532 | 0 | 0
4 | 0.9756 | -0.46923 | 0 | 0
5 | 0.97461 | -0.48901 | 0.029059 | 0.0072829
6 | 0.97561 | -0.46926 | 0 | 0
7 | 0.97548 | -0.47151 | 0.0044587 | 0.0011174
8 | 0.97783 | -0.42557 | 0 | 0
9 | 0.97248 | -0.53076 | 0 | 0
10 | 0.97186 | -0.54298 | 0 | 0
11 | 0.97278 | -0.5248 | 0.010178 | 0.0025509
12 | 0.97234 | -0.53346 | 0.0025488 | 0.00063879
13 | 0.98067 | -0.37027 | 0.0022803 | 0.00057151
14 | 0.97706 | -0.44081 | 0 | 0
15 | 0.97348 | -0.51097 | 0.002578 | 0.00064612
16 | 0.97351 | -0.51042 | 0 | 0
17 | 0.97146 | -0.55096 | 0.016265 | 0.0040764
18 | 0.97364 | -0.50792 | 0 | 0
19 | 0.97335 | -0.51362 | 0.0025586 | 0.00064123
20 | 0.97339 | -0.51292 | 0 | 0
21 | 0.97357 | -0.50932 | 0.0076246 | 0.0019109
22 | 0.97361 | -0.50855 | 0.0048098 | 0.0012054
23 | 0.97289 | -0.52285 | 0 | 0
24 | 0.97508 | -0.47968 | 0 | 0
25 | 0.97184 | -0.54363 | 0 | 0
26 | 0.97254 | -0.52968 | 0 | 0
27 | 0.97485 | -0.48417 | 0.019734 | 0.0049457
28 | 0.97752 | -0.43185 | 0 | 0
29 | 0.97151 | -0.55005 | 0.012574 | 0.0031512
30 | 0.97099 | -0.56031 | 0 | 0
31 | 0.97247 | -0.53109 | 0.0049116 | 0.001231
32 | 0.97246 | -0.53135 | 0.0061109 | 0.0015315
33 | 0.97796 | -0.42325 | 0 | 0
34 | 0.98117 | -0.36057 | 0 | 0
35 | 0.97768 | -0.4287 | 0.0085402 | 0.0021404
36 | 0.97745 | -0.43314 | 0 | 0
37 | 0.97731 | -0.43593 | 0.0062928 | 0.0015771
38 | 0.9767 | -0.44801 | 0 | 0
39 | 0.97645 | -0.45287 | 0.0031366 | 0.0007861
40 | 0.97706 | -0.44086 | 0.0037726 | 0.00094549
41 | 0.98476 | -0.29078 | 0 | 0
42 | 0.98349 | -0.31535 | 0 | 0
43 | 0.9879 | -0.2302 | 0.0025661 | 0.00064312
44 | 0.97561 | -0.46909 | 0 | 0
45 | 0.97502 | -0.48068 | 0 | 0
46 | 0.97606 | -0.46022 | 0.0025528 | 0.00063979
47 | 0.97024 | -0.57516 | 0.0048695 | 0.0012204
48 | 0.98619 | -0.2634 | 0 | 0
49 | 0.98602 | -0.26663 | 0.011719 | 0.002937
50 | 0.987 | -0.2477 | 0 | 0
51 | 0.98616 | -0.26396 | 0.0048818 | 0.0012235
52 | 0.98602 | -0.26648 | 0 | 0
53 | 0.98599 | -0.26713 | 0 | 0
54 | 0.98492 | -0.28786 | 0.0058347 | 0.0014623
55 | 0.9884 | -0.22074 | 0.003422 | 0.00085764
56 | 0.98632 | -0.26083 | 0.013334 | 0.0033418
57 | 0.97239 | -0.53273 | 0.0048903 | 0.0012256
58 | 0.98228 | -0.33894 | 0 | 0
59 | 0.98083 | -0.36726 | 0.0036371 | 0.00091155
60 | 0.97008 | -0.57836 | 0.0048883 | 0.0012251
61 | 0.98578 | -0.27143 | 0.015626 | 0.0039163
62 | 0.98587 | -0.26965 | 0.0053655 | 0.0013447
63 | 0.98336 | -0.31778 | 0.0021988 | 0.00055107
64 | 0.98252 | -0.33405 | 0.002264 | 0.00056741
65 | 0.98935 | -0.20237 | 0 | 0
66 | 0.98024 | -0.3785 | 0.0022894 | 0.00057378
67 | 0.98025 | -0.37823 | 0.0022019 | 0.00055185
68 | 0.97422 | -0.49652 | 0 | 0
69 | 0.97635 | -0.45469 | 0.0024791 | 0.00062131
70 | 0.98328 | -0.31935 | 0.002273 | 0.00056968
71 | 0.9833 | -0.31908 | 0.0022025 | 0.000552
72 | 0.98589 | -0.26903 | 0.0041936 | 0.001051
73 | 0.98598 | -0.26733 | 0.0042166 | 0.0010568
74 | 0.98451 | -0.29569 | 0 | 0
75 | 0.98991 | -0.19168 | 0 | 0
76 | 0.9758 | -0.4655 | 0 | 0
77 | 0.97552 | -0.47092 | 0.0048868 | 0.0012248
78 | 0.9757 | -0.4674 | 0.0046663 | 0.0011695
79 | 0.97547 | -0.47204 | 0 | 0
80 | 0.97698 | -0.44237 | 0.0044365 | 0.0011119
81 | 0.97696 | -0.4427 | 0.0020418 | 0.00051173
82 | 0.97542 | -0.47302 | 0.0024307 | 0.00060918
83 | 0.97692 | -0.44346 | 0.0019468 | 0.00048792
84 | 0.97689 | -0.44399 | 0.0019569 | 0.00049043
85 | 0.97688 | -0.44425 | 0.0020491 | 0.00051356
86 | 0.97694 | -0.44303 | 0.0021551 | 0.00054013
87 | 0.98153 | -0.35342 | 0 | 0
88 | 0.97539 | -0.4736 | 0.0020182 | 0.00050582
89 | 0.97743 | -0.43351 | 0.009597 | 0.0024052
90 | 0.97764 | -0.42932 | 0.0050049 | 0.0012543
91 | 0.97741 | -0.43376 | 0 | 0
92 | 0.97786 | -0.42492 | 0 | 0
93 | 0.97737 | -0.43466 | 0.0033654 | 0.00084345
94 | 0.97696 | -0.44262 | 0.0048386 | 0.0012127
95 | 0.9792 | -0.39881 | 0.0022551 | 0.00056518
96 | 0.97411 | -0.49858 | 0.0033088 | 0.00082926
97 | 0.97414 | -0.49804 | 0.0034105 | 0.00085476
98 | 0.97664 | -0.44894 | 0.0048461 | 0.0012146
99 | 0.9805 | -0.37347 | 0 | 0
100 | 0.97343 | -0.5121 | 0.0024855 | 0.00062293
101 | 0.99389 | -0.11634 | 0.0088707 | 0.0022232
102 | 0.99381 | -0.11783 | 0.008409 | 0.0021075
103 | 0.99401 | -0.11408 | 0 | 0
104 | 0.99372 | -0.11971 | 0 | 0
105 | 0.99446 | -0.10541 | 0.0049875 | 0.00125
106 | 0.99395 | -0.11511 | 0.0032253 | 0.00080833
107 | 0.99368 | -0.12043 | 0.0030752 | 0.00077072
108 | 0.9937 | -0.11996 | 0.0029001 | 0.00072684
109 | 0.99477 | -0.099392 | 0 | 0
110 | 0.99446 | -0.10526 | 0.0059356 | 0.0014876
111 | 0.99541 | -0.086913 | 0.0073675 | 0.0018465
112 | 0.9944 | -0.10642 | 0.00721 | 0.001807
113 | 0.99604 | -0.074864 | 0 | 0
114 | 0.99594 | -0.076816 | 0.0079741 | 0.0019985
115 | 0.99919 | -0.01531 | 0.0070643 | 0.0017705
116 | 0.99327 | -0.12742 | 0.0096567 | 0.0024202
117 | 0.99335 | -0.12592 | 0 | 0
118 | 0.99366 | -0.12005 | 0.0090171 | 0.0022599
119 | 0.99216 | -0.14858 | 0.0040603 | 0.0010176
120 | 1 | 0 | -0.58657 | -0.15055
121 | 0.98907 | -0.20786 | 0.0032721 | 0.00082007
122 | 0.98889 | -0.21124 | 0 | 0
123 | 0.98868 | -0.21541 | 0.013989 | 0.0035061
124 | 0.98332 | -0.31856 | 0.0021996 | 0.00055128
125 | 0.98433 | -0.29923 | 0 | 0
126 | 0.98358 | -0.31369 | 0.0038361 | 0.00096143
127 | 0.98401 | -0.30541 | 0.0049316 | 0.001236
128 | 0.98356 | -0.31401 | 0.0022556 | 0.00056532
129 | 0.98352 | -0.315 | 0.0056416 | 0.0014139
130 | 0.9834 | -0.31723 | 0.0026928 | 0.00067488
131 | 0.98329 | -0.31933 | 0.0045595 | 0.0011427
132 | 0.98247 | -0.3353 | 0.0035235 | 0.00088308
133 | 0.98138 | -0.35649 | 0.0018107 | 0.00045381
134 | 0.98125 | -0.35894 | 0.0029666 | 0.00074349
135 | 0.98106 | -0.36263 | 0.0038457 | 0.00096383
136 | 0.98102 | -0.36341 | 0.0050634 | 0.001269
137 | 0.98207 | -0.3431 | 0.0081228 | 0.0020358
138 | 0.98271 | -0.33059 | 0 | 0
139 | 0.9804 | -0.37563 | 0.0056829 | 0.0014243
140 | 0.9801 | -0.38146 | 0.0059588 | 0.0014934
141 | 0.98019 | -0.37984 | 0 | 0
142 | 0.98121 | -0.35997 | 0.0047612 | 0.0011933
143 | 0.98129 | -0.35844 | 0.0055337 | 0.0013869
144 | 0.98014 | -0.38069 | 0.0036869 | 0.00092402
145 | 0.98131 | -0.35803 | 0.008499 | 0.00213
146 | 0.98138 | -0.35669 | 0.0037162 | 0.00093138
147 | 0.98183 | -0.34786 | 0.0048715 | 0.0012209
148 | 0.98199 | -0.34469 | 0.0036772 | 0.00092159
149 | 0.98204 | -0.34361 | 0.0042026 | 0.0010533
150 | 0.98032 | -0.37691 | 0.0021993 | 0.0005512
151 | 0.98028 | -0.3777 | 0.0021987 | 0.00055106
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.018695 | -0.0046853 | 0.018708 | 0.0046932 | 1.3193e-05 | 7.9148e-06 | 0.028677 | 0.028677 | 0.028677 | 0.97003 | -0.57915 | 0.97077 | -0.56434 | 7.8784
1 | -0.018708 | -0.0046932 | 0.018719 | 0.0046999 | 1.1092e-05 | 6.6536e-06 | 0.028677 | 0.028677 | 0.028677 | 0.97077 | -0.56434 | 0.9714 | -0.55192 | 7.8783
2 | -0.038167 | -0.009574 | 0.038215 | 0.0096045 | 4.846e-05 | 3.0546e-05 | 0.058468 | 0.058468 | 0.058468 | 0.9714 | -0.55192 | 0.97275 | -0.52532 | 16.0626
3 | -0.038215 | -0.0096045 | 0.038318 | 0.0096692 | 0.00010263 | 6.4687e-05 | 0.058468 | 0.058467 | 0.058468 | 0.97275 | -0.52532 | 0.9756 | -0.46923 | 16.0626
4 | 0.0044592 | 0.0011174 | -0.0044587 | -0.0011174 | 4.8532e-07 | -3.8715e-08 | 0.0068012 | 0.0068013 | 0.0068013 | 0.9756 | -0.46923 | 0.97548 | -0.47151 | 1.8685
5 | -0.042777 | -0.010787 | 0.042867 | 0.010843 | 8.9587e-05 | 5.6634e-05 | 0.065269 | 0.065268 | 0.065269 | 0.9756 | -0.46923 | 0.97783 | -0.42557 | 17.9309
6 | -0.029059 | -0.0072829 | 0.029087 | 0.0073 | 2.7365e-05 | 1.7051e-05 | 0.044367 | 0.044367 | 0.044367 | 0.97461 | -0.48901 | 0.97561 | -0.46926 | 12.1888
7 | -0.038424 | -0.0096399 | 0.03843 | 0.0096442 | 6.8977e-06 | 4.3476e-06 | 0.058608 | 0.058608 | 0.058608 | 0.97561 | -0.46926 | 0.9758 | -0.4655 | 16.1011
8 | 0.009337 | 0.0023399 | -0.0093362 | -0.0023396 | 7.4019e-07 | 3.522e-07 | 0.014241 | 0.014241 | 0.014241 | 0.97561 | -0.46926 | 0.97552 | -0.47092 | 3.9123
9 | -0.10064 | -0.025372 | 0.10091 | 0.025542 | 0.0002671 | 0.00017056 | 0.15321 | 0.15321 | 0.15321 | 0.97783 | -0.42557 | 0.98067 | -0.37027 | 42.0904
10 | 0.057778 | 0.014528 | -0.057736 | -0.014502 | 4.2028e-05 | 2.6716e-05 | 0.087941 | 0.087941 | 0.087941 | 0.97783 | -0.42557 | 0.97706 | -0.44081 | 24.1595
11 | 0.016281 | 0.0040856 | -0.016271 | -0.00408 | 9.4774e-06 | 5.5607e-06 | 0.024913 | 0.024913 | 0.024913 | 0.97248 | -0.53076 | 0.97186 | -0.54298 | 6.8443
12 | -0.01883 | -0.0047238 | 0.018835 | 0.0047271 | 5.3599e-06 | 3.2167e-06 | 0.028813 | 0.028813 | 0.028813 | 0.97248 | -0.53076 | 0.97278 | -0.5248 | 7.9158
13 | 0.0025491 | 0.00063829 | -0.0025488 | -0.00063879 | 3.2779e-07 | -5.03e-07 | 0.0039003 | 0.0039005 | 0.0039005 | 0.97248 | -0.53076 | 0.97234 | -0.53346 | 1.0716
14 | 0.016271 | 0.00408 | -0.016265 | -0.0040764 | 6.1836e-06 | 3.6284e-06 | 0.024913 | 0.024913 | 0.024913 | 0.97186 | -0.54298 | 0.97146 | -0.55096 | 6.8444
15 | -0.029013 | -0.0072779 | 0.029036 | 0.0072925 | 2.3358e-05 | 1.4556e-05 | 0.044382 | 0.044382 | 0.044382 | 0.97278 | -0.5248 | 0.97364 | -0.50792 | 12.1929
16 | -0.10319 | -0.026114 | 0.10328 | 0.026167 | 8.3529e-05 | 5.3344e-05 | 0.15667 | 0.15667 | 0.15667 | 0.98067 | -0.37027 | 0.98153 | -0.35342 | 43.0409
17 | 0.0065922 | 0.001652 | -0.0065917 | -0.0016519 | 4.8899e-07 | 1.5094e-07 | 0.01004 | 0.01004 | 0.01004 | 0.97706 | -0.44081 | 0.97698 | -0.44237 | 2.7581
18 | 0.0079957 | 0.0020039 | -0.007995 | -0.0020036 | 7.2041e-07 | 2.9882e-07 | 0.012177 | 0.012177 | 0.012177 | 0.97706 | -0.44081 | 0.97696 | -0.4427 | 3.3454
19 | 0.043148 | 0.010846 | -0.043097 | -0.010814 | 5.0786e-05 | 3.2111e-05 | 0.065724 | 0.065724 | 0.065724 | 0.97706 | -0.44081 | 0.9758 | -0.4655 | 18.0561
20 | -0.002578 | -0.00064612 | 0.0025781 | 0.00064602 | 6.7528e-08 | -1.0096e-07 | 0.0039407 | 0.0039406 | 0.0039407 | 0.97348 | -0.51097 | 0.97351 | -0.51042 | 1.0826
21 | -0.0076228 | -0.0019099 | 0.0076237 | 0.0019103 | 9.0675e-07 | 3.5882e-07 | 0.011651 | 0.011651 | 0.011651 | 0.97351 | -0.51042 | 0.97364 | -0.50792 | 3.2009
22 | 0.0050447 | 0.0012639 | -0.0050443 | -0.0012639 | 4.0475e-07 | 3.3344e-08 | 0.0077107 | 0.0077107 | 0.0077107 | 0.97351 | -0.51042 | 0.97343 | -0.5121 | 2.1183
23 | -0.03666 | -0.0092028 | 0.03668 | 0.0092153 | 1.9947e-05 | 1.2556e-05 | 0.056033 | 0.056033 | 0.056033 | 0.97364 | -0.50792 | 0.97422 | -0.49652 | 15.3937
24 | -0.0025586 | -0.00064123 | 0.0025586 | 0.0006411 | 8.4717e-08 | -1.2933e-07 | 0.0039114 | 0.0039113 | 0.0039114 | 0.97335 | -0.51362 | 0.97339 | -0.51292 | 1.0746
25 | -0.0025586 | -0.0006411 | 0.0025587 | 0.00064095 | 9.9937e-08 | -1.5259e-07 | 0.0039113 | 0.0039113 | 0.0039113 | 0.97339 | -0.51292 | 0.97343 | -0.5121 | 1.0745
26 | -0.045942 | -0.011538 | 0.045943 | 0.011539 | 1.689e-06 | 1.0696e-06 | 0.070226 | 0.070226 | 0.070226 | 0.97357 | -0.50932 | 0.97361 | -0.50855 | 19.2929
27 | 0.038317 | 0.009627 | -0.038292 | -0.0096114 | 2.4735e-05 | 1.5591e-05 | 0.058573 | 0.058573 | 0.058573 | 0.97357 | -0.50932 | 0.97289 | -0.52285 | 16.0914
28 | -0.050753 | -0.012744 | 0.050823 | 0.012789 | 7.0016e-05 | 4.4424e-05 | 0.077577 | 0.077577 | 0.077577 | 0.97361 | -0.50855 | 0.97508 | -0.47968 | 21.3124
29 | 0.022373 | 0.0056197 | -0.022351 | -0.0056062 | 2.2155e-05 | 1.3554e-05 | 0.034223 | 0.034224 | 0.034224 | 0.97289 | -0.52285 | 0.97184 | -0.54363 | 9.4021
30 | 0.01592 | 0.0039916 | -0.015914 | -0.0039886 | 5.1735e-06 | 3.0222e-06 | 0.024349 | 0.024349 | 0.024349 | 0.97289 | -0.52285 | 0.97254 | -0.52968 | 6.6894
31 | 0.019738 | 0.0049483 | -0.019734 | -0.0049457 | 4.2203e-06 | 2.5463e-06 | 0.030122 | 0.030122 | 0.030122 | 0.97508 | -0.47968 | 0.97485 | -0.48417 | 8.2752
32 | -0.070561 | -0.017737 | 0.070723 | 0.01784 | 0.00016152 | 0.00010291 | 0.1077 | 0.1077 | 0.1077 | 0.97508 | -0.47968 | 0.97752 | -0.43185 | 29.5875
33 | 0.012577 | 0.0031533 | -0.012574 | -0.0031512 | 3.8476e-06 | 2.1198e-06 | 0.019258 | 0.019258 | 0.019258 | 0.97184 | -0.54363 | 0.97151 | -0.55005 | 5.2907
34 | 0.0097733 | 0.0024528 | -0.0097655 | -0.002449 | 7.7721e-06 | 3.8286e-06 | 0.014965 | 0.014966 | 0.014966 | 0.97184 | -0.54363 | 0.97099 | -0.56031 | 4.1115
35 | 0.0049119 | 0.001231 | -0.0049116 | -0.001231 | 3.3144e-07 | 1.796e-08 | 0.0075154 | 0.0075154 | 0.0075154 | 0.97254 | -0.52968 | 0.97247 | -0.53109 | 2.0647
36 | 0.011002 | 0.0027576 | -0.011002 | -0.0027572 | 8.7738e-07 | 4.5908e-07 | 0.016834 | 0.016834 | 0.016834 | 0.97254 | -0.52968 | 0.97246 | -0.53135 | 4.6247
37 | -0.070723 | -0.01784 | 0.070752 | 0.017859 | 2.9134e-05 | 1.8562e-05 | 0.1077 | 0.1077 | 0.1077 | 0.97752 | -0.43185 | 0.97796 | -0.42325 | 29.5875
38 | 0.0097655 | 0.002449 | -0.0097586 | -0.0024456 | 6.9051e-06 | 3.4032e-06 | 0.014966 | 0.014966 | 0.014966 | 0.97099 | -0.56031 | 0.97024 | -0.57516 | 4.1116
39 | 0.0048906 | 0.0012256 | -0.0048903 | -0.0012256 | 3.2027e-07 | 1.5778e-08 | 0.0074834 | 0.0074834 | 0.0074834 | 0.97246 | -0.53135 | 0.97239 | -0.53273 | 2.0559
40 | -0.092508 | -0.023313 | 0.092786 | 0.02349 | 0.00027833 | 0.00017766 | 0.1408 | 0.1408 | 0.1408 | 0.97796 | -0.42325 | 0.98117 | -0.36057 | 38.6817
41 | 0.021756 | 0.0054542 | -0.02175 | -0.0054507 | 5.6428e-06 | 3.4391e-06 | 0.033103 | 0.033103 | 0.033103 | 0.97796 | -0.42325 | 0.97768 | -0.4287 | 9.0943
42 | -0.11177 | -0.028252 | 0.11188 | 0.028326 | 0.00011606 | 7.3736e-05 | 0.16959 | 0.16959 | 0.16959 | 0.98117 | -0.36057 | 0.98228 | -0.33894 | 23.2951
43 | 0.01898 | 0.0047614 | -0.018974 | -0.0047578 | 6.0491e-06 | 3.6257e-06 | 0.028787 | 0.028787 | 0.028787 | 0.98117 | -0.36057 | 0.98083 | -0.36726 | 7.9085
44 | 0.01321 | 0.0033103 | -0.013207 | -0.0033088 | 2.7922e-06 | 1.5561e-06 | 0.020105 | 0.020105 | 0.020105 | 0.97768 | -0.4287 | 0.97745 | -0.43314 | 5.5234
45 | 0.013207 | 0.0033088 | -0.013205 | -0.0033078 | 1.7567e-06 | 9.7906e-07 | 0.020105 | 0.020105 | 0.020105 | 0.97745 | -0.43314 | 0.97731 | -0.43593 | 5.5235
46 | 0.0069126 | 0.0017307 | -0.0069109 | -0.0017301 | 1.6221e-06 | 5.489e-07 | 0.010524 | 0.010524 | 0.010524 | 0.97731 | -0.43593 | 0.97706 | -0.44086 | 2.8913
47 | 0.0031373 | 0.0007855 | -0.0031366 | -0.0007861 | 7.2649e-07 | -5.9609e-07 | 0.0047794 | 0.0047798 | 0.0047798 | 0.9767 | -0.44801 | 0.97645 | -0.45287 | 1.3131
48 | -0.0031373 | -0.0007855 | 0.0031384 | 0.00078463 | 1.0667e-06 | -8.7649e-07 | 0.0047794 | 0.0047789 | 0.0047794 | 0.9767 | -0.44801 | 0.97706 | -0.44086 | 1.313
49 | 0.099097 | 0.025139 | -0.09898 | -0.025064 | 0.00011692 | 7.4651e-05 | 0.14985 | 0.14985 | 0.14985 | 0.98476 | -0.29078 | 0.98349 | -0.31535 | 41.1672
50 | -0.099097 | -0.025139 | 0.099386 | 0.025324 | 0.00028958 | 0.00018489 | 0.14985 | 0.14985 | 0.14985 | 0.98476 | -0.29078 | 0.9879 | -0.2302 | 41.1672
51 | 0.0088754 | 0.0022245 | -0.0088744 | -0.002224 | 1.027e-06 | 4.6459e-07 | 0.013428 | 0.013429 | 0.013429 | 0.98349 | -0.31535 | 0.98336 | -0.31778 | 3.6892
52 | 0.090104 | 0.02284 | -0.090023 | -0.022788 | 8.0887e-05 | 5.1621e-05 | 0.13642 | 0.13642 | 0.13642 | 0.98349 | -0.31535 | 0.98252 | -0.33405 | 37.4781
53 | -0.10195 | -0.025967 | 0.10209 | 0.026055 | 0.00013706 | 8.752e-05 | 0.15371 | 0.15371 | 0.15371 | 0.9879 | -0.2302 | 0.98935 | -0.20237 | 42.229
54 | 0.043457 | 0.010935 | -0.043433 | -0.01092 | 2.4059e-05 | 1.5216e-05 | 0.066297 | 0.066297 | 0.066297 | 0.97561 | -0.46909 | 0.97502 | -0.48068 | 18.2135
55 | -0.043457 | -0.010935 | 0.043475 | 0.010947 | 1.8423e-05 | 1.1651e-05 | 0.066297 | 0.066297 | 0.066297 | 0.97561 | -0.46909 | 0.97606 | -0.46022 | 18.2134
56 | 0.043433 | 0.01092 | -0.0434 | -0.010899 | 3.2828e-05 | 2.0762e-05 | 0.066297 | 0.066297 | 0.066297 | 0.97502 | -0.48068 | 0.97422 | -0.49652 | 18.2135
57 | -0.046028 | -0.011587 | 0.04604 | 0.011595 | 1.2183e-05 | 7.7146e-06 | 0.070189 | 0.070189 | 0.070189 | 0.97606 | -0.46022 | 0.97635 | -0.45469 | 19.2826
58 | 0.0048891 | 0.0012252 | -0.0048883 | -0.0012251 | 7.4623e-07 | 4.054e-08 | 0.0074981 | 0.0074983 | 0.0074983 | 0.97024 | -0.57516 | 0.97008 | -0.57836 | 2.06
59 | 0.011721 | 0.002938 | -0.011719 | -0.002937 | 1.8039e-06 | 9.5829e-07 | 0.017685 | 0.017685 | 0.017685 | 0.98619 | -0.2634 | 0.98602 | -0.26663 | 4.8585
60 | -0.016602 | -0.0041615 | 0.016615 | 0.0041687 | 1.243e-05 | 7.2806e-06 | 0.025051 | 0.025051 | 0.025051 | 0.98619 | -0.2634 | 0.987 | -0.2477 | 6.8821
61 | 0.0048819 | 0.0012235 | -0.0048818 | -0.0012235 | 1.3042e-07 | 1.688e-09 | 0.0073661 | 0.0073662 | 0.0073662 | 0.98619 | -0.2634 | 0.98616 | -0.26396 | 2.0237
62 | -0.36631 | -0.092932 | 0.36678 | 0.093235 | 0.00047561 | 0.00030306 | 0.55265 | 0.55265 | 0.55265 | 0.987 | -0.2477 | 0.9884 | -0.22074 | 30.3657
63 | 0.034357 | 0.0086225 | -0.034336 | -0.008609 | 2.1503e-05 | 1.3489e-05 | 0.051802 | 0.051802 | 0.051802 | 0.987 | -0.2477 | 0.98632 | -0.26083 | 14.2314
64 | 0.31533 | 0.08014 | -0.31505 | -0.079959 | 0.00028491 | 0.00018127 | 0.4758 | 0.4758 | 0.4758 | 0.987 | -0.2477 | 0.98602 | -0.26648 | 26.143
65 | 0.0084109 | 0.0021078 | -0.0084106 | -0.0021077 | 2.6245e-07 | 1.1256e-07 | 0.012693 | 0.012693 | 0.012693 | 0.98602 | -0.26648 | 0.98599 | -0.26713 | 3.4871
66 | 0.30664 | 0.077851 | -0.30632 | -0.077651 | 0.00031512 | 0.00020043 | 0.46311 | 0.46311 | 0.46311 | 0.98602 | -0.26648 | 0.98492 | -0.28786 | 25.4456
67 | 0.0041939 | 0.0010509 | -0.0041936 | -0.001051 | 3.7892e-07 | -7.9164e-08 | 0.0063293 | 0.0063294 | 0.0063294 | 0.98599 | -0.26713 | 0.98589 | -0.26903 | 1.7388
68 | 0.0042167 | 0.0010568 | -0.0042166 | -0.0010568 | 3.8379e-08 | -7.6702e-09 | 0.0063637 | 0.0063637 | 0.0063637 | 0.98599 | -0.26713 | 0.98598 | -0.26733 | 1.7483
69 | 0.30049 | 0.076189 | -0.30038 | -0.076117 | 0.00011309 | 7.1914e-05 | 0.4543 | 0.4543 | 0.4543 | 0.98492 | -0.28786 | 0.98451 | -0.29569 | 24.9613
70 | -0.3702 | -0.094092 | 0.37072 | 0.094423 | 0.00051884 | 0.00033063 | 0.55781 | 0.55781 | 0.55781 | 0.9884 | -0.22074 | 0.98991 | -0.19168 | 30.6487
71 | 0.021002 | 0.0052672 | -0.020993 | -0.0052618 | 8.8211e-06 | 5.3466e-06 | 0.031686 | 0.031686 | 0.031686 | 0.98632 | -0.26083 | 0.98587 | -0.26965 | 8.7049
72 | 0.012328 | 0.0030903 | -0.012326 | -0.003089 | 2.4454e-06 | 1.3284e-06 | 0.018675 | 0.018675 | 0.018675 | 0.98228 | -0.33894 | 0.98207 | -0.3431 | 5.1306
73 | -0.12421 | -0.031416 | 0.12426 | 0.031448 | 4.9789e-05 | 3.1675e-05 | 0.18826 | 0.18826 | 0.18826 | 0.98228 | -0.33894 | 0.98271 | -0.33059 | 25.8603
74 | 0.015337 | 0.0038462 | -0.015331 | -0.0038427 | 6.1201e-06 | 3.5366e-06 | 0.023269 | 0.023269 | 0.023269 | 0.98083 | -0.36726 | 0.9804 | -0.37563 | 6.3926
75 | -0.015626 | -0.0039163 | 0.015628 | 0.0039171 | 1.3252e-06 | 7.6716e-07 | 0.023588 | 0.023588 | 0.023588 | 0.98578 | -0.27143 | 0.98587 | -0.26965 | 6.4801
76 | 0.0066756 | 0.001673 | -0.0066753 | -0.0016729 | 2.4865e-07 | 7.6698e-08 | 0.010101 | 0.010101 | 0.010101 | 0.98336 | -0.31778 | 0.98332 | -0.31856 | 2.7751
77 | 0.087759 | 0.022221 | -0.087594 | -0.022115 | 0.0001658 | 0.00010579 | 0.13299 | 0.13299 | 0.13299 | 0.98252 | -0.33405 | 0.9805 | -0.37347 | 36.5361
78 | 0.017271 | 0.0043317 | -0.017267 | -0.004329 | 4.5119e-06 | 2.6588e-06 | 0.025977 | 0.025978 | 0.025978 | 0.98935 | -0.20237 | 0.98907 | -0.20786 | 7.1367
79 | -0.11936 | -0.030386 | 0.11942 | 0.030426 | 6.1595e-05 | 3.9355e-05 | 0.17969 | 0.17969 | 0.17969 | 0.98935 | -0.20237 | 0.98991 | -0.19168 | 49.3656
80 | -0.0022894 | -0.00057378 | 0.0022894 | 0.00057371 | 3.0043e-08 | -6.4392e-08 | 0.0034753 | 0.0034753 | 0.0034753 | 0.98024 | -0.3785 | 0.98025 | -0.37823 | 0.95476
81 | -0.0044913 | -0.0011256 | 0.0044914 | 0.0011256 | 1.1334e-07 | -9.4353e-09 | 0.0068178 | 0.0068177 | 0.0068178 | 0.98025 | -0.37823 | 0.98028 | -0.3777 | 1.873
82 | 0.0067199 | 0.0016841 | -0.0067194 | -0.001684 | 4.8735e-07 | 1.5831e-07 | 0.010264 | 0.010264 | 0.010264 | 0.97422 | -0.49652 | 0.97414 | -0.49804 | 2.8198
83 | -0.048519 | -0.012216 | 0.048533 | 0.012224 | 1.3336e-05 | 8.4536e-06 | 0.073967 | 0.073967 | 0.073967 | 0.97635 | -0.45469 | 0.97664 | -0.44894 | 20.3206
84 | -0.002273 | -0.00056968 | 0.0022731 | 0.00056961 | 2.9312e-08 | -6.5035e-08 | 0.0034398 | 0.0034398 | 0.0034398 | 0.98328 | -0.31935 | 0.9833 | -0.31908 | 0.94501
85 | -0.0044756 | -0.0011216 | 0.0044757 | 0.0011216 | 1.1179e-07 | -1.0892e-08 | 0.0067728 | 0.0067728 | 0.0067728 | 0.9833 | -0.31908 | 0.98332 | -0.31856 | 1.8607
86 | 0.1662 | 0.042073 | -0.16617 | -0.042055 | 2.8229e-05 | 1.7688e-05 | 0.25134 | 0.25134 | 0.25134 | 0.98451 | -0.29569 | 0.98433 | -0.29923 | 13.8101
87 | 0.13418 | 0.034044 | -0.13406 | -0.033972 | 0.00011601 | 7.1863e-05 | 0.20295 | 0.20295 | 0.20295 | 0.98451 | -0.29569 | 0.98358 | -0.31369 | 11.1512
88 | -0.49015 | -0.12485 | 0.49117 | 0.1255 | 0.0010212 | 0.00065197 | 0.7375 | 0.7375 | 0.7375 | 0.98991 | -0.19168 | 0.99216 | -0.14858 | 40.5218
89 | 0.0046667 | 0.0011695 | -0.0046663 | -0.0011695 | 4.2386e-07 | -7.5122e-09 | 0.0071163 | 0.0071164 | 0.0071164 | 0.9758 | -0.4655 | 0.9757 | -0.4674 | 1.9551
90 | 0.0044494 | 0.0011148 | -0.0044492 | -0.0011148 | 2.3747e-07 | -1.9654e-08 | 0.0067868 | 0.0067869 | 0.0067869 | 0.97552 | -0.47092 | 0.97547 | -0.47204 | 1.8645
91 | 0.0044492 | 0.0011148 | -0.004449 | -0.0011148 | 2.0635e-07 | -1.706e-08 | 0.0067869 | 0.0067869 | 0.0067869 | 0.97547 | -0.47204 | 0.97542 | -0.47302 | 1.8645
92 | 0.0021552 | 0.00053996 | -0.0021551 | -0.00054013 | 6.8068e-08 | -1.6738e-07 | 0.0032825 | 0.0032826 | 0.0032826 | 0.97698 | -0.44237 | 0.97694 | -0.44303 | 0.9018
93 | 0.0059531 | 0.0014919 | -0.0059529 | -0.0014918 | 2.1369e-07 | 4.9976e-08 | 0.0090672 | 0.0090672 | 0.0090672 | 0.97696 | -0.4427 | 0.97692 | -0.44346 | 2.491
94 | 0.0020183 | 0.00050566 | -0.0020182 | -0.00050582 | 5.6237e-08 | -1.6146e-07 | 0.0030789 | 0.003079 | 0.003079 | 0.97542 | -0.47302 | 0.97539 | -0.4736 | 0.84587
95 | 0.0040061 | 0.0010039 | -0.004006 | -0.0010039 | 1.015e-07 | -2.6057e-08 | 0.0061019 | 0.0061019 | 0.0061019 | 0.97692 | -0.44346 | 0.97689 | -0.44399 | 1.6764
96 | 0.0020491 | 0.00051349 | -0.0020491 | -0.00051356 | 2.5397e-08 | -7.0779e-08 | 0.0031213 | 0.0031213 | 0.0031213 | 0.97689 | -0.44399 | 0.97688 | -0.44425 | 0.8575
97 | 0.013692 | 0.0034327 | -0.01369 | -0.0034316 | 2.0042e-06 | 1.1259e-06 | 0.020757 | 0.020757 | 0.020757 | 0.98153 | -0.35342 | 0.98138 | -0.35649 | 5.7025
98 | -0.11697 | -0.0296 | 0.11707 | 0.029665 | 0.00010181 | 6.5052e-05 | 0.17743 | 0.17743 | 0.17743 | 0.98153 | -0.35342 | 0.98247 | -0.3353 | 48.7434
99 | -0.012963 | -0.0032486 | 0.012965 | 0.00325 | 2.59e-06 | 1.4353e-06 | 0.019734 | 0.019734 | 0.019734 | 0.97743 | -0.43351 | 0.97764 | -0.42932 | 5.4214
100 | 0.0033656 | 0.00084333 | -0.0033655 | -0.00084335 | 4.0092e-08 | -2.5385e-08 | 0.0051236 | 0.0051236 | 0.0051236 | 0.97743 | -0.43351 | 0.97741 | -0.43376 | 1.4076
101 | -0.01797 | -0.0045043 | 0.017974 | 0.0045066 | 3.7655e-06 | 2.2416e-06 | 0.027351 | 0.027351 | 0.027351 | 0.97764 | -0.42932 | 0.97786 | -0.42492 | 7.5141
102 | 0.0033655 | 0.00084335 | -0.0033654 | -0.00084345 | 1.4516e-07 | -9.1899e-08 | 0.0051236 | 0.0051237 | 0.0051237 | 0.97741 | -0.43376 | 0.97737 | -0.43466 | 1.4076
103 | 0.058283 | 0.014693 | -0.058234 | -0.014662 | 4.932e-05 | 3.1355e-05 | 0.08872 | 0.08872 | 0.08872 | 0.97786 | -0.42492 | 0.97696 | -0.44262 | 24.3736
104 | -0.076257 | -0.0192 | 0.076352 | 0.019261 | 9.5323e-05 | 6.077e-05 | 0.11607 | 0.11607 | 0.11607 | 0.97786 | -0.42492 | 0.9792 | -0.39881 | 31.8877
105 | 0.053395 | 0.013449 | -0.053379 | -0.013439 | 1.6132e-05 | 1.0243e-05 | 0.08135 | 0.08135 | 0.08135 | 0.97696 | -0.44262 | 0.97664 | -0.44894 | 22.349
106 | -0.078607 | -0.019826 | 0.078702 | 0.019887 | 9.5455e-05 | 6.0866e-05 | 0.1195 | 0.1195 | 0.1195 | 0.9792 | -0.39881 | 0.9805 | -0.37347 | 32.8292
107 | -0.0033088 | -0.00082926 | 0.0033089 | 0.0008292 | 8.4253e-08 | -5.5566e-08 | 0.0050544 | 0.0050543 | 0.0050544 | 0.97411 | -0.49858 | 0.97414 | -0.49804 | 1.3886
108 | 0.0088912 | 0.0022285 | -0.0088897 | -0.0022279 | 1.4557e-06 | 6.6281e-07 | 0.013493 | 0.013494 | 0.013494 | 0.9805 | -0.37347 | 0.98032 | -0.37691 | 3.707
109 | 0.014386 | 0.0036056 | -0.014385 | -0.003605 | 1.0171e-06 | 5.7515e-07 | 0.021538 | 0.021538 | 0.021538 | 0.99389 | -0.11634 | 0.99381 | -0.11783 | 5.9171
110 | -0.023257 | -0.0058288 | 0.023259 | 0.0058303 | 2.5032e-06 | 1.5307e-06 | 0.034819 | 0.034819 | 0.034819 | 0.99389 | -0.11634 | 0.99401 | -0.11408 | 9.5657
111 | 0.005976 | 0.0014975 | -0.0059755 | -0.0014974 | 5.3544e-07 | 1.1162e-07 | 0.0089477 | 0.0089477 | 0.0089477 | 0.99381 | -0.11783 | 0.99372 | -0.11971 | 2.4582
112 | -0.026485 | -0.0066385 | 0.026496 | 0.0066453 | 1.0949e-05 | 6.7666e-06 | 0.039647 | 0.039647 | 0.039647 | 0.99401 | -0.11408 | 0.99446 | -0.10541 | 10.8922
113 | 0.0032254 | 0.00080819 | -0.0032253 | -0.00080833 | 1.5777e-07 | -1.3294e-07 | 0.0048283 | 0.0048284 | 0.0048284 | 0.99401 | -0.11408 | 0.99395 | -0.11511 | 1.3265
114 | 0.0030753 | 0.00077061 | -0.0030752 | -0.00077072 | 1.0589e-07 | -1.0472e-07 | 0.004605 | 0.0046051 | 0.0046051 | 0.99372 | -0.11971 | 0.99368 | -0.12043 | 1.2651
115 | 0.0029001 | 0.0007268 | -0.0029001 | -0.00072684 | 3.4324e-08 | -4.0906e-08 | 0.0043427 | 0.0043428 | 0.0043428 | 0.99372 | -0.11971 | 0.9937 | -0.11996 | 1.1931
116 | -0.031483 | -0.0078953 | 0.031492 | 0.0079009 | 9.0341e-06 | 5.641e-06 | 0.04711 | 0.04711 | 0.04711 | 0.99446 | -0.10541 | 0.99477 | -0.099392 | 12.9424
117 | 0.01315 | 0.0032967 | -0.013146 | -0.0032947 | 3.6733e-06 | 2.0223e-06 | 0.01967 | 0.01967 | 0.01967 | 0.99477 | -0.099392 | 0.99446 | -0.10526 | 5.4039
118 | -0.044642 | -0.011198 | 0.044668 | 0.011214 | 2.6572e-05 | 1.68e-05 | 0.06678 | 0.06678 | 0.06678 | 0.99477 | -0.099392 | 0.99541 | -0.086913 | 18.3463
119 | 0.0072104 | 0.0018071 | -0.00721 | -0.001807 | 3.9876e-07 | 1.3669e-07 | 0.010789 | 0.010789 | 0.010789 | 0.99446 | -0.10526 | 0.9944 | -0.10642 | 2.964
120 | -0.052036 | -0.013061 | 0.052066 | 0.01308 | 2.9923e-05 | 1.8979e-05 | 0.077794 | 0.077794 | 0.077794 | 0.99541 | -0.086913 | 0.99604 | -0.074864 | 21.3719
121 | 0.52369 | 0.13436 | -0.52364 | -0.13432 | 4.9594e-05 | 3.167e-05 | 0.78347 | 0.78347 | 0.78347 | 0.99604 | -0.074864 | 0.99594 | -0.076816 | 43.0477
122 | -0.57576 | -0.14744 | 0.57742 | 0.1485 | 0.0016662 | 0.0010644 | 0.86126 | 0.86126 | 0.86126 | 0.99604 | -0.074864 | 0.99919 | -0.01531 | 47.322
123 | 0.51567 | 0.13233 | -0.51459 | -0.13164 | 0.0010792 | 0.00068915 | 0.77155 | 0.77155 | 0.77155 | 0.99594 | -0.076816 | 0.99366 | -0.12005 | 42.3931
124 | -0.58449 | -0.15027 | 0.58492 | 0.15055 | 0.00043522 | 0.00027804 | 0.87178 | 0.87178 | 0.87178 | 0.99919 | -0.01531 | 1 | 0 | 47.9
125 | -0.0096567 | -0.0024202 | 0.0096574 | 0.0024205 | 6.8863e-07 | 3.2715e-07 | 0.014467 | 0.014467 | 0.014467 | 0.99327 | -0.12742 | 0.99335 | -0.12592 | 3.9744
126 | -0.50543 | -0.12929 | 0.50557 | 0.12938 | 0.00014378 | 9.1803e-05 | 0.75805 | 0.75805 | 0.75805 | 0.99335 | -0.12592 | 0.99366 | -0.12005 | 41.6512
127 | 0.49577 | 0.12686 | -0.49523 | -0.12652 | 0.00054323 | 0.00034682 | 0.74358 | 0.74359 | 0.74359 | 0.99335 | -0.12592 | 0.99216 | -0.14858 | 40.8563
128 | 0.013995 | 0.0035089 | -0.013992 | -0.0035077 | 2.2559e-06 | 1.2697e-06 | 0.021055 | 0.021055 | 0.021055 | 0.98907 | -0.20786 | 0.98889 | -0.21124 | 5.7843
129 | 0.013992 | 0.0035077 | -0.013989 | -0.0035061 | 2.7777e-06 | 1.5634e-06 | 0.021055 | 0.021055 | 0.021055 | 0.98889 | -0.21124 | 0.98868 | -0.21541 | 5.7843
130 | 0.16617 | 0.042055 | -0.16612 | -0.042024 | 4.9219e-05 | 3.084e-05 | 0.25134 | 0.25134 | 0.25134 | 0.98433 | -0.29923 | 0.98401 | -0.30541 | 13.8101
131 | 0.13023 | 0.033011 | -0.13023 | -0.033009 | 2.0392e-06 | 1.2607e-06 | 0.19715 | 0.19715 | 0.19715 | 0.98358 | -0.31369 | 0.98356 | -0.31401 | 10.8324
132 | 0.16119 | 0.040788 | -0.16111 | -0.040742 | 7.4179e-05 | 4.6419e-05 | 0.24389 | 0.24389 | 0.24389 | 0.98401 | -0.30541 | 0.98352 | -0.315 | 13.4004
133 | 0.12797 | 0.032444 | -0.12795 | -0.032432 | 1.9774e-05 | 1.2209e-05 | 0.19374 | 0.19374 | 0.19374 | 0.98356 | -0.31401 | 0.9834 | -0.31723 | 10.6449
134 | 0.15547 | 0.039328 | -0.15536 | -0.039254 | 0.00011617 | 7.4068e-05 | 0.23535 | 0.23535 | 0.23535 | 0.98352 | -0.315 | 0.98271 | -0.33059 | 32.3285
135 | 0.12526 | 0.031757 | -0.12524 | -0.031749 | 1.2648e-05 | 7.7976e-06 | 0.18966 | 0.18966 | 0.18966 | 0.9834 | -0.31723 | 0.98329 | -0.31933 | 10.421
136 | 0.12068 | 0.030606 | -0.12059 | -0.030548 | 9.2578e-05 | 5.8407e-05 | 0.18276 | 0.18276 | 0.18276 | 0.98329 | -0.31933 | 0.98247 | -0.3353 | 16.7365
137 | 0.011879 | 0.0029778 | -0.011877 | -0.002977 | 1.3851e-06 | 7.4261e-07 | 0.018012 | 0.018012 | 0.018012 | 0.98138 | -0.35649 | 0.98125 | -0.35894 | 4.9482
138 | 0.0089109 | 0.0022336 | -0.0089093 | -0.0022328 | 1.5664e-06 | 7.136e-07 | 0.013513 | 0.013513 | 0.013513 | 0.98125 | -0.35894 | 0.98106 | -0.36263 | 3.7124
139 | 0.0050636 | 0.001269 | -0.0050634 | -0.001269 | 1.8802e-07 | 1.3002e-08 | 0.0076801 | 0.0076801 | 0.0076801 | 0.98106 | -0.36263 | 0.98102 | -0.36341 | 2.1099
140 | 0.0042027 | 0.0010532 | -0.0042026 | -0.0010533 | 1.0248e-07 | -1.9685e-08 | 0.0063678 | 0.0063679 | 0.0063679 | 0.98207 | -0.3431 | 0.98204 | -0.34361 | 1.7494
141 | 0.031095 | 0.0078063 | -0.031074 | -0.0077932 | 2.0904e-05 | 1.306e-05 | 0.047089 | 0.047089 | 0.047089 | 0.98271 | -0.33059 | 0.98199 | -0.34469 | 12.9365
142 | 0.0096482 | 0.0024184 | -0.0096463 | -0.0024175 | 1.9359e-06 | 9.3549e-07 | 0.014644 | 0.014644 | 0.014644 | 0.9804 | -0.37563 | 0.98019 | -0.37984 | 4.0231
143 | -0.0059588 | -0.0014934 | 0.0059592 | 0.0014935 | 4.6012e-07 | 1.0552e-07 | 0.0090467 | 0.0090467 | 0.0090467 | 0.9801 | -0.38146 | 0.98019 | -0.37984 | 2.4854
144 | 0.003687 | 0.00092396 | -0.0036869 | -0.00092402 | 1.4773e-07 | -6.3939e-08 | 0.0055972 | 0.0055973 | 0.0055973 | 0.98019 | -0.37984 | 0.98014 | -0.38069 | 1.5377
145 | -0.0047612 | -0.0011933 | 0.0047616 | 0.0011933 | 3.4698e-07 | -2.1254e-09 | 0.0072204 | 0.0072204 | 0.0072204 | 0.98121 | -0.35997 | 0.98129 | -0.35844 | 1.9836
146 | -0.010295 | -0.0025801 | 0.010295 | 0.0025802 | 2.0021e-07 | 1.0046e-07 | 0.015612 | 0.015612 | 0.015612 | 0.98129 | -0.35844 | 0.98131 | -0.35803 | 4.2889
147 | -0.018794 | -0.0047103 | 0.018796 | 0.004711 | 1.2023e-06 | 7.196e-07 | 0.028499 | 0.028499 | 0.028499 | 0.98131 | -0.35803 | 0.98138 | -0.35669 | 7.8294
148 | -0.022512 | -0.0056424 | 0.022521 | 0.0056482 | 9.4724e-06 | 5.7883e-06 | 0.034134 | 0.034134 | 0.034134 | 0.98138 | -0.35669 | 0.98183 | -0.34786 | 9.3774
149 | -0.027393 | -0.0068691 | 0.027397 | 0.0068717 | 4.1448e-06 | 2.5716e-06 | 0.041517 | 0.041517 | 0.041517 | 0.98183 | -0.34786 | 0.98199 | -0.34469 | 11.4057
150 | 0.0066904 | 0.0016767 | -0.0066902 | -0.0016766 | 2.5139e-07 | 7.8936e-08 | 0.010155 | 0.010155 | 0.010155 | 0.98032 | -0.37691 | 0.98028 | -0.3777 | 2.7899

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60065 | 0.15408

## res_load
| p_mw | q_mvar
0 | 0.018695 | 0.0046853
1 | 0.019448 | 0.0048741
2 | 0.029059 | 0.0072829
3 | 0.0044587 | 0.0011174
4 | 0.010178 | 0.0025509
5 | 0.0025488 | 0.00063879
6 | 0.0022803 | 0.00057151
7 | 0.002578 | 0.00064612
8 | 0.016265 | 0.0040764
9 | 0.0025586 | 0.00064123
10 | 0.0076246 | 0.0019109
11 | 0.0048098 | 0.0012054
12 | 0.019734 | 0.0049457
13 | 0.012574 | 0.0031512
14 | 0.0049116 | 0.001231
15 | 0.0061109 | 0.0015315
16 | 0.0085402 | 0.0021404
17 | 0.0062928 | 0.0015771
18 | 0.0031366 | 0.0007861
19 | 0.0037726 | 0.00094549
20 | 0.0025661 | 0.00064312
21 | 0.0025528 | 0.00063979
22 | 0.0048695 | 0.0012204
23 | 0.011719 | 0.002937
24 | 0.0048818 | 0.0012235
25 | 0.0058347 | 0.0014623
26 | 0.003422 | 0.00085764
27 | 0.013334 | 0.0033418
28 | 0.0048903 | 0.0012256
29 | 0.0036371 | 0.00091155
30 | 0.0048883 | 0.0012251
31 | 0.015626 | 0.0039163
32 | 0.0053655 | 0.0013447
33 | 0.0021988 | 0.00055107
34 | 0.002264 | 0.00056741
35 | 0.0022894 | 0.00057378
36 | 0.0022019 | 0.00055185
37 | 0.0024791 | 0.00062131
38 | 0.002273 | 0.00056968
39 | 0.0022025 | 0.000552
40 | 0.0041936 | 0.001051
41 | 0.0042166 | 0.0010568
42 | 0.0048868 | 0.0012248
43 | 0.0046663 | 0.0011695
44 | 0.0044365 | 0.0011119
45 | 0.0020418 | 0.00051173
46 | 0.0024307 | 0.00060918
47 | 0.0019468 | 0.00048792
48 | 0.0019569 | 0.00049043
49 | 0.0020491 | 0.00051356
50 | 0.0021551 | 0.00054013
51 | 0.0020182 | 0.00050582
52 | 0.009597 | 0.0024052
53 | 0.0050049 | 0.0012543
54 | 0.0033654 | 0.00084345
55 | 0.0048386 | 0.0012127
56 | 0.0022551 | 0.00056518
57 | 0.0033088 | 0.00082926
58 | 0.0034105 | 0.00085476
59 | 0.0048461 | 0.0012146
60 | 0.0024855 | 0.00062293
61 | 0.0088707 | 0.0022232
62 | 0.008409 | 0.0021075
63 | 0.0049875 | 0.00125
64 | 0.0032253 | 0.00080833
65 | 0.0030752 | 0.00077072
66 | 0.0029001 | 0.00072684
67 | 0.0059356 | 0.0014876
68 | 0.0073675 | 0.0018465
69 | 0.00721 | 0.001807
70 | 0.0079741 | 0.0019985
71 | 0.0070643 | 0.0017705
72 | 0.0096567 | 0.0024202
73 | 0.0090171 | 0.0022599
74 | 0.0040603 | 0.0010176
75 | 0.014079 | 0.0035286
76 | 0.0032721 | 0.00082007
77 | 0.013989 | 0.0035061
78 | 0.0021996 | 0.00055128
79 | 0.0038361 | 0.00096143
80 | 0.0049316 | 0.001236
81 | 0.0022556 | 0.00056532
82 | 0.0056416 | 0.0014139
83 | 0.0026928 | 0.00067488
84 | 0.0045595 | 0.0011427
85 | 0.0035235 | 0.00088308
86 | 0.0018107 | 0.00045381
87 | 0.0029666 | 0.00074349
88 | 0.0038457 | 0.00096383
89 | 0.0050634 | 0.001269
90 | 0.0081228 | 0.0020358
91 | 0.0056829 | 0.0014243
92 | 0.0059588 | 0.0014934
93 | 0.0047612 | 0.0011933
94 | 0.0055337 | 0.0013869
95 | 0.0036869 | 0.00092402
96 | 0.008499 | 0.00213
97 | 0.0037162 | 0.00093138
98 | 0.0048715 | 0.0012209
99 | 0.0036772 | 0.00092159
100 | 0.0042026 | 0.0010533
101 | 0.0021993 | 0.0005512
102 | 0.0021987 | 0.00055106

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1