## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1632-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1632-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1632-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1632-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1632-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1632-3_0_4_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1632-3_0_4_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1632-3_0_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_1632-3_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1632-3_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1632-3_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1632-3_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1632-3_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1632-3_0_4_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1632-3_0_4_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_1632-3_0_4_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1632-3_0_4_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_1632-3_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1632-3_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1632-3_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1632-3_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1632-3_0_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1632-3_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1632-3_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_MV_226_0_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1632-3_0_4_load_0 | 0 | 0.042088 | 0.010548 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1632-3_0_4_load_22 | 6 | 0.080898 | 0.020275 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1632-3_0_4_load_13 | 7 | 0.015172 | 0.0038025 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1632-3_0_4_load_11 | 8 | 0.080413 | 0.020153 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1632-3_0_4_load_21 | 13 | 0.0052111 | 0.001306 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1632-3_0_4_load_23 | 14 | 0.0076432 | 0.0019156 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1632-3_0_4_load_24 | 15 | 0.08905 | 0.022318 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1632-3_0_4_load_18 | 16 | 0.0055435 | 0.0013893 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1632-3_0_4_load_17 | 17 | 0.0040706 | 0.0010202 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1632-3_0_4_load_19 | 21 | 0.00089499 | 0.00022431 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1632-3_0_4_load_20 | 23 | 0.017565 | 0.0044021 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1632-3_0_4_line_0 |  | 0 | 1 | 0.011895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_1632-3_0_4_line_1 |  | 0 | 2 | 0.018034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1632-3_0_4_line_2 |  | 1 | 3 | 0.071596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1632-3_0_4_line_3 |  | 2 | 4 | 0.036627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1632-3_0_4_line_4 |  | 2 | 5 | 0.19499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1632-3_0_4_line_5 |  | 3 | 6 | 0.017141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1632-3_0_4_line_6 |  | 4 | 7 | 0.070314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1632-3_0_4_line_7 |  | 4 | 8 | 0.021561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1632-3_0_4_line_8 |  | 5 | 16 | 0.048376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1632-3_0_4_line_9 |  | 6 | 9 | 0.019716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1632-3_0_4_line_10 |  | 7 | 17 | 0.010168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1632-3_0_4_line_11 |  | 8 | 18 | 0.020411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1632-3_0_4_line_12 |  | 9 | 10 | 0.052959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1632-3_0_4_line_13 |  | 10 | 15 | 0.020053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1632-3_0_4_line_14 |  | 11 | 12 | 0.13192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1632-3_0_4_line_15 |  | 11 | 13 | 0.010248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1632-3_0_4_line_16 |  | 12 | 14 | 0.071651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1632-3_0_4_line_17 |  | 14 | 19 | 0.061498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1632-3_0_4_line_18 |  | 18 | 20 | 0.033441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1632-3_0_4_line_19 |  | 19 | 22 | 0.025041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1632-3_0_4_line_20 |  | 20 | 21 | 0.020142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1632-3_0_4_line_21 |  | 21 | 22 | 0.0028225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1632-3_0_4_line_22 |  | 22 | 23 | 0.032135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1632-3_0_4_trafo_1 | 0.63 MVA 20/0.4 kV | 24 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2723551.288 | 1211714.3084 | 2723540.0591 | 1211710.3839
1 | 2723522.933 | 1211715.5777 | 2723531.8912 | 1211711.7047 | 2723540.0591 | 1211710.3839
2 | 2723551.288 | 1211714.3084 | 2723540.6422 | 1211719.6587 | 2723536.9239 | 1211722.6618 | 2723537.0507 | 1211725.7112 | 2723537.4502 | 1211726.609 | 2723537.8701 | 1211727.9855 | 2723540.4323 | 1211730.8852 | 2723546.032 | 1211734.2927 | 2723552.1116 | 1211736.5426 | 2723562.0799 | 1211739.3067 | 2723565.3105 | 1211741.8645 | 2723581.5416 | 1211749.7735
3 | 2723522.933 | 1211715.5777 | 2723508.8833 | 1211713.8966 | 2723506.6548 | 1211731.9421 | 2723505.7394 | 1211736.1375
4 | 2723522.933 | 1211715.5777 | 2723508.8833 | 1211713.8966 | 2723513.488 | 1211677.286 | 2723515.519 | 1211667.6763 | 2723518.0779 | 1211660.1012 | 2723520.8345 | 1211654.7208 | 2723524.0231 | 1211650.5058 | 2723528.8714 | 1211646.1584 | 2723476.6127 | 1211635.9686 | 2723471.4103 | 1211669.5201 | 2723468.8133 | 1211686.2792 | 2723464.763 | 1211685.4948
5 | 2723581.5416 | 1211749.7735 | 2723583.8742 | 1211743.9507 | 2723584.9909 | 1211738.4807 | 2723585.3815 | 1211733.9408 | 2723585.3127 | 1211733.2156
6 | 2723505.7394 | 1211736.1375 | 2723484.8713 | 1211725.3083 | 2723480.6021 | 1211724.8195 | 2723475.56 | 1211727.1503 | 2723453.7577 | 1211756.9839
7 | 2723505.7394 | 1211736.1375 | 2723504.8992 | 1211740.0009 | 2723502.0853 | 1211746.3141 | 2723498.508 | 1211753.1564 | 2723496.935 | 1211755.6809
8 | 2723464.763 | 1211685.4948 | 2723463.9733 | 1211689.4926 | 2723486.1197 | 1211693.6653 | 2723483.9194 | 1211715.3187
9 | 2723586.1518 | 1211714.0193 | 2723584.3016 | 1211717.4725 | 2723584.1776 | 1211721.2506 | 2723585.3127 | 1211733.2156
10 | 2723447.7585 | 1211765.193 | 2723453.7577 | 1211756.9839
11 | 2723486.1406 | 1211773.0046 | 2723496.935 | 1211755.6809
12 | 2723626.9619 | 1211702.9897 | 2723614.9867 | 1211696.57 | 2723608.0535 | 1211696.2594 | 2723604.7828 | 1211697.1034 | 2723600.1774 | 1211699.2652 | 2723596.2113 | 1211703.2194 | 2723589.7602 | 1211715.9511 | 2723586.1518 | 1211714.0193
13 | 2723626.9619 | 1211702.9897 | 2723626.7081 | 1211704.5968 | 2723625.2951 | 1211706.7581 | 2723623.0653 | 1211708.3576 | 2723618.7385 | 1211711.0144 | 2723615.0713 | 1211718.1495
14 | 2723629.6125 | 1211787.7432 | 2723642.2027 | 1211794.1869 | 2723654.3914 | 1211796.8972 | 2723658.6078 | 1211797.3627 | 2723663.7373 | 1211796.6797 | 2723666.3555 | 1211795.7777 | 2723668.2703 | 1211794.7054 | 2723671.2127 | 1211792.8317 | 2723673.3807 | 1211788.7179 | 2723674.8189 | 1211789.3704 | 2723676.6474 | 1211790.2646 | 2723677.2869 | 1211790.5781 | 2723675.7151 | 1211793.8035 | 2723675.2629 | 1211794.7171 | 2723680.8539 | 1211797.4351 | 2723689.8135 | 1211801.9132 | 2723686.5929 | 1211806.5722 | 2723678.3153 | 1211817.5757 | 2723656.923 | 1211837.5365 | 2723653.9364 | 1211840.4435 | 2723650.5386 | 1211843.7534
15 | 2723629.6125 | 1211787.7432 | 2723620.4874 | 1211783.0801
16 | 2723650.5386 | 1211843.7534 | 2723641.8281 | 1211832.3974 | 2723619.2456 | 1211819.9643 | 2723604.5057 | 1211813.098 | 2723594.2253 | 1211809.9937 | 2723589.8064 | 1211808.8655
17 | 2723529.9077 | 1211794.9387 | 2723584.0334 | 1211807.3916 | 2723589.8064 | 1211808.8655
18 | 2723486.1406 | 1211773.0046 | 2723480.776 | 1211781.3666 | 2723488.7822 | 1211787.4815 | 2723493.9018 | 1211797.1838 | 2723494.9578 | 1211799.4074
19 | 2723515.6458 | 1211809.3767 | 2723522.199 | 1211795.3794 | 2723523.3983 | 1211792.8912 | 2723529.9077 | 1211794.9387
20 | 2723494.9578 | 1211799.4074 | 2723513.1032 | 1211808.1514
21 | 2723515.6458 | 1211809.3767 | 2723513.1032 | 1211808.1514
22 | 2723515.6458 | 1211809.3767 | 2723521.5965 | 1211812.3467 | 2723526.7089 | 1211816.5224 | 2723529.9779 | 1211821.2604 | 2723530.7 | 1211830.4269 | 2723532.1513 | 1211834.1153

## bus_geodata
| x | y | coords
0 | 2723540.0591 | 1211710.3839
1 | 2723551.288 | 1211714.3084
2 | 2723522.933 | 1211715.5777
3 | 2723581.5416 | 1211749.7735
4 | 2723505.7394 | 1211736.1375
5 | 2723464.763 | 1211685.4948
6 | 2723585.3127 | 1211733.2156
7 | 2723453.7577 | 1211756.9839
8 | 2723496.935 | 1211755.6809
9 | 2723586.1518 | 1211714.0193
10 | 2723626.9619 | 1211702.9897
11 | 2723629.6125 | 1211787.7432
12 | 2723650.5386 | 1211843.7534
13 | 2723620.4874 | 1211783.0801
14 | 2723589.8064 | 1211808.8655
15 | 2723615.0713 | 1211718.1495
16 | 2723483.9194 | 1211715.3187
17 | 2723447.7585 | 1211765.193
18 | 2723486.1406 | 1211773.0046
19 | 2723529.9077 | 1211794.9387
20 | 2723494.9578 | 1211799.4074
21 | 2723513.1032 | 1211808.1514
22 | 2723515.6459 | 1211809.3767
23 | 2723532.1513 | 1211834.1153
24 | 2723536.9239 | 1211722.6618

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99903 | -0.018535 | 0.042088 | 0.010548
1 | 1 | 0 | -0.35324 | -0.089286
2 | 0.99677 | -0.061632 | 0 | 0
3 | 0.99442 | -0.10664 | 0 | 0
4 | 0.99237 | -0.14617 | 0 | 0
5 | 0.99579 | -0.080629 | 0 | 0
6 | 0.99308 | -0.13234 | 0.080898 | 0.020275
7 | 0.99114 | -0.17014 | 0.015172 | 0.0038025
8 | 0.99017 | -0.1889 | 0.080413 | 0.020153
9 | 0.99147 | -0.16342 | 0 | 0
10 | 0.98713 | -0.24741 | 0 | 0
11 | 0.98596 | -0.27064 | 0 | 0
12 | 0.98659 | -0.25832 | 0 | 0
13 | 0.98591 | -0.2716 | 0.0052111 | 0.001306
14 | 0.98694 | -0.25163 | 0.0076432 | 0.0019156
15 | 0.98548 | -0.27941 | 0.08905 | 0.022318
16 | 0.99554 | -0.085345 | 0.0055435 | 0.0013893
17 | 0.9911 | -0.17088 | 0.0040706 | 0.0010202
18 | 0.98958 | -0.20028 | 0 | 0
19 | 0.98766 | -0.23748 | 0 | 0
20 | 0.98862 | -0.21894 | 0 | 0
21 | 0.98804 | -0.2302 | 0.00089499 | 0.00022431
22 | 0.98796 | -0.23173 | 0 | 0
23 | 0.98744 | -0.24182 | 0.017565 | 0.0044021
24 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.17976 | -0.045496 | 0.17992 | 0.045598 | 0.00016008 | 0.00010214 | 0.26791 | 0.26791 | 0.26791 | 0.99903 | -0.018535 | 1 | 0 | 36.8007
1 | 0.13768 | 0.034948 | -0.13739 | -0.034766 | 0.00028481 | 0.00018204 | 0.20522 | 0.20522 | 0.20522 | 0.99903 | -0.018535 | 0.99677 | -0.061632 | 56.3795
2 | 0.17166 | 0.043688 | -0.17079 | -0.043128 | 0.00087754 | 0.00055976 | 0.25568 | 0.25568 | 0.25568 | 1 | 0 | 0.99442 | -0.10664 | 35.1203
3 | 0.13184 | 0.033376 | -0.13131 | -0.033035 | 0.0005327 | 0.00034045 | 0.19694 | 0.19694 | 0.19694 | 0.99677 | -0.061632 | 0.99237 | -0.14617 | 54.1035
4 | 0.0055498 | 0.0013902 | -0.0055448 | -0.0013895 | 5.0193e-06 | 6.7322e-07 | 0.0082847 | 0.0082856 | 0.0082856 | 0.99677 | -0.061632 | 0.99579 | -0.080629 | 2.2763
5 | 0.17079 | 0.043128 | -0.17058 | -0.042994 | 0.00021009 | 0.00013401 | 0.25568 | 0.25568 | 0.25568 | 0.99442 | -0.10664 | 0.99308 | -0.13234 | 35.1203
6 | 0.019265 | 0.0048358 | -0.019243 | -0.0048227 | 2.2007e-05 | 1.3177e-05 | 0.028889 | 0.02889 | 0.02889 | 0.99237 | -0.14617 | 0.99114 | -0.17014 | 7.9368
7 | 0.11204 | 0.028199 | -0.11182 | -0.028053 | 0.00022833 | 0.00014585 | 0.16805 | 0.16805 | 0.16805 | 0.99237 | -0.14617 | 0.99017 | -0.1889 | 46.1669
8 | 0.0055448 | 0.0013895 | -0.0055435 | -0.0013893 | 1.2454e-06 | 1.6791e-07 | 0.0082856 | 0.0082858 | 0.0082858 | 0.99579 | -0.080629 | 0.99554 | -0.085345 | 2.2763
9 | 0.089679 | 0.022719 | -0.089545 | -0.022634 | 0.00013367 | 8.5297e-05 | 0.13446 | 0.13446 | 0.13446 | 0.99308 | -0.13234 | 0.99147 | -0.16342 | 36.9396
10 | 0.0040707 | 0.0010201 | -0.0040706 | -0.0010202 | 1.4241e-07 | -3.989e-08 | 0.0061114 | 0.0061115 | 0.0061115 | 0.99114 | -0.17014 | 0.9911 | -0.17088 | 1.679
11 | 0.031404 | 0.0079002 | -0.031387 | -0.0078895 | 1.7055e-05 | 1.0653e-05 | 0.047204 | 0.047204 | 0.047204 | 0.99017 | -0.1889 | 0.98958 | -0.20028 | 12.9681
12 | 0.089545 | 0.022634 | -0.089186 | -0.022405 | 0.00035905 | 0.00022911 | 0.13446 | 0.13446 | 0.13446 | 0.99147 | -0.16342 | 0.98713 | -0.24741 | 36.9396
13 | 0.089186 | 0.022405 | -0.08905 | -0.022318 | 0.00013596 | 8.6756e-05 | 0.13446 | 0.13446 | 0.13446 | 0.98713 | -0.24741 | 0.98548 | -0.27941 | 36.9397
14 | -0.0052113 | -0.001306 | 0.0052144 | 0.0013063 | 3.0598e-06 | 2.7477e-07 | 0.0078649 | 0.0078643 | 0.0078649 | 0.98596 | -0.27064 | 0.98659 | -0.25832 | 2.1607
15 | 0.0052113 | 0.001306 | -0.0052111 | -0.001306 | 2.3771e-07 | 2.1447e-08 | 0.0078649 | 0.007865 | 0.007865 | 0.98596 | -0.27064 | 0.98591 | -0.2716 | 2.1607
16 | -0.0052144 | -0.0013063 | 0.0052161 | 0.0013065 | 1.6617e-06 | 1.4821e-07 | 0.0078643 | 0.007864 | 0.0078643 | 0.98659 | -0.25832 | 0.98694 | -0.25163 | 2.1605
17 | -0.012859 | -0.003222 | 0.012868 | 0.0032268 | 8.6685e-06 | 4.7614e-06 | 0.019388 | 0.019388 | 0.019388 | 0.98694 | -0.25163 | 0.98766 | -0.23748 | 5.3263
18 | 0.031387 | 0.0078895 | -0.031359 | -0.0078721 | 2.7942e-05 | 1.7454e-05 | 0.047204 | 0.047204 | 0.047204 | 0.98958 | -0.20028 | 0.98862 | -0.21894 | 12.9681
19 | -0.012868 | -0.0032268 | 0.012871 | 0.0032287 | 3.5297e-06 | 1.9384e-06 | 0.019388 | 0.019387 | 0.019388 | 0.98766 | -0.23748 | 0.98796 | -0.23173 | 5.3262
20 | 0.031359 | 0.0078721 | -0.031342 | -0.0078615 | 1.6831e-05 | 1.0513e-05 | 0.047204 | 0.047204 | 0.047204 | 0.98862 | -0.21894 | 0.98804 | -0.2302 | 12.9681
21 | 0.030447 | 0.0076372 | -0.030445 | -0.0076358 | 2.2256e-06 | 1.3883e-06 | 0.045856 | 0.045856 | 0.045856 | 0.98804 | -0.2302 | 0.98796 | -0.23173 | 12.5978
22 | 0.017573 | 0.0044071 | -0.017565 | -0.0044021 | 8.4426e-06 | 4.992e-06 | 0.026469 | 0.026469 | 0.026469 | 0.98796 | -0.23173 | 0.98744 | -0.24182 | 7.2717

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35324 | 0.089286

## res_load
| p_mw | q_mvar
0 | 0.042088 | 0.010548
1 | 0.080898 | 0.020275
2 | 0.015172 | 0.0038025
3 | 0.080413 | 0.020153
4 | 0.0052111 | 0.001306
5 | 0.0076432 | 0.0019156
6 | 0.08905 | 0.022318
7 | 0.0055435 | 0.0013893
8 | 0.0040706 | 0.0010202
9 | 0.00089499 | 0.00022431
10 | 0.017565 | 0.0044021

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1