## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1632-47_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1632-47_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1632-47_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1632-47_0_4_node_31 | 0.4 | n |  | TRUE
4 | bus_LV_1632-47_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1632-47_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1632-47_0_4_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_1632-47_0_4_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_1632-47_0_4_node_49 | 0.4 | n |  | TRUE
9 | bus_LV_1632-47_0_4_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_1632-47_0_4_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_1632-47_0_4_node_48 | 0.4 | n |  | TRUE
12 | bus_LV_1632-47_0_4_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_1632-47_0_4_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_1632-47_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1632-47_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1632-47_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1632-47_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1632-47_0_4_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1632-47_0_4_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_1632-47_0_4_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1632-47_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1632-47_0_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1632-47_0_4_node_55 | 0.4 | n |  | TRUE
24 | bus_LV_1632-47_0_4_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_1632-47_0_4_node_11 | 0.4 | n |  | TRUE
26 | bus_LV_1632-47_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_1632-47_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1632-47_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_1632-47_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_1632-47_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_1632-47_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1632-47_0_4_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1632-47_0_4_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_1632-47_0_4_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_1632-47_0_4_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_1632-47_0_4_node_17 | 0.4 | n |  | TRUE
37 | bus_LV_1632-47_0_4_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_1632-47_0_4_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_1632-47_0_4_node_53 | 0.4 | n |  | TRUE
40 | bus_LV_1632-47_0_4_node_54 | 0.4 | n |  | TRUE
41 | bus_LV_1632-47_0_4_node_47 | 0.4 | n |  | TRUE
42 | bus_LV_1632-47_0_4_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_1632-47_0_4_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_1632-47_0_4_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_1632-47_0_4_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_1632-47_0_4_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_1632-47_0_4_node_50 | 0.4 | n |  | TRUE
48 | bus_LV_1632-47_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_1632-47_0_4_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_1632-47_0_4_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_1632-47_0_4_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_1632-47_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_1632-47_0_4_node_52 | 0.4 | n |  | TRUE
54 | bus_LV_1632-47_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_MV_144_0_node_129 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1632-47_0_4_load_0 | 0 | 0.011723 | 0.0029382 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1632-47_0_4_load_1 | 1 | 0.0094415 | 0.0023663 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1632-47_0_4_load_2 | 2 | 0.0045409 | 0.0011381 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1632-47_0_4_load_31 | 3 | 0.0051277 | 0.0012851 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1632-47_0_4_load_3 | 4 | 0.0071208 | 0.0017846 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1632-47_0_4_load_4 | 5 | 0.0036127 | 0.00090542 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1632-47_0_4_load_30 | 6 | 0.013896 | 0.0034826 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1632-47_0_4_load_28 | 7 | 0.0058132 | 0.0014569 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1632-47_0_4_load_49 | 8 | 0.0070392 | 0.0017642 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1632-47_0_4_load_29 | 10 | 0.0047538 | 0.0011914 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1632-47_0_4_load_48 | 11 | 0.010091 | 0.0025292 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1632-47_0_4_load_5 | 13 | 0.014793 | 0.0037074 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1632-47_0_4_load_6 | 14 | 0.016277 | 0.0040793 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1632-47_0_4_load_26 | 18 | 0.022843 | 0.005725 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1632-47_0_4_load_25 | 19 | 0.01617 | 0.0040526 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1632-47_0_4_load_22 | 20 | 0.013038 | 0.0032676 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1632-47_0_4_load_24 | 22 | 0.0069647 | 0.0017455 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1632-47_0_4_load_55 | 23 | 0.02198 | 0.0055087 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1632-47_0_4_load_10 | 24 | 0.013407 | 0.0033601 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1632-47_0_4_load_13 | 27 | 0.0075958 | 0.0019037 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1632-47_0_4_load_14 | 28 | 0.0050112 | 0.0012559 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1632-47_0_4_load_15 | 29 | 0.0081501 | 0.0020426 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1632-47_0_4_load_16 | 30 | 0.0057187 | 0.0014332 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1632-47_0_4_load_27 | 31 | 0.005257 | 0.0013175 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1632-47_0_4_load_33 | 32 | 0.007416 | 0.0018586 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1632-47_0_4_load_42 | 33 | 0.0064746 | 0.0016227 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1632-47_0_4_load_34 | 34 | 0.011808 | 0.0029593 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1632-47_0_4_load_40 | 35 | 0.0058196 | 0.0014585 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1632-47_0_4_load_17 | 36 | 0.002182 | 0.00054685 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1632-47_0_4_load_18 | 37 | 0.077025 | 0.019304 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1632-47_0_4_load_53 | 39 | 0.0018291 | 0.00045841 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1632-47_0_4_load_54 | 40 | 0.0016215 | 0.00040638 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1632-47_0_4_load_47 | 41 | 0.0078738 | 0.0019734 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1632-47_0_4_load_35 | 42 | 0.0018123 | 0.00045421 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1632-47_0_4_load_36 | 43 | 0.0017544 | 0.00043969 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1632-47_0_4_load_37 | 44 | 0.0024471 | 0.0006133 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1632-47_0_4_load_38 | 45 | 0.010272 | 0.0025744 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1632-47_0_4_load_39 | 46 | 0.0016023 | 0.00040157 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1632-47_0_4_load_50 | 47 | 0.0027454 | 0.00068805 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1632-47_0_4_load_44 | 48 | 0.0015022 | 0.00037648 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1632-47_0_4_load_51 | 49 | 0.01048 | 0.0026265 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1632-47_0_4_load_45 | 50 | 0.0088148 | 0.0022092 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1632-47_0_4_load_41 | 51 | 0.0071508 | 0.0017921 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1632-47_0_4_load_43 | 52 | 0.011568 | 0.0028993 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1632-47_0_4_load_52 | 53 | 0.0065346 | 0.0016377 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1632-47_0_4_load_46 | 54 | 0.001747 | 0.00043783 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1632-47_0_4_line_0 |  | 0 | 1 | 0.024811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_1632-47_0_4_line_1 |  | 0 | 2 | 0.028514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_1632-47_0_4_line_2 |  | 0 | 3 | 0.13527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1632-47_0_4_line_3 |  | 1 | 4 | 0.00085438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_1632-47_0_4_line_4 |  | 2 | 5 | 0.014721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1632-47_0_4_line_5 |  | 3 | 6 | 0.0057475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1632-47_0_4_line_6 |  | 4 | 8 | 0.0054962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_1632-47_0_4_line_7 |  | 5 | 9 | 0.0079274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_1632-47_0_4_line_8 |  | 6 | 7 | 0.020974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1632-47_0_4_line_9 |  | 7 | 10 | 0.015827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1632-47_0_4_line_10 |  | 8 | 11 | 0.0037454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1632-47_0_4_line_11 |  | 9 | 12 | 0.019889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1632-47_0_4_line_12 |  | 11 | 41 | 0.0018466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1632-47_0_4_line_13 |  | 12 | 38 | 0.011814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1632-47_0_4_line_14 |  | 13 | 14 | 5.3292e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1632-47_0_4_line_15 |  | 14 | 15 | 0.021962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1632-47_0_4_line_16 |  | 15 | 16 | 0.002252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1632-47_0_4_line_17 |  | 16 | 22 | 0.01706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1632-47_0_4_line_18 |  | 17 | 18 | 0.010731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1632-47_0_4_line_19 |  | 17 | 19 | 0.030238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1632-47_0_4_line_20 |  | 18 | 23 | 0.015636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1632-47_0_4_line_21 |  | 19 | 21 | 0.02704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1632-47_0_4_line_22 |  | 20 | 21 | 0.017728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1632-47_0_4_line_23 |  | 21 | 37 | 0.03596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1632-47_0_4_line_24 |  | 22 | 29 | 0.00082658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1632-47_0_4_line_25 |  | 24 | 25 | 0.013333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1632-47_0_4_line_26 |  | 24 | 26 | 0.01128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1632-47_0_4_line_27 |  | 25 | 27 | 0.0047366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1632-47_0_4_line_28 |  | 25 | 28 | 0.017371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1632-47_0_4_line_29 |  | 26 | 29 | 0.011743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1632-47_0_4_line_30 |  | 26 | 30 | 0.017168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_1632-47_0_4_line_31 |  | 27 | 31 | 0.0019324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1632-47_0_4_line_32 |  | 28 | 32 | 0.00060843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1632-47_0_4_line_33 |  | 30 | 33 | 0.0049131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_1632-47_0_4_line_34 |  | 32 | 34 | 0.0069104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1632-47_0_4_line_35 |  | 33 | 35 | 0.0050062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_1632-47_0_4_line_36 |  | 34 | 41 | 0.007116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_1632-47_0_4_line_37 |  | 35 | 51 | 0.0051845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1632-47_0_4_line_38 |  | 36 | 37 | 0.013092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1632-47_0_4_line_39 |  | 36 | 38 | 0.02391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1632-47_0_4_line_40 |  | 39 | 40 | 0.0052998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1632-47_0_4_line_41 |  | 40 | 54 | 0.005266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1632-47_0_4_line_42 |  | 42 | 43 | 0.0027252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1632-47_0_4_line_43 |  | 42 | 44 | 0.0037897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1632-47_0_4_line_44 |  | 43 | 45 | 0.0041321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1632-47_0_4_line_45 |  | 44 | 46 | 0.0065542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1632-47_0_4_line_46 |  | 45 | 47 | 0.0027228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1632-47_0_4_line_47 |  | 46 | 48 | 0.0054748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1632-47_0_4_line_48 |  | 47 | 49 | 0.0055621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_1632-47_0_4_line_49 |  | 48 | 50 | 0.00043875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1632-47_0_4_line_50 |  | 49 | 53 | 0.0012621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_1632-47_0_4_line_51 |  | 50 | 54 | 0.0049371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1632-47_0_4_line_52 |  | 51 | 52 | 0.0071257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_1632-47_0_4_line_53 |  | 52 | 53 | 0.0073312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1632-47_0_4_trafo_50 | 0.63 MVA 20/0.4 kV | 55 | 47 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2724299.5951 | 1211320.1562 | 2724310.8469 | 1211298.0437
1 | 2724299.5951 | 1211320.1562 | 2724295.4102 | 1211328.3805 | 2724285.8523 | 1211345.1315
2 | 2724299.5951 | 1211320.1562 | 2724421.4407 | 1211378.8965
3 | 2724311.2344 | 1211297.2822 | 2724310.8469 | 1211298.0437
4 | 2724276.6807 | 1211356.6049 | 2724284.7196 | 1211347.1166 | 2724285.8523 | 1211345.1315
5 | 2724420.8583 | 1211384.611 | 2724420.973 | 1211382.5508 | 2724421.4407 | 1211378.8965
6 | 2724313.7269 | 1211292.3837 | 2724311.2344 | 1211297.2822
7 | 2724271.2286 | 1211362.3585 | 2724276.2952 | 1211357.0599 | 2724276.6807 | 1211356.6049
8 | 2724420.8583 | 1211384.611 | 2724419.952 | 1211400.877 | 2724419.0655 | 1211405.4751
9 | 2724416.069 | 1211421.0163 | 2724419.0655 | 1211405.4751
10 | 2724313.7269 | 1211292.3837 | 2724315.4255 | 1211289.0456
11 | 2724271.2286 | 1211362.3585 | 2724261.6206 | 1211371.8323 | 2724256.093 | 1211368.6147
12 | 2724316.2629 | 1211287.3999 | 2724315.4255 | 1211289.0456
13 | 2724256.093 | 1211368.6147 | 2724245.7695 | 1211362.8174
14 | 2724259.0844 | 1211232.8977 | 2724259.1341 | 1211232.9171
15 | 2724279.5829 | 1211240.9278 | 2724270.249 | 1211237.2416 | 2724259.1341 | 1211232.9171
16 | 2724280.3794 | 1211238.8205 | 2724279.5829 | 1211240.9278
17 | 2724280.3794 | 1211238.8205 | 2724296.2089 | 1211245.1817
18 | 2724206.9405 | 1211272.3947 | 2724196.6674 | 1211269.2934
19 | 2724206.9405 | 1211272.3947 | 2724214.5601 | 1211278.458 | 2724233.9966 | 1211284.9768
20 | 2724181.6989 | 1211264.7745 | 2724196.6674 | 1211269.2934
21 | 2724259.6336 | 1211293.575 | 2724233.9966 | 1211284.9768
22 | 2724259.6336 | 1211293.575 | 2724265.9152 | 1211276.9976
23 | 2724259.6336 | 1211293.575 | 2724248.3021 | 1211327.7031
24 | 2724296.9759 | 1211245.4899 | 2724296.2089 | 1211245.1817
25 | 2724330.7776 | 1211258.875 | 2724318.3698 | 1211253.9963
26 | 2724307.8719 | 1211249.8685 | 2724318.3698 | 1211253.9963
27 | 2724330.7776 | 1211258.875 | 2724333.3058 | 1211258.2939 | 2724335.3608 | 1211257.6878
28 | 2724330.7776 | 1211258.875 | 2724322.8999 | 1211274.3565
29 | 2724307.8719 | 1211249.8685 | 2724296.9759 | 1211245.4899
30 | 2724307.8719 | 1211249.8685 | 2724300.6853 | 1211265.46
31 | 2724335.3608 | 1211257.6878 | 2724337.2143 | 1211257.1412 | 2724337.2143 | 1211257.1412
32 | 2724322.8999 | 1211274.3565 | 2724322.624 | 1211274.8988
33 | 2724300.6853 | 1211265.46 | 2724298.6286 | 1211269.922
34 | 2724322.624 | 1211274.8988 | 2724319.4901 | 1211281.0577
35 | 2724296.533 | 1211274.4685 | 2724298.6286 | 1211269.922
36 | 2724316.2629 | 1211287.3999 | 2724319.4901 | 1211281.0577
37 | 2724296.533 | 1211274.4685 | 2724294.3627 | 1211279.1769
38 | 2724244.5317 | 1211340.2407 | 2724248.2706 | 1211327.7981 | 2724248.3021 | 1211327.7031
39 | 2724245.7695 | 1211362.8174 | 2724243.0709 | 1211358.8137 | 2724242.0403 | 1211354.6445 | 2724242.0034 | 1211348.3945 | 2724243.7945 | 1211342.6941 | 2724244.5317 | 1211340.2407
40 | 2724268.149 | 1211336.0478 | 2724270.3675 | 1211331.2347
41 | 2724272.5719 | 1211326.4523 | 2724270.3675 | 1211331.2347
42 | 2724281.444 | 1211307.204 | 2724282.5848 | 1211304.7291
43 | 2724281.444 | 1211307.204 | 2724279.8576 | 1211310.6458
44 | 2724284.3145 | 1211300.9765 | 2724282.5848 | 1211304.7291
45 | 2724277.114 | 1211316.5981 | 2724279.8576 | 1211310.6458
46 | 2724284.3145 | 1211300.9765 | 2724285.4543 | 1211298.5038
47 | 2724274.8222 | 1211321.5701 | 2724277.114 | 1211316.5981
48 | 2724285.4543 | 1211298.5038 | 2724287.7826 | 1211293.4524
49 | 2724274.6386 | 1211321.9685 | 2724274.8222 | 1211321.5701
50 | 2724288.3109 | 1211292.3062 | 2724287.7826 | 1211293.4524
51 | 2724274.6386 | 1211321.9685 | 2724272.5719 | 1211326.4523
52 | 2724291.3798 | 1211285.6482 | 2724294.3627 | 1211279.1769
53 | 2724288.3109 | 1211292.3062 | 2724291.3798 | 1211285.6482

## bus_geodata
| x | y | coords
0 | 2724299.5951 | 1211320.1562
1 | 2724310.8469 | 1211298.0437
2 | 2724285.8523 | 1211345.1315
3 | 2724421.4407 | 1211378.8965
4 | 2724311.2344 | 1211297.2822
5 | 2724276.6807 | 1211356.6049
6 | 2724420.8583 | 1211384.611
7 | 2724419.0655 | 1211405.4751
8 | 2724313.7269 | 1211292.3837
9 | 2724271.2286 | 1211362.3585
10 | 2724416.069 | 1211421.0163
11 | 2724315.4255 | 1211289.0456
12 | 2724256.093 | 1211368.6147
13 | 2724259.0844 | 1211232.8977
14 | 2724259.1341 | 1211232.9171
15 | 2724279.5829 | 1211240.9278
16 | 2724280.3794 | 1211238.8205
17 | 2724206.9405 | 1211272.3947
18 | 2724196.6674 | 1211269.2934
19 | 2724233.9966 | 1211284.9768
20 | 2724265.9152 | 1211276.9976
21 | 2724259.6336 | 1211293.575
22 | 2724296.2089 | 1211245.1817
23 | 2724181.6989 | 1211264.7745
24 | 2724318.3698 | 1211253.9963
25 | 2724330.7776 | 1211258.875
26 | 2724307.8719 | 1211249.8685
27 | 2724335.3608 | 1211257.6878
28 | 2724322.9 | 1211274.3565
29 | 2724296.9759 | 1211245.4899
30 | 2724300.6853 | 1211265.46
31 | 2724337.2143 | 1211257.1412
32 | 2724322.624 | 1211274.8988
33 | 2724298.6286 | 1211269.922
34 | 2724319.4901 | 1211281.0577
35 | 2724296.533 | 1211274.4685
36 | 2724244.5317 | 1211340.2407
37 | 2724248.3021 | 1211327.7031
38 | 2724245.7695 | 1211362.8174
39 | 2724268.149 | 1211336.0478
40 | 2724270.3675 | 1211331.2347
41 | 2724316.2629 | 1211287.3999
42 | 2724281.444 | 1211307.204
43 | 2724282.5848 | 1211304.7291
44 | 2724279.8576 | 1211310.6458
45 | 2724284.3145 | 1211300.9765
46 | 2724277.114 | 1211316.5981
47 | 2724285.4543 | 1211298.5038
48 | 2724274.8222 | 1211321.5701
49 | 2724287.7826 | 1211293.4524
50 | 2724274.6386 | 1211321.9685
51 | 2724294.3627 | 1211279.1769
52 | 2724291.3798 | 1211285.6482
53 | 2724288.3109 | 1211292.3062
54 | 2724272.5719 | 1211326.4523
55 | 2724307.8719 | 1211249.8685

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98697 | -0.24933 | 0.011723 | 0.0029382
1 | 0.98852 | -0.21938 | 0.0094415 | 0.0023663
2 | 0.98555 | -0.27682 | 0.0045409 | 0.0011381
3 | 0.98328 | -0.32122 | 0.0051277 | 0.0012851
4 | 0.98858 | -0.2183 | 0.0071208 | 0.0017846
5 | 0.98483 | -0.29064 | 0.0036127 | 0.00090542
6 | 0.98315 | -0.32376 | 0.013896 | 0.0034826
7 | 0.98294 | -0.32775 | 0.0058132 | 0.0014569
8 | 0.98895 | -0.21114 | 0.0070392 | 0.0017642
9 | 0.98446 | -0.29792 | 0 | 0
10 | 0.98287 | -0.32911 | 0.0047538 | 0.0011914
11 | 0.98921 | -0.2061 | 0.010091 | 0.0025292
12 | 0.98352 | -0.31621 | 0 | 0
13 | 0.99239 | -0.14529 | 0.014793 | 0.0037074
14 | 0.99239 | -0.14527 | 0.016277 | 0.0040793
15 | 0.99302 | -0.1332 | 0 | 0
16 | 0.99308 | -0.13197 | 0 | 0
17 | 0.97564 | -0.47025 | 0 | 0
18 | 0.97519 | -0.47906 | 0.022843 | 0.005725
19 | 0.9769 | -0.44547 | 0.01617 | 0.0040526
20 | 0.97822 | -0.4196 | 0.013038 | 0.0032676
21 | 0.97843 | -0.41539 | 0 | 0
22 | 0.99356 | -0.1226 | 0.0069647 | 0.0017455
23 | 0.97487 | -0.48536 | 0.02198 | 0.0055087
24 | 0.99307 | -0.13205 | 0.013407 | 0.0033601
25 | 0.99191 | -0.15418 | 0 | 0
26 | 0.99409 | -0.11248 | 0 | 0
27 | 0.99186 | -0.15525 | 0.0075958 | 0.0019037
28 | 0.99047 | -0.18176 | 0.0050112 | 0.0012559
29 | 0.99359 | -0.12205 | 0.0081501 | 0.0020426
30 | 0.99589 | -0.078123 | 0.0057187 | 0.0014332
31 | 0.99185 | -0.15543 | 0.005257 | 0.0013175
32 | 0.99043 | -0.18271 | 0.007416 | 0.0018586
33 | 0.99641 | -0.06815 | 0.0064746 | 0.0016227
34 | 0.98988 | -0.1932 | 0.011808 | 0.0029593
35 | 0.99695 | -0.057809 | 0.0058196 | 0.0014585
36 | 0.98183 | -0.34915 | 0.002182 | 0.00054685
37 | 0.98091 | -0.36704 | 0.077025 | 0.019304
38 | 0.98296 | -0.32709 | 0 | 0
39 | 0.99948 | -0.01004 | 0.0018291 | 0.00045841
40 | 0.99949 | -0.009871 | 0.0016215 | 0.00040638
41 | 0.98934 | -0.20351 | 0.0078738 | 0.0019734
42 | 0.99978 | -0.0042675 | 0.0018123 | 0.00045421
43 | 0.99983 | -0.0032517 | 0.0017544 | 0.00043969
44 | 0.99971 | -0.0055604 | 0.0024471 | 0.0006133
45 | 0.99992 | -0.0015853 | 0.010272 | 0.0025744
46 | 0.99961 | -0.0075172 | 0.0016023 | 0.00040157
47 | 1 | 0 | -0.43479 | -0.1105
48 | 0.99953 | -0.008999 | 0.0015022 | 0.00037648
49 | 0.99933 | -0.012764 | 0.01048 | 0.0026265
50 | 0.99953 | -0.0091062 | 0.0088148 | 0.0022092
51 | 0.99753 | -0.046936 | 0.0071508 | 0.0017921
52 | 0.99833 | -0.031715 | 0.011568 | 0.0028993
53 | 0.99918 | -0.015586 | 0.0065346 | 0.0016377
54 | 0.9995 | -0.0095539 | 0.001747 | 0.00043783
55 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.20403 | -0.051644 | 0.20433 | 0.051831 | 0.00029381 | 0.00018709 | 0.30779 | 0.30779 | 0.30779 | 0.98697 | -0.24933 | 0.98852 | -0.21938 | 28.1864
1 | 0.16261 | 0.041224 | -0.1624 | -0.041088 | 0.00021452 | 0.0001362 | 0.24533 | 0.24533 | 0.24533 | 0.98697 | -0.24933 | 0.98555 | -0.27682 | 22.4664
2 | 0.029697 | 0.0074822 | -0.029595 | -0.0074188 | 0.00010175 | 6.3398e-05 | 0.044787 | 0.044788 | 0.044788 | 0.98697 | -0.24933 | 0.98328 | -0.32122 | 12.3044
3 | -0.21377 | -0.054197 | 0.21378 | 0.054205 | 1.1074e-05 | 7.0543e-06 | 0.32201 | 0.32201 | 0.32201 | 0.98852 | -0.21938 | 0.98858 | -0.2183 | 29.4878
4 | 0.15786 | 0.039949 | -0.15775 | -0.039883 | 0.00010465 | 6.6416e-05 | 0.23848 | 0.23848 | 0.23848 | 0.98555 | -0.27682 | 0.98483 | -0.29064 | 21.8386
5 | 0.024468 | 0.0061337 | -0.024465 | -0.0061319 | 2.9551e-06 | 1.8184e-06 | 0.037028 | 0.037028 | 0.037028 | 0.98328 | -0.32122 | 0.98315 | -0.32376 | 10.1726
6 | -0.2209 | -0.055989 | 0.22098 | 0.056038 | 7.6058e-05 | 4.8466e-05 | 0.33273 | 0.33273 | 0.33273 | 0.98858 | -0.2183 | 0.98895 | -0.21114 | 30.4693
7 | 0.15414 | 0.038978 | -0.15409 | -0.038943 | 5.3805e-05 | 3.4133e-05 | 0.23302 | 0.23302 | 0.23302 | 0.98483 | -0.29064 | 0.98446 | -0.29792 | 21.3387
8 | 0.010569 | 0.0026493 | -0.010567 | -0.0026483 | 2.0127e-06 | 1.0222e-06 | 0.015997 | 0.015997 | 0.015997 | 0.98315 | -0.32376 | 0.98294 | -0.32775 | 4.3948
9 | 0.0047541 | 0.0011914 | -0.0047538 | -0.0011914 | 3.0742e-07 | -3.8591e-09 | 0.0071968 | 0.0071969 | 0.0071969 | 0.98294 | -0.32775 | 0.98287 | -0.32911 | 1.9772
10 | -0.22802 | -0.057802 | 0.22807 | 0.057837 | 5.5182e-05 | 3.5172e-05 | 0.34332 | 0.34332 | 0.34332 | 0.98895 | -0.21114 | 0.98921 | -0.2061 | 31.4392
11 | 0.15409 | 0.038943 | -0.15395 | -0.038858 | 0.00013499 | 8.5637e-05 | 0.23302 | 0.23302 | 0.23302 | 0.98446 | -0.29792 | 0.98352 | -0.31621 | 21.3388
12 | -0.23816 | -0.060366 | 0.23819 | 0.060385 | 2.9665e-05 | 1.8914e-05 | 0.3585 | 0.3585 | 0.3585 | 0.98921 | -0.2061 | 0.98934 | -0.20351 | 32.8293
13 | 0.15395 | 0.038858 | -0.15387 | -0.038807 | 8.0185e-05 | 5.0869e-05 | 0.23302 | 0.23302 | 0.23302 | 0.98352 | -0.31621 | 0.98296 | -0.32709 | 21.3388
14 | -0.014793 | -0.0037074 | 0.014793 | 0.0037074 | 9.8302e-09 | 5.6029e-09 | 0.022181 | 0.022181 | 0.022181 | 0.99239 | -0.14529 | 0.99239 | -0.14527 | 6.0936
15 | -0.031069 | -0.0077867 | 0.031087 | 0.0077979 | 1.7874e-05 | 1.1155e-05 | 0.046586 | 0.046586 | 0.046586 | 0.99239 | -0.14527 | 0.99302 | -0.1332 | 12.7984
16 | -0.031087 | -0.0077979 | 0.031089 | 0.007799 | 1.8328e-06 | 1.1438e-06 | 0.046586 | 0.046586 | 0.046586 | 0.99302 | -0.1332 | 0.99308 | -0.13197 | 12.7984
17 | -0.031089 | -0.007799 | 0.031103 | 0.0078077 | 1.3884e-05 | 8.665e-06 | 0.046586 | 0.046586 | 0.046586 | 0.99308 | -0.13197 | 0.99356 | -0.1226 | 12.7984
18 | 0.044848 | 0.01125 | -0.04483 | -0.011238 | 1.883e-05 | 1.1917e-05 | 0.068405 | 0.068405 | 0.068405 | 0.97564 | -0.47025 | 0.97519 | -0.47906 | 18.7926
19 | -0.044848 | -0.01125 | 0.044902 | 0.011283 | 5.3059e-05 | 3.358e-05 | 0.068405 | 0.068405 | 0.068405 | 0.97564 | -0.47025 | 0.9769 | -0.44547 | 18.7925
20 | 0.021987 | 0.0055127 | -0.02198 | -0.0055087 | 6.5996e-06 | 4.0287e-06 | 0.033549 | 0.033549 | 0.033549 | 0.97519 | -0.47906 | 0.97487 | -0.48536 | 9.2169
21 | -0.061072 | -0.015336 | 0.061159 | 0.015392 | 8.7769e-05 | 5.5833e-05 | 0.093035 | 0.093035 | 0.093035 | 0.9769 | -0.44547 | 0.97843 | -0.41539 | 25.5591
22 | -0.013038 | -0.0032676 | 0.01304 | 0.003269 | 2.6148e-06 | 1.4508e-06 | 0.019832 | 0.019832 | 0.019832 | 0.97822 | -0.4196 | 0.97843 | -0.41539 | 5.4485
23 | -0.0742 | -0.018661 | 0.074372 | 0.01877 | 0.00017179 | 0.00010949 | 0.11287 | 0.11287 | 0.11287 | 0.97843 | -0.41539 | 0.98091 | -0.36704 | 31.0075
24 | -0.038068 | -0.0095532 | 0.038069 | 0.0095539 | 1.0077e-06 | 6.3421e-07 | 0.057017 | 0.057017 | 0.057017 | 0.99356 | -0.1226 | 0.99359 | -0.12205 | 15.6639
25 | 0.28408 | 0.072245 | -0.28378 | -0.072052 | 0.0003025 | 0.00019308 | 0.42604 | 0.42604 | 0.42604 | 0.99307 | -0.13205 | 0.99191 | -0.15418 | 39.0147
26 | -0.29749 | -0.075605 | 0.29777 | 0.075784 | 0.00028064 | 0.00017917 | 0.44613 | 0.44613 | 0.44613 | 0.99307 | -0.13205 | 0.99409 | -0.11248 | 40.8544
27 | 0.012854 | 0.0032216 | -0.012853 | -0.0032212 | 6.6042e-07 | 3.6153e-07 | 0.019282 | 0.019282 | 0.019282 | 0.99191 | -0.15418 | 0.99186 | -0.15525 | 5.2974
28 | 0.27092 | 0.06883 | -0.27057 | -0.068601 | 0.00035925 | 0.00022925 | 0.40676 | 0.40676 | 0.40676 | 0.99191 | -0.15418 | 0.99047 | -0.18176 | 37.249
29 | 0.04624 | 0.01161 | -0.046219 | -0.011596 | 2.1101e-05 | 1.3352e-05 | 0.069222 | 0.069222 | 0.069222 | 0.99409 | -0.11248 | 0.99359 | -0.12205 | 19.0171
30 | -0.34401 | -0.087394 | 0.34458 | 0.087758 | 0.00056995 | 0.0003641 | 0.51535 | 0.51535 | 0.51535 | 0.99409 | -0.11248 | 0.99589 | -0.078123 | 47.1934
31 | 0.0052571 | 0.0013175 | -0.005257 | -0.0013175 | 4.5075e-08 | 3.9079e-09 | 0.0078869 | 0.0078869 | 0.0078869 | 0.99186 | -0.15525 | 0.99185 | -0.15543 | 2.1667
32 | 0.26555 | 0.067345 | -0.26554 | -0.067337 | 1.2122e-05 | 7.7345e-06 | 0.39923 | 0.39923 | 0.39923 | 0.99047 | -0.18176 | 0.99043 | -0.18271 | 36.5596
33 | -0.3503 | -0.089191 | 0.35047 | 0.089299 | 0.00016856 | 0.00010769 | 0.5239 | 0.5239 | 0.5239 | 0.99589 | -0.078123 | 0.99641 | -0.06815 | 47.9758
34 | 0.25813 | 0.065479 | -0.258 | -0.065396 | 0.0001301 | 8.2997e-05 | 0.38809 | 0.38809 | 0.38809 | 0.99043 | -0.18271 | 0.98988 | -0.1932 | 35.5393
35 | -0.35694 | -0.090922 | 0.35712 | 0.091035 | 0.00017815 | 0.00011382 | 0.53356 | 0.53356 | 0.53356 | 0.99641 | -0.06815 | 0.99695 | -0.057809 | 48.8612
36 | 0.24619 | 0.062436 | -0.24607 | -0.062358 | 0.000122 | 7.7803e-05 | 0.37034 | 0.37034 | 0.37034 | 0.98988 | -0.1932 | 0.98934 | -0.20351 | 33.9138
37 | -0.36294 | -0.092494 | 0.36313 | 0.092616 | 0.00019055 | 0.00012175 | 0.54225 | 0.54225 | 0.54225 | 0.99695 | -0.057809 | 0.99753 | -0.046936 | 49.6567
38 | 0.15153 | 0.038157 | -0.1514 | -0.038075 | 0.00012954 | 8.2572e-05 | 0.22971 | 0.22971 | 0.22971 | 0.98183 | -0.34915 | 0.98091 | -0.36704 | 31.554
39 | -0.15371 | -0.038704 | 0.15387 | 0.038807 | 0.00016228 | 0.00010295 | 0.23302 | 0.23302 | 0.23302 | 0.98183 | -0.34915 | 0.98296 | -0.32709 | 21.3388
40 | -0.0018291 | -0.00045841 | 0.0018291 | 0.00045835 | 1.4737e-08 | -6.0026e-08 | 0.0027231 | 0.0027231 | 0.0027231 | 0.99948 | -0.01004 | 0.99949 | -0.009871 | 0.74811
41 | -0.0034506 | -0.00086473 | 0.0034506 | 0.00086469 | 5.2113e-08 | -3.5664e-08 | 0.0051371 | 0.0051371 | 0.0051371 | 0.99949 | -0.009871 | 0.9995 | -0.0095539 | 1.4113
42 | -0.02138 | -0.0053596 | 0.021381 | 0.0053602 | 1.0348e-06 | 6.2656e-07 | 0.031822 | 0.031822 | 0.031822 | 0.99978 | -0.0042675 | 0.99983 | -0.0032517 | 8.7422
43 | 0.019568 | 0.0049054 | -0.019567 | -0.0049047 | 1.2055e-06 | 7.218e-07 | 0.029124 | 0.029124 | 0.029124 | 0.99978 | -0.0042675 | 0.99971 | -0.0055604 | 8.0012
44 | -0.023136 | -0.0057999 | 0.023137 | 0.005801 | 1.8371e-06 | 1.1216e-06 | 0.034433 | 0.034433 | 0.034433 | 0.99983 | -0.0032517 | 0.99992 | -0.0015853 | 9.4595
45 | 0.01712 | 0.0042914 | -0.017118 | -0.0042904 | 1.5959e-06 | 9.3547e-07 | 0.025482 | 0.025482 | 0.025482 | 0.99971 | -0.0055604 | 0.99961 | -0.0075172 | 7.0005
46 | -0.03341 | -0.0083754 | 0.033412 | 0.008377 | 2.524e-06 | 1.5796e-06 | 0.049719 | 0.049719 | 0.049719 | 0.99992 | -0.0015853 | 1 | 0 | 13.659
47 | 0.015516 | 0.0038889 | -0.015515 | -0.0038882 | 1.0952e-06 | 6.2918e-07 | 0.023097 | 0.023097 | 0.023097 | 0.99961 | -0.0075172 | 0.99953 | -0.008999 | 6.3453
48 | 0.39973 | 0.10213 | -0.39948 | -0.10197 | 0.00024655 | 0.00015757 | 0.5955 | 0.5955 | 0.5955 | 1 | 0 | 0.99933 | -0.012764 | 54.5325
49 | 0.014013 | 0.0035118 | -0.014012 | -0.0035117 | 7.1598e-08 | 4.0072e-08 | 0.020861 | 0.020861 | 0.020861 | 0.99953 | -0.008999 | 0.99953 | -0.0091062 | 5.7309
50 | 0.389 | 0.099343 | -0.38895 | -0.099309 | 5.3051e-05 | 3.3903e-05 | 0.57989 | 0.57989 | 0.57989 | 0.99933 | -0.012764 | 0.99918 | -0.015586 | 53.1036
51 | 0.0051977 | 0.0013025 | -0.0051976 | -0.0013025 | 1.1085e-07 | 6.2372e-09 | 0.0077379 | 0.0077379 | 0.0077379 | 0.99953 | -0.0091062 | 0.9995 | -0.0095539 | 2.1258
52 | -0.37028 | -0.094408 | 0.37055 | 0.094582 | 0.00027231 | 0.000174 | 0.55292 | 0.55292 | 0.55292 | 0.99753 | -0.046936 | 0.99833 | -0.031715 | 50.6335
53 | -0.38212 | -0.097481 | 0.38242 | 0.097671 | 0.00029791 | 0.00019037 | 0.57016 | 0.57016 | 0.57016 | 0.99833 | -0.031715 | 0.99918 | -0.015586 | 52.2124

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43754 | 0.11119

## res_load
| p_mw | q_mvar
0 | 0.011723 | 0.0029382
1 | 0.0094415 | 0.0023663
2 | 0.0045409 | 0.0011381
3 | 0.0051277 | 0.0012851
4 | 0.0071208 | 0.0017846
5 | 0.0036127 | 0.00090542
6 | 0.013896 | 0.0034826
7 | 0.0058132 | 0.0014569
8 | 0.0070392 | 0.0017642
9 | 0.0047538 | 0.0011914
10 | 0.010091 | 0.0025292
11 | 0.014793 | 0.0037074
12 | 0.016277 | 0.0040793
13 | 0.022843 | 0.005725
14 | 0.01617 | 0.0040526
15 | 0.013038 | 0.0032676
16 | 0.0069647 | 0.0017455
17 | 0.02198 | 0.0055087
18 | 0.013407 | 0.0033601
19 | 0.0075958 | 0.0019037
20 | 0.0050112 | 0.0012559
21 | 0.0081501 | 0.0020426
22 | 0.0057187 | 0.0014332
23 | 0.005257 | 0.0013175
24 | 0.007416 | 0.0018586
25 | 0.0064746 | 0.0016227
26 | 0.011808 | 0.0029593
27 | 0.0058196 | 0.0014585
28 | 0.002182 | 0.00054685
29 | 0.077025 | 0.019304
30 | 0.0018291 | 0.00045841
31 | 0.0016215 | 0.00040638
32 | 0.0078738 | 0.0019734
33 | 0.0018123 | 0.00045421
34 | 0.0017544 | 0.00043969
35 | 0.0024471 | 0.0006133
36 | 0.010272 | 0.0025744
37 | 0.0016023 | 0.00040157
38 | 0.0027454 | 0.00068805
39 | 0.0015022 | 0.00037648
40 | 0.01048 | 0.0026265
41 | 0.0088148 | 0.0022092
42 | 0.0071508 | 0.0017921
43 | 0.011568 | 0.0028993
44 | 0.0065346 | 0.0016377
45 | 0.001747 | 0.00043783

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1