## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1632-62_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1632-62_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1632-62_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1632-62_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1632-62_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1632-62_0_4_node_48 | 0.4 | n |  | TRUE
6 | bus_LV_1632-62_0_4_node_24 | 0.4 | n |  | TRUE
7 | bus_LV_1632-62_0_4_node_49 | 0.4 | n |  | TRUE
8 | bus_LV_1632-62_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1632-62_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1632-62_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1632-62_0_4_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_1632-62_0_4_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1632-62_0_4_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_1632-62_0_4_node_45 | 0.4 | n |  | TRUE
15 | bus_LV_1632-62_0_4_node_44 | 0.4 | n |  | TRUE
16 | bus_LV_1632-62_0_4_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_1632-62_0_4_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_1632-62_0_4_node_37 | 0.4 | n |  | TRUE
19 | bus_LV_1632-62_0_4_node_61 | 0.4 | n |  | TRUE
20 | bus_LV_1632-62_0_4_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_1632-62_0_4_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1632-62_0_4_node_47 | 0.4 | n |  | TRUE
23 | bus_LV_1632-62_0_4_node_92 | 0.4 | n |  | TRUE
24 | bus_LV_1632-62_0_4_node_79 | 0.4 | n |  | TRUE
25 | bus_LV_1632-62_0_4_node_71 | 0.4 | n |  | TRUE
26 | bus_LV_1632-62_0_4_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1632-62_0_4_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1632-62_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_1632-62_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_1632-62_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_1632-62_0_4_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_1632-62_0_4_node_68 | 0.4 | n |  | TRUE
33 | bus_LV_1632-62_0_4_node_50 | 0.4 | n |  | TRUE
34 | bus_LV_1632-62_0_4_node_69 | 0.4 | n |  | TRUE
35 | bus_LV_1632-62_0_4_node_58 | 0.4 | n |  | TRUE
36 | bus_LV_1632-62_0_4_node_52 | 0.4 | n |  | TRUE
37 | bus_LV_1632-62_0_4_node_51 | 0.4 | n |  | TRUE
38 | bus_LV_1632-62_0_4_node_66 | 0.4 | n |  | TRUE
39 | bus_LV_1632-62_0_4_node_80 | 0.4 | n |  | TRUE
40 | bus_LV_1632-62_0_4_node_65 | 0.4 | n |  | TRUE
41 | bus_LV_1632-62_0_4_node_70 | 0.4 | n |  | TRUE
42 | bus_LV_1632-62_0_4_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_1632-62_0_4_node_20 | 0.4 | n |  | TRUE
44 | bus_LV_1632-62_0_4_node_21 | 0.4 | n |  | TRUE
45 | bus_LV_1632-62_0_4_node_23 | 0.4 | n |  | TRUE
46 | bus_LV_1632-62_0_4_node_62 | 0.4 | n |  | TRUE
47 | bus_LV_1632-62_0_4_node_67 | 0.4 | n |  | TRUE
48 | bus_LV_1632-62_0_4_node_25 | 0.4 | n |  | TRUE
49 | bus_LV_1632-62_0_4_node_26 | 0.4 | n |  | TRUE
50 | bus_LV_1632-62_0_4_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_1632-62_0_4_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_1632-62_0_4_node_60 | 0.4 | n |  | TRUE
53 | bus_LV_1632-62_0_4_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_1632-62_0_4_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_1632-62_0_4_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_1632-62_0_4_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_1632-62_0_4_node_32 | 0.4 | n |  | TRUE
58 | bus_LV_1632-62_0_4_node_33 | 0.4 | n |  | TRUE
59 | bus_LV_1632-62_0_4_node_34 | 0.4 | n |  | TRUE
60 | bus_LV_1632-62_0_4_node_35 | 0.4 | n |  | TRUE
61 | bus_LV_1632-62_0_4_node_64 | 0.4 | n |  | TRUE
62 | bus_LV_1632-62_0_4_node_72 | 0.4 | n |  | TRUE
63 | bus_LV_1632-62_0_4_node_90 | 0.4 | n |  | TRUE
64 | bus_LV_1632-62_0_4_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_1632-62_0_4_node_91 | 0.4 | n |  | TRUE
66 | bus_LV_1632-62_0_4_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_1632-62_0_4_node_81 | 0.4 | n |  | TRUE
68 | bus_LV_1632-62_0_4_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_1632-62_0_4_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_1632-62_0_4_node_43 | 0.4 | n |  | TRUE
71 | bus_LV_1632-62_0_4_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_1632-62_0_4_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_1632-62_0_4_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_1632-62_0_4_node_83 | 0.4 | n |  | TRUE
75 | bus_LV_1632-62_0_4_node_82 | 0.4 | n |  | TRUE
76 | bus_LV_1632-62_0_4_node_88 | 0.4 | n |  | TRUE
77 | bus_LV_1632-62_0_4_node_87 | 0.4 | n |  | TRUE
78 | bus_LV_1632-62_0_4_node_85 | 0.4 | n |  | TRUE
79 | bus_LV_1632-62_0_4_node_89 | 0.4 | n |  | TRUE
80 | bus_LV_1632-62_0_4_node_84 | 0.4 | n |  | TRUE
81 | bus_LV_1632-62_0_4_node_73 | 0.4 | n |  | TRUE
82 | bus_LV_1632-62_0_4_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_1632-62_0_4_node_75 | 0.4 | n |  | TRUE
84 | bus_LV_1632-62_0_4_node_76 | 0.4 | n |  | TRUE
85 | bus_LV_1632-62_0_4_node_77 | 0.4 | n |  | TRUE
86 | bus_LV_1632-62_0_4_node_78 | 0.4 | n |  | TRUE
87 | bus_MV_224_0_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1632-62_0_4_load_0 | 0 | 0.0041509 | 0.0010403 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1632-62_0_4_load_1 | 1 | 0.0046628 | 0.0011686 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1632-62_0_4_load_2 | 2 | 0.0021644 | 0.00054244 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1632-62_0_4_load_3 | 3 | 0.0018559 | 0.00046514 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1632-62_0_4_load_4 | 4 | 0.003299 | 0.00082681 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1632-62_0_4_load_48 | 5 | 0.0018394 | 0.00046101 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1632-62_0_4_load_24 | 6 | 0.011571 | 0.0029 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1632-62_0_4_load_49 | 7 | 0.0032139 | 0.00080549 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1632-62_0_4_load_5 | 8 | 0.0064082 | 0.001606 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1632-62_0_4_load_6 | 9 | 0.0112 | 0.0028069 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1632-62_0_4_load_8 | 10 | 0.002196 | 0.00055038 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1632-62_0_4_load_46 | 13 | 0.0047232 | 0.0011837 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1632-62_0_4_load_45 | 14 | 0.0047823 | 0.0011986 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1632-62_0_4_load_44 | 15 | 0.0023772 | 0.00059579 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1632-62_0_4_load_40 | 16 | 0.0018385 | 0.00046078 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1632-62_0_4_load_36 | 17 | 0.0039193 | 0.00098228 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1632-62_0_4_load_22 | 21 | 0.005275 | 0.001322 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1632-62_0_4_load_92 | 23 | 0.0087823 | 0.0022011 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1632-62_0_4_load_71 | 25 | 0.0081264 | 0.0020367 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1632-62_0_4_load_28 | 26 | 0.0052017 | 0.0013037 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1632-62_0_4_load_13 | 27 | 0.0035993 | 0.00090206 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1632-62_0_4_load_14 | 28 | 0.0024114 | 0.00060437 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1632-62_0_4_load_16 | 30 | 0.0019454 | 0.00048758 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1632-62_0_4_load_50 | 33 | 0.0033015 | 0.00082743 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1632-62_0_4_load_69 | 34 | 0.0027452 | 0.00068802 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1632-62_0_4_load_58 | 35 | 0.0033003 | 0.00082712 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1632-62_0_4_load_52 | 36 | 0.0028661 | 0.0007183 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1632-62_0_4_load_51 | 37 | 0.0041335 | 0.0010359 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1632-62_0_4_load_80 | 39 | 0.08586 | 0.021518 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1632-62_0_4_load_70 | 41 | 0.0025059 | 0.00062805 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1632-62_0_4_load_19 | 42 | 0.0045821 | 0.0011484 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1632-62_0_4_load_20 | 43 | 0.010563 | 0.0026472 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1632-62_0_4_load_21 | 44 | 0.0031843 | 0.00079806 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1632-62_0_4_load_23 | 45 | 0.0068548 | 0.001718 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1632-62_0_4_load_67 | 47 | 0.0030842 | 0.00077299 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1632-62_0_4_load_25 | 48 | 0.0047202 | 0.001183 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1632-62_0_4_load_26 | 49 | 0.0049806 | 0.0012482 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1632-62_0_4_load_27 | 50 | 0.0045054 | 0.0011292 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1632-62_0_4_load_60 | 52 | 0.0097312 | 0.0024389 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1632-62_0_4_load_59 | 53 | 0.0052976 | 0.0013277 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1632-62_0_4_load_38 | 54 | 0.0086298 | 0.0021628 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1632-62_0_4_load_30 | 55 | 0.0035465 | 0.00088883 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1632-62_0_4_load_31 | 56 | 0.0038996 | 0.00097733 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1632-62_0_4_load_33 | 58 | 0.0082086 | 0.0020573 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1632-62_0_4_load_34 | 59 | 0.0036017 | 0.00090268 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1632-62_0_4_load_64 | 61 | 0.0052452 | 0.0013146 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1632-62_0_4_load_72 | 62 | 0.0035883 | 0.0008993 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1632-62_0_4_load_90 | 63 | 0.0041469 | 0.0010393 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1632-62_0_4_load_55 | 64 | 0.0067627 | 0.0016949 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1632-62_0_4_load_91 | 65 | 0.0029727 | 0.00074502 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1632-62_0_4_load_81 | 67 | 0.0039195 | 0.00098232 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1632-62_0_4_load_56 | 68 | 0.0060639 | 0.0015197 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1632-62_0_4_load_41 | 69 | 0.0038456 | 0.00096379 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1632-62_0_4_load_43 | 70 | 0.012251 | 0.0030704 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1632-62_0_4_load_54 | 72 | 0.0041561 | 0.0010416 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1632-62_0_4_load_57 | 73 | 0.0076478 | 0.0019167 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1632-62_0_4_load_83 | 74 | 0.0037329 | 0.00093554 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1632-62_0_4_load_82 | 75 | 0.0057085 | 0.0014307 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1632-62_0_4_load_85 | 78 | 0.0013242 | 0.00033189 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1632-62_0_4_load_89 | 79 | 0.0058427 | 0.0014643 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1632-62_0_4_load_84 | 80 | 0.002256 | 0.0005654 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1632-62_0_4_load_73 | 81 | 0.0047591 | 0.0011927 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1632-62_0_4_load_74 | 82 | 0.005937 | 0.001488 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1632-62_0_4_load_75 | 83 | 0.0037282 | 0.00093437 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1632-62_0_4_load_76 | 84 | 0.0035714 | 0.00089508 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1632-62_0_4_load_77 | 85 | 0.0041094 | 0.0010299 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1632-62_0_4_load_78 | 86 | 0.0034916 | 0.00087509 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1632-62_0_4_line_0 |  | 0 | 1 | 0.0086523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1632-62_0_4_line_1 |  | 0 | 2 | 0.011355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1632-62_0_4_line_2 |  | 1 | 3 | 0.0080583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1632-62_0_4_line_3 |  | 2 | 4 | 0.0066421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1632-62_0_4_line_4 |  | 3 | 5 | 0.0033981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1632-62_0_4_line_5 |  | 4 | 6 | 0.013455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1632-62_0_4_line_6 |  | 5 | 7 | 0.011058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1632-62_0_4_line_7 |  | 7 | 33 | 0.0048637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1632-62_0_4_line_8 |  | 8 | 9 | 0.009623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1632-62_0_4_line_9 |  | 9 | 10 | 0.015662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1632-62_0_4_line_10 |  | 10 | 11 | 0.018357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1632-62_0_4_line_11 |  | 11 | 15 | 0.0036108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1632-62_0_4_line_12 |  | 11 | 16 | 0.018255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1632-62_0_4_line_13 |  | 12 | 13 | 0.0047776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1632-62_0_4_line_14 |  | 12 | 14 | 0.0031059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1632-62_0_4_line_15 |  | 13 | 25 | 0.0049407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1632-62_0_4_line_16 |  | 14 | 26 | 0.0055363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1632-62_0_4_line_17 |  | 15 | 32 | 0.017079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1632-62_0_4_line_18 |  | 16 | 69 | 0.0018081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1632-62_0_4_line_19 |  | 17 | 18 | 0.010029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1632-62_0_4_line_20 |  | 18 | 54 | 0.0095034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1632-62_0_4_line_21 |  | 18 | 66 | 0.006169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1632-62_0_4_line_22 |  | 19 | 20 | 0.12177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1632-62_0_4_line_23 |  | 19 | 21 | 0.030877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1632-62_0_4_line_24 |  | 20 | 74 | 0.029425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1632-62_0_4_line_25 |  | 21 | 43 | 0.016042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1632-62_0_4_line_26 |  | 22 | 23 | 0.024707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1632-62_0_4_line_27 |  | 22 | 24 | 0.048361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1632-62_0_4_line_28 |  | 24 | 52 | 0.011793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1632-62_0_4_line_29 |  | 26 | 49 | 0.008571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1632-62_0_4_line_30 |  | 27 | 28 | 0.0068091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1632-62_0_4_line_31 |  | 27 | 29 | 0.0123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1632-62_0_4_line_32 |  | 28 | 30 | 0.021991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1632-62_0_4_line_33 |  | 29 | 31 | 0.049194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1632-62_0_4_line_34 |  | 30 | 32 | 0.004469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_1632-62_0_4_line_35 |  | 31 | 33 | 0.028773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1632-62_0_4_line_36 |  | 31 | 34 | 0.011209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1632-62_0_4_line_37 |  | 32 | 35 | 0.019146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1632-62_0_4_line_38 |  | 34 | 41 | 0.00028539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1632-62_0_4_line_39 |  | 35 | 73 | 0.024124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_1632-62_0_4_line_40 |  | 36 | 37 | 0.0074503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1632-62_0_4_line_41 |  | 37 | 71 | 0.02717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1632-62_0_4_line_42 |  | 38 | 39 | 0.056553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1632-62_0_4_line_43 |  | 38 | 40 | 0.031604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1632-62_0_4_line_44 |  | 39 | 79 | 0.026023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1632-62_0_4_line_45 |  | 40 | 76 | 0.050312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1632-62_0_4_line_46 |  | 40 | 61 | 0.013845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1632-62_0_4_line_47 |  | 41 | 47 | 0.023924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1632-62_0_4_line_48 |  | 42 | 43 | 0.0024861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1632-62_0_4_line_49 |  | 42 | 44 | 0.013997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1632-62_0_4_line_50 |  | 44 | 45 | 0.0058568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1632-62_0_4_line_51 |  | 45 | 46 | 0.018685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1632-62_0_4_line_52 |  | 46 | 47 | 0.03052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1632-62_0_4_line_53 |  | 48 | 49 | 0.0049996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1632-62_0_4_line_54 |  | 48 | 50 | 0.0053751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1632-62_0_4_line_55 |  | 50 | 51 | 0.011485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1632-62_0_4_line_56 |  | 51 | 52 | 0.02968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1632-62_0_4_line_57 |  | 51 | 53 | 0.0077197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1632-62_0_4_line_58 |  | 53 | 54 | 0.00093688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1632-62_0_4_line_59 |  | 55 | 56 | 0.0080543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1632-62_0_4_line_60 |  | 55 | 57 | 0.026267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1632-62_0_4_line_61 |  | 56 | 58 | 0.013307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1632-62_0_4_line_62 |  | 57 | 59 | 0.013707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_1632-62_0_4_line_63 |  | 57 | 60 | 0.011196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1632-62_0_4_line_64 |  | 58 | 61 | 0.021563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1632-62_0_4_line_65 |  | 59 | 62 | 5.5927e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_1632-62_0_4_line_66 |  | 60 | 63 | 0.01872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1632-62_0_4_line_67 |  | 62 | 64 | 2.8869e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_1632-62_0_4_line_68 |  | 63 | 65 | 0.0070224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1632-62_0_4_line_69 |  | 64 | 71 | 0.01841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_1632-62_0_4_line_70 |  | 65 | 67 | 0.0060221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1632-62_0_4_line_71 |  | 66 | 67 | 0.010937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1632-62_0_4_line_72 |  | 66 | 68 | 0.013319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1632-62_0_4_line_73 |  | 69 | 70 | 0.0057765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1632-62_0_4_line_74 |  | 71 | 72 | 0.012397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_1632-62_0_4_line_75 |  | 72 | 73 | 0.00093135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_1632-62_0_4_line_76 |  | 74 | 75 | 0.0088304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1632-62_0_4_line_77 |  | 75 | 85 | 0.018678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1632-62_0_4_line_78 |  | 76 | 77 | 0.10905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1632-62_0_4_line_79 |  | 77 | 78 | 0.074164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1632-62_0_4_line_80 |  | 78 | 80 | 0.012661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1632-62_0_4_line_81 |  | 81 | 82 | 0.013361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1632-62_0_4_line_82 |  | 81 | 83 | 0.0082941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1632-62_0_4_line_83 |  | 82 | 84 | 0.00802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1632-62_0_4_line_84 |  | 83 | 85 | 0.0057858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1632-62_0_4_line_85 |  | 84 | 86 | 0.0059435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1632-62_0_4_trafo_16 | 0.63 MVA 20/0.4 kV | 87 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2723021.1619 | 1213628.6207 | 2723029.8031 | 1213629.0594
1 | 2723021.1619 | 1213628.6207 | 2723009.8218 | 1213628.0449
2 | 2723037.851 | 1213629.468 | 2723029.8031 | 1213629.0594
3 | 2723009.8218 | 1213628.0449 | 2723003.1882 | 1213627.7081
4 | 2723037.851 | 1213629.468 | 2723041.2447 | 1213629.6403
5 | 2722989.7507 | 1213627.0259 | 2723003.1882 | 1213627.7081
6 | 2723052.2889 | 1213630.2011 | 2723041.2447 | 1213629.6403
7 | 2723052.2889 | 1213630.2011 | 2723057.1463 | 1213630.4477
8 | 2722974.729 | 1213676.61 | 2722984.3448 | 1213676.9836
9 | 2722999.9953 | 1213677.5916 | 2722984.3448 | 1213676.9836
10 | 2723018.3388 | 1213678.3043 | 2722999.9953 | 1213677.5916
11 | 2723018.3388 | 1213678.3043 | 2723021.9469 | 1213678.4447
12 | 2723018.3388 | 1213678.3043 | 2723017.683 | 1213696.5475
13 | 2722952.835 | 1213711.7235 | 2722950.0721 | 1213707.8258
14 | 2722952.835 | 1213711.7235 | 2722955.1677 | 1213713.7741
15 | 2722950.0721 | 1213707.8258 | 2722947.2149 | 1213703.795
16 | 2722959.3259 | 1213717.4292 | 2722955.1677 | 1213713.7741
17 | 2723039.0126 | 1213679.1092 | 2723021.9469 | 1213678.4447
18 | 2723017.6181 | 1213698.3544 | 2723017.683 | 1213696.5475
19 | 2722993.6547 | 1213729.3233 | 2722987.3288 | 1213721.5406
20 | 2722993.6547 | 1213729.3233 | 2722986.1155 | 1213735.109
21 | 2722997.5603 | 1213734.1076 | 2722993.6547 | 1213729.3233
22 | 2722980.8387 | 1213569.4246 | 2722995.518 | 1213540.0269 | 2723005.5159 | 1213524.2877 | 2723010.1593 | 1213516.5219 | 2723013.26 | 1213511.3486 | 2723023.4698 | 1213494.1793 | 2723026.0012 | 1213490.0839 | 2723045.922 | 1213513.0348
23 | 2722980.8387 | 1213569.4246 | 2723011.6761 | 1213570.9827
24 | 2723045.922 | 1213513.0348 | 2723065.8408 | 1213534.6927
25 | 2723011.6761 | 1213570.9827 | 2723027.6975 | 1213571.7921
26 | 2722952.3974 | 1213778.2213 | 2722956.2188 | 1213770.8833 | 2722959.6756 | 1213766.4846 | 2722960.8675 | 1213762.8508 | 2722960.5031 | 1213755.8379
27 | 2722952.3974 | 1213778.2213 | 2722957.8298 | 1213783.3929 | 2722960.4802 | 1213793.0327 | 2722988.5908 | 1213780.2915
28 | 2722988.5908 | 1213780.2915 | 2722985.5963 | 1213774.4363 | 2722984.5214 | 1213769.3315
29 | 2722959.3259 | 1213717.4292 | 2722960.5815 | 1213718.5329 | 2722965.4344 | 1213723.4368
30 | 2723072.2509 | 1213680.5425 | 2723065.4481 | 1213680.2492
31 | 2723084.5396 | 1213681.0724 | 2723072.2509 | 1213680.5425
32 | 2723043.4774 | 1213679.3017 | 2723065.4481 | 1213680.2492
33 | 2723085.8819 | 1213631.9067 | 2723084.5396 | 1213681.0724
34 | 2723039.0126 | 1213679.1092 | 2723043.4774 | 1213679.3017
35 | 2723085.8819 | 1213631.9067 | 2723057.1463 | 1213630.4477
36 | 2723085.8819 | 1213631.9067 | 2723086.1994 | 1213620.7018
37 | 2723039.0126 | 1213679.1092 | 2723038.2423 | 1213698.2393
38 | 2723086.2074 | 1213620.4165 | 2723086.1994 | 1213620.7018
39 | 2723038.2423 | 1213698.2393 | 2723037.2717 | 1213722.3437
40 | 2723063.8837 | 1213736.7387 | 2723071.3281 | 1213737.0341
41 | 2723036.7355 | 1213735.6614 | 2723063.8837 | 1213736.7387
42 | 2723119.4736 | 1213738.9716 | 2723122.2132 | 1213682.4845
43 | 2723118.426 | 1213770.5521 | 2723119.4736 | 1213738.9716
44 | 2723122.2132 | 1213682.4845 | 2723148.226 | 1213681.7445
45 | 2723118.426 | 1213770.5521 | 2723143.6876 | 1213814.0628
46 | 2723118.426 | 1213770.5521 | 2723104.588 | 1213770.0994
47 | 2723086.2074 | 1213620.4165 | 2723086.885 | 1213596.5017
48 | 2723030.1804 | 1213571.9176 | 2723027.6975 | 1213571.7921
49 | 2723044.1594 | 1213572.6239 | 2723030.1804 | 1213571.9176
50 | 2723050.0088 | 1213572.9194 | 2723044.1594 | 1213572.6239
51 | 2723068.6697 | 1213573.8622 | 2723050.0088 | 1213572.9194
52 | 2723068.6697 | 1213573.8622 | 2723087.0318 | 1213591.3213 | 2723086.885 | 1213596.5017
53 | 2722965.4344 | 1213723.4368 | 2722965.4344 | 1213723.4368 | 2722968.5937 | 1213727.3117
54 | 2722971.9903 | 1213731.4776 | 2722968.5937 | 1213727.3117
55 | 2722979.2481 | 1213740.3792 | 2722971.9903 | 1213731.4776
56 | 2722979.2481 | 1213740.3792 | 2722981.4972 | 1213744.7956 | 2722984.3923 | 1213768.7182 | 2722984.5214 | 1213769.3315
57 | 2722979.2481 | 1213740.3792 | 2722985.3722 | 1213735.6794
58 | 2722986.1155 | 1213735.109 | 2722985.3722 | 1213735.6794
59 | 2723069.736 | 1213768.9593 | 2723061.686 | 1213768.6959
60 | 2723035.4329 | 1213767.8371 | 2723061.686 | 1213768.6959
61 | 2723083.0361 | 1213769.3944 | 2723069.736 | 1213768.9593
62 | 2723035.4329 | 1213767.8371 | 2723035.9873 | 1213754.1415
63 | 2723024.2102 | 1213767.4719 | 2723035.4329 | 1213767.8371
64 | 2723104.588 | 1213770.0994 | 2723083.0361 | 1213769.3944
65 | 2723035.9873 | 1213754.1415 | 2723035.9896 | 1213754.0856
66 | 2723024.2102 | 1213767.4719 | 2723012.527 | 1213752.8451
67 | 2723035.9896 | 1213754.0856 | 2723035.9908 | 1213754.0567
68 | 2723012.527 | 1213752.8451 | 2723008.1443 | 1213747.3582
69 | 2723036.7355 | 1213735.6614 | 2723035.9908 | 1213754.0567
70 | 2723008.1443 | 1213747.3582 | 2723004.3859 | 1213742.6529
71 | 2722997.5603 | 1213734.1076 | 2723004.3859 | 1213742.6529
72 | 2722997.5603 | 1213734.1076 | 2723010.8683 | 1213734.6354
73 | 2723017.4106 | 1213704.1272 | 2723017.6181 | 1213698.3544
74 | 2723036.7355 | 1213735.6614 | 2723037.2343 | 1213723.2743
75 | 2723037.2343 | 1213723.2743 | 2723037.2717 | 1213722.3437
76 | 2723071.8184 | 1213541.1922 | 2723065.8408 | 1213534.6927
77 | 2723071.8184 | 1213541.1922 | 2723084.4622 | 1213554.94
78 | 2723143.6876 | 1213814.0628 | 2723152.007 | 1213818.5047 | 2723158.5815 | 1213819.141 | 2723189.2171 | 1213819.8966 | 2723193.0126 | 1213820.0752 | 2723223.1252 | 1213819.6637 | 2723251.5573 | 1213818.5838
79 | 2723251.5573 | 1213818.5838 | 2723253.349 | 1213744.4412
80 | 2723253.6549 | 1213731.7839 | 2723253.349 | 1213744.4412
81 | 2723094.2626 | 1213565.0401 | 2723099.1118 | 1213569.6985 | 2723104.236 | 1213573.9159
82 | 2723094.2626 | 1213565.0401 | 2723089.873 | 1213560.8231 | 2723088.3789 | 1213559.1986
83 | 2723104.236 | 1213573.9159 | 2723110.4283 | 1213579.0125
84 | 2723088.3789 | 1213559.1986 | 2723084.4622 | 1213554.94
85 | 2723115.0174 | 1213582.7895 | 2723110.4283 | 1213579.0125

## bus_geodata
| x | y | coords
0 | 2723021.1619 | 1213628.6207
1 | 2723029.8031 | 1213629.0594
2 | 2723009.8218 | 1213628.0449
3 | 2723037.851 | 1213629.468
4 | 2723003.1882 | 1213627.7081
5 | 2723041.2447 | 1213629.6403
6 | 2722989.7507 | 1213627.0259
7 | 2723052.2889 | 1213630.2011
8 | 2722974.729 | 1213676.61
9 | 2722984.3448 | 1213676.9836
10 | 2722999.9953 | 1213677.5916
11 | 2723018.3388 | 1213678.3043
12 | 2722952.835 | 1213711.7235
13 | 2722950.0721 | 1213707.8258
14 | 2722955.1677 | 1213713.7741
15 | 2723021.9469 | 1213678.4447
16 | 2723017.683 | 1213696.5475
17 | 2722987.3288 | 1213721.5406
18 | 2722993.6547 | 1213729.3233
19 | 2722980.8387 | 1213569.4246
20 | 2723045.922 | 1213513.0348
21 | 2723011.6761 | 1213570.9827
22 | 2722952.3974 | 1213778.2213
23 | 2722960.5031 | 1213755.8379
24 | 2722988.5908 | 1213780.2915
25 | 2722947.2149 | 1213703.795
26 | 2722959.3259 | 1213717.4292
27 | 2723072.2509 | 1213680.5425
28 | 2723065.4481 | 1213680.2492
29 | 2723084.5396 | 1213681.0724
30 | 2723043.4774 | 1213679.3017
31 | 2723085.8819 | 1213631.9067
32 | 2723039.0126 | 1213679.1092
33 | 2723057.1463 | 1213630.4477
34 | 2723086.1994 | 1213620.7018
35 | 2723038.2423 | 1213698.2393
36 | 2723071.3281 | 1213737.0341
37 | 2723063.8837 | 1213736.7387
38 | 2723119.4736 | 1213738.9716
39 | 2723122.2132 | 1213682.4845
40 | 2723118.426 | 1213770.5521
41 | 2723086.2074 | 1213620.4165
42 | 2723030.1804 | 1213571.9176
43 | 2723027.6975 | 1213571.7921
44 | 2723044.1594 | 1213572.6239
45 | 2723050.0088 | 1213572.9194
46 | 2723068.6697 | 1213573.8622
47 | 2723086.885 | 1213596.5017
48 | 2722968.5937 | 1213727.3117
49 | 2722965.4344 | 1213723.4368
50 | 2722971.9903 | 1213731.4776
51 | 2722979.248 | 1213740.3792
52 | 2722984.5214 | 1213769.3315
53 | 2722985.3722 | 1213735.6794
54 | 2722986.1155 | 1213735.109
55 | 2723061.686 | 1213768.6959
56 | 2723069.736 | 1213768.9593
57 | 2723035.4329 | 1213767.8371
58 | 2723083.0361 | 1213769.3944
59 | 2723035.9873 | 1213754.1415
60 | 2723024.2102 | 1213767.4719
61 | 2723104.588 | 1213770.0994
62 | 2723035.9896 | 1213754.0856
63 | 2723012.527 | 1213752.8451
64 | 2723035.9908 | 1213754.0567
65 | 2723008.1443 | 1213747.3582
66 | 2722997.5603 | 1213734.1076
67 | 2723004.3859 | 1213742.6529
68 | 2723010.8683 | 1213734.6354
69 | 2723017.6181 | 1213698.3544
70 | 2723017.4106 | 1213704.1272
71 | 2723036.7355 | 1213735.6614
72 | 2723037.2343 | 1213723.2743
73 | 2723037.2717 | 1213722.3437
74 | 2723065.8408 | 1213534.6927
75 | 2723071.8184 | 1213541.1922
76 | 2723143.6876 | 1213814.0628
77 | 2723251.5573 | 1213818.5838
78 | 2723253.349 | 1213744.4412
79 | 2723148.226 | 1213681.7445
80 | 2723253.6549 | 1213731.7839
81 | 2723094.2626 | 1213565.0401
82 | 2723104.236 | 1213573.9159
83 | 2723088.3789 | 1213559.1986
84 | 2723110.4283 | 1213579.0125
85 | 2723084.4622 | 1213554.94
86 | 2723115.0174 | 1213582.7895
87 | 2723039.0126 | 1213679.1092

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98886 | -0.2131 | 0.0041509 | 0.0010403
1 | 0.98903 | -0.20983 | 0.0046628 | 0.0011686
2 | 0.98868 | -0.21655 | 0.0021644 | 0.00054244
3 | 0.98922 | -0.20612 | 0.0018559 | 0.00046514
4 | 0.98859 | -0.21831 | 0.003299 | 0.00082681
5 | 0.98931 | -0.20445 | 0.0018394 | 0.00046101
6 | 0.98845 | -0.22109 | 0.011571 | 0.0029
7 | 0.98961 | -0.19863 | 0.0032139 | 0.00080549
8 | 0.99823 | -0.033941 | 0.0064082 | 0.001606
9 | 0.99829 | -0.032863 | 0.0112 | 0.0028069
10 | 0.99854 | -0.028041 | 0.002196 | 0.00055038
11 | 0.99887 | -0.021687 | 0 | 0
12 | 0.98615 | -0.26588 | 0 | 0
13 | 0.98609 | -0.26698 | 0.0047232 | 0.0011837
14 | 0.98619 | -0.26517 | 0.0047823 | 0.0011986
15 | 0.99899 | -0.019307 | 0.0023772 | 0.00059579
16 | 0.99857 | -0.027409 | 0.0018385 | 0.00046078
17 | 0.98815 | -0.2269 | 0.0039193 | 0.00098228
18 | 0.98819 | -0.2262 | 0 | 0
19 | 0.98266 | -0.33289 | 0 | 0
20 | 0.9787 | -0.41022 | 0 | 0
21 | 0.98367 | -0.31338 | 0.005275 | 0.001322
22 | 0.98614 | -0.26598 | 0 | 0
23 | 0.98595 | -0.26987 | 0.0087823 | 0.0022011
24 | 0.98654 | -0.25837 | 0 | 0
25 | 0.98606 | -0.2677 | 0.0081264 | 0.0020367
26 | 0.98628 | -0.26342 | 0.0052017 | 0.0013037
27 | 0.99694 | -0.05808 | 0.0035993 | 0.00090206
28 | 0.99765 | -0.044536 | 0.0024114 | 0.00060437
29 | 0.99569 | -0.081817 | 0 | 0
30 | 1 | 0 | -0.4056 | -0.10324
31 | 0.9907 | -0.17735 | 0 | 0
32 | 0.99961 | -0.0073478 | 0 | 0
33 | 0.98975 | -0.19579 | 0.0033015 | 0.00082743
34 | 0.98994 | -0.19206 | 0.0027452 | 0.00068802
35 | 0.99818 | -0.034412 | 0.0033003 | 0.00082712
36 | 0.99528 | -0.089675 | 0.0028661 | 0.0007183
37 | 0.9953 | -0.089299 | 0.0041335 | 0.0010359
38 | 0.98197 | -0.34572 | 0 | 0
39 | 0.97716 | -0.43992 | 0.08586 | 0.021518
40 | 0.98466 | -0.29347 | 0 | 0
41 | 0.98992 | -0.19242 | 0.0025059 | 0.00062805
42 | 0.98438 | -0.29946 | 0.0045821 | 0.0011484
43 | 0.98427 | -0.30173 | 0.010563 | 0.0026472
44 | 0.9851 | -0.2855 | 0.0031843 | 0.00079806
45 | 0.98542 | -0.27933 | 0.0068548 | 0.001718
46 | 0.98655 | -0.25739 | 0 | 0
47 | 0.9884 | -0.22165 | 0.0030842 | 0.00077299
48 | 0.98658 | -0.25742 | 0.0047202 | 0.001183
49 | 0.98646 | -0.25991 | 0.0049806 | 0.0012482
50 | 0.98674 | -0.25429 | 0.0045054 | 0.0011292
51 | 0.98714 | -0.24668 | 0 | 0
52 | 0.98663 | -0.25651 | 0.0097312 | 0.0024389
53 | 0.98753 | -0.23901 | 0.0052976 | 0.0013277
54 | 0.98758 | -0.23799 | 0.0086298 | 0.0021628
55 | 0.99008 | -0.18903 | 0.0035465 | 0.00088883
56 | 0.98924 | -0.20518 | 0.0038996 | 0.00097733
57 | 0.99291 | -0.13492 | 0 | 0
58 | 0.9879 | -0.23099 | 0.0082086 | 0.0020573
59 | 0.99422 | -0.10991 | 0.0036017 | 0.00090268
60 | 0.99198 | -0.15285 | 0 | 0
61 | 0.98589 | -0.26979 | 0.0052452 | 0.0013146
62 | 0.99422 | -0.10984 | 0.0035883 | 0.0008993
63 | 0.99042 | -0.18291 | 0.0041469 | 0.0010393
64 | 0.99422 | -0.1098 | 0.0067627 | 0.0016949
65 | 0.98987 | -0.19369 | 0.0029727 | 0.00074502
66 | 0.98861 | -0.21812 | 0 | 0
67 | 0.9894 | -0.20263 | 0.0039195 | 0.00098232
68 | 0.98853 | -0.21956 | 0.0060639 | 0.0015197
69 | 0.99854 | -0.027917 | 0.0038456 | 0.00096379
70 | 0.99848 | -0.029155 | 0.012251 | 0.0030704
71 | 0.99547 | -0.085953 | 0 | 0
72 | 0.99634 | -0.069421 | 0.0041561 | 0.0010416
73 | 0.99641 | -0.068157 | 0.0076478 | 0.0019167
74 | 0.97774 | -0.429 | 0.0037329 | 0.00093554
75 | 0.97749 | -0.43404 | 0.0057085 | 0.0014307
76 | 0.9845 | -0.29672 | 0 | 0
77 | 0.98414 | -0.30375 | 0 | 0
78 | 0.98389 | -0.30853 | 0.0013242 | 0.00033189
79 | 0.97702 | -0.4427 | 0.0058427 | 0.0014643
80 | 0.98387 | -0.30905 | 0.002256 | 0.0005654
81 | 0.97679 | -0.44773 | 0.0047591 | 0.0011927
82 | 0.97663 | -0.4509 | 0.005937 | 0.001488
83 | 0.97693 | -0.44504 | 0.0037282 | 0.00093437
84 | 0.97658 | -0.45194 | 0.0035714 | 0.00089508
85 | 0.97704 | -0.44277 | 0.0041094 | 0.0010299
86 | 0.97656 | -0.45231 | 0.0034916 | 0.00087509
87 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.021191 | -0.0053127 | 0.021194 | 0.0053147 | 3.2993e-06 | 2.0006e-06 | 0.031888 | 0.031888 | 0.031888 | 0.98886 | -0.2131 | 0.98903 | -0.20983 | 8.7605
1 | 0.01704 | 0.0042724 | -0.017037 | -0.0042708 | 2.7997e-06 | 1.6462e-06 | 0.025642 | 0.025642 | 0.025642 | 0.98886 | -0.2131 | 0.98868 | -0.21655 | 7.0445
2 | -0.025857 | -0.0064833 | 0.025862 | 0.0064862 | 4.5735e-06 | 2.8236e-06 | 0.038904 | 0.038904 | 0.038904 | 0.98903 | -0.20983 | 0.98922 | -0.20612 | 10.6878
3 | 0.014873 | 0.0037283 | -0.014872 | -0.0037276 | 1.2481e-06 | 7.1359e-07 | 0.022385 | 0.022385 | 0.022385 | 0.98868 | -0.21655 | 0.98859 | -0.21831 | 6.1496
4 | -0.027718 | -0.0069513 | 0.02772 | 0.0069527 | 2.2153e-06 | 1.3742e-06 | 0.041695 | 0.041695 | 0.041695 | 0.98922 | -0.20612 | 0.98931 | -0.20445 | 11.4547
5 | 0.011573 | 0.0029008 | -0.011571 | -0.0029 | 1.5309e-06 | 8.0732e-07 | 0.017419 | 0.017419 | 0.017419 | 0.98859 | -0.21831 | 0.98845 | -0.22109 | 4.7855
6 | -0.029559 | -0.0074137 | 0.029567 | 0.0074188 | 8.1978e-06 | 5.1046e-06 | 0.044462 | 0.044462 | 0.044462 | 0.98931 | -0.20445 | 0.98961 | -0.19863 | 12.2148
7 | -0.032781 | -0.0082243 | 0.032786 | 0.008227 | 4.432e-06 | 2.774e-06 | 0.049295 | 0.049295 | 0.049295 | 0.98961 | -0.19863 | 0.98975 | -0.19579 | 13.5425
8 | -0.0064082 | -0.001606 | 0.0064085 | 0.0016061 | 3.2928e-07 | 8.4932e-08 | 0.0095524 | 0.0095524 | 0.0095524 | 0.99823 | -0.033941 | 0.99829 | -0.032863 | 2.6243
9 | -0.017608 | -0.0044131 | 0.017612 | 0.0044155 | 4.046e-06 | 2.3846e-06 | 0.026246 | 0.026246 | 0.026246 | 0.99829 | -0.032863 | 0.99854 | -0.028041 | 7.2106
10 | -0.019808 | -0.0049658 | 0.019814 | 0.0049694 | 5.9985e-06 | 3.5988e-06 | 0.029519 | 0.029519 | 0.029519 | 0.99854 | -0.028041 | 0.99887 | -0.021687 | 8.1096
11 | -0.037756 | -0.0094679 | 0.03776 | 0.0094706 | 4.2838e-06 | 2.6944e-06 | 0.056247 | 0.056247 | 0.056247 | 0.99887 | -0.021687 | 0.99899 | -0.019307 | 15.4524
12 | 0.017941 | 0.0044985 | -0.017936 | -0.0044956 | 4.8904e-06 | 2.891e-06 | 0.026728 | 0.026728 | 0.026728 | 0.99887 | -0.021687 | 0.99857 | -0.027409 | 7.3429
13 | 0.012851 | 0.0032209 | -0.01285 | -0.0032205 | 6.7363e-07 | 3.7017e-07 | 0.01939 | 0.019391 | 0.019391 | 0.98615 | -0.26588 | 0.98609 | -0.26698 | 5.3271
14 | -0.012851 | -0.0032209 | 0.012851 | 0.0032211 | 4.3792e-07 | 2.4064e-07 | 0.01939 | 0.01939 | 0.01939 | 0.98615 | -0.26588 | 0.98619 | -0.26517 | 5.3271
15 | 0.0081267 | 0.0020368 | -0.0081264 | -0.0020367 | 2.7864e-07 | 1.153e-07 | 0.012263 | 0.012263 | 0.012263 | 0.98609 | -0.26698 | 0.98606 | -0.2677 | 3.369
16 | -0.017633 | -0.0044197 | 0.017635 | 0.0044206 | 1.4697e-06 | 8.6994e-07 | 0.026606 | 0.026606 | 0.026606 | 0.98619 | -0.26517 | 0.98628 | -0.26342 | 7.3094
17 | -0.040137 | -0.010066 | 0.04016 | 0.010081 | 2.2893e-05 | 1.4428e-05 | 0.059788 | 0.059788 | 0.059788 | 0.99899 | -0.019307 | 0.99961 | -0.0073478 | 16.4252
18 | 0.016098 | 0.0040348 | -0.016097 | -0.0040346 | 3.9017e-07 | 2.2605e-07 | 0.023988 | 0.023988 | 0.023988 | 0.99857 | -0.027409 | 0.99854 | -0.027917 | 6.5902
19 | -0.0039193 | -0.00098228 | 0.0039195 | 0.00098223 | 1.3101e-07 | -4.464e-08 | 0.0059019 | 0.0059019 | 0.0059019 | 0.98815 | -0.2269 | 0.98819 | -0.2262 | 1.6214
20 | 0.069586 | 0.017478 | -0.069546 | -0.017453 | 3.9138e-05 | 2.4926e-05 | 0.1048 | 0.1048 | 0.1048 | 0.98819 | -0.2262 | 0.98758 | -0.23799 | 28.7901
21 | -0.073505 | -0.018461 | 0.073533 | 0.018479 | 2.8348e-05 | 1.8064e-05 | 0.1107 | 0.1107 | 0.1107 | 0.98819 | -0.2262 | 0.98861 | -0.21812 | 30.4114
22 | 0.035225 | 0.008898 | -0.035095 | -0.0088163 | 0.00013004 | 8.1688e-05 | 0.053365 | 0.053365 | 0.053365 | 0.98266 | -0.33289 | 0.9787 | -0.41022 | 14.6608
23 | -0.035225 | -0.008898 | 0.035258 | 0.0089187 | 3.2974e-05 | 2.0712e-05 | 0.053365 | 0.053365 | 0.053365 | 0.98266 | -0.33289 | 0.98367 | -0.31338 | 14.6606
24 | 0.035095 | 0.0088163 | -0.035063 | -0.0087966 | 3.1424e-05 | 1.9742e-05 | 0.053365 | 0.053365 | 0.053365 | 0.9787 | -0.41022 | 0.97774 | -0.429 | 14.6608
25 | -0.040533 | -0.010241 | 0.040555 | 0.010255 | 2.2638e-05 | 1.4284e-05 | 0.061344 | 0.061344 | 0.061344 | 0.98367 | -0.31338 | 0.98427 | -0.30173 | 16.8528
26 | 0.0087839 | 0.0022018 | -0.0087823 | -0.0022011 | 1.6277e-06 | 7.2657e-07 | 0.013254 | 0.013254 | 0.013254 | 0.98614 | -0.26598 | 0.98595 | -0.26987 | 3.6413
27 | -0.0087839 | -0.0022018 | 0.0087871 | 0.0022032 | 3.186e-06 | 1.4218e-06 | 0.013254 | 0.013254 | 0.013254 | 0.98614 | -0.26598 | 0.98654 | -0.25837 | 3.6413
28 | -0.0087871 | -0.0022032 | 0.0087879 | 0.0022035 | 7.769e-07 | 3.4662e-07 | 0.013254 | 0.013254 | 0.013254 | 0.98654 | -0.25837 | 0.98663 | -0.25651 | 3.6412
29 | -0.022836 | -0.0057242 | 0.02284 | 0.0057266 | 3.8154e-06 | 2.3325e-06 | 0.034454 | 0.034454 | 0.034454 | 0.98628 | -0.26342 | 0.98646 | -0.25991 | 9.4654
30 | -0.11482 | -0.02929 | 0.1149 | 0.029338 | 7.5159e-05 | 4.8013e-05 | 0.17157 | 0.17157 | 0.17157 | 0.99694 | -0.05808 | 0.99765 | -0.044536 | 47.1334
31 | 0.11122 | 0.028388 | -0.1111 | -0.028306 | 0.0001274 | 8.1376e-05 | 0.16619 | 0.16619 | 0.16619 | 0.99694 | -0.05808 | 0.99569 | -0.081817 | 45.6576
32 | -0.11731 | -0.029942 | 0.11756 | 0.030104 | 0.00025302 | 0.00016165 | 0.17516 | 0.17516 | 0.17516 | 0.99765 | -0.044536 | 1 | 0 | 48.1215
33 | 0.1111 | 0.028306 | -0.11059 | -0.027981 | 0.00050953 | 0.00032546 | 0.16619 | 0.16619 | 0.16619 | 0.99569 | -0.081817 | 0.9907 | -0.17735 | 45.6576
34 | 0.28639 | 0.073137 | -0.28629 | -0.073072 | 0.00010168 | 6.4898e-05 | 0.42663 | 0.42663 | 0.42663 | 1 | 0 | 0.99961 | -0.0073478 | 39.0691
35 | 0.036119 | 0.0090744 | -0.036087 | -0.0090545 | 3.1764e-05 | 1.9959e-05 | 0.054258 | 0.054258 | 0.054258 | 0.9907 | -0.17735 | 0.98975 | -0.19579 | 14.906
36 | 0.074468 | 0.018906 | -0.074415 | -0.018873 | 5.2669e-05 | 3.3564e-05 | 0.11194 | 0.11194 | 0.11194 | 0.9907 | -0.17735 | 0.98994 | -0.19206 | 30.7517
37 | 0.24613 | 0.062991 | -0.24581 | -0.062786 | 0.00032207 | 0.00020537 | 0.36685 | 0.36685 | 0.36685 | 0.99961 | -0.0073478 | 0.99818 | -0.034412 | 33.5941
38 | 0.07167 | 0.018185 | -0.071669 | -0.018184 | 1.2439e-06 | 7.9242e-07 | 0.10781 | 0.10781 | 0.10781 | 0.98994 | -0.19206 | 0.98992 | -0.19242 | 29.618
39 | 0.24251 | 0.061959 | -0.24211 | -0.061707 | 0.000395 | 0.00025186 | 0.36193 | 0.36193 | 0.36193 | 0.99818 | -0.034412 | 0.99641 | -0.068157 | 33.1436
40 | -0.0028661 | -0.0007183 | 0.0028661 | 0.00071824 | 5.1297e-08 | -6.3994e-08 | 0.004285 | 0.0042849 | 0.004285 | 0.99528 | -0.089675 | 0.9953 | -0.089299 | 1.1772
41 | -0.0069996 | -0.0017542 | 0.0070007 | 0.0017545 | 1.1157e-06 | 3.609e-07 | 0.010465 | 0.010464 | 0.010465 | 0.9953 | -0.089299 | 0.99547 | -0.085953 | 2.8749
42 | 0.092117 | 0.023247 | -0.091703 | -0.022983 | 0.00041357 | 0.00026397 | 0.13965 | 0.13965 | 0.13965 | 0.98197 | -0.34572 | 0.97716 | -0.43992 | 38.3642
43 | -0.092117 | -0.023247 | 0.092348 | 0.023394 | 0.00023111 | 0.00014751 | 0.13965 | 0.13965 | 0.13965 | 0.98197 | -0.34572 | 0.98466 | -0.29347 | 38.3641
44 | 0.0058434 | 0.0014645 | -0.0058427 | -0.0014643 | 7.7272e-07 | 1.686e-07 | 0.0088984 | 0.0088985 | 0.0088985 | 0.97716 | -0.43992 | 0.97702 | -0.4427 | 2.4446
45 | 0.0035828 | 0.00089583 | -0.0035823 | -0.00089612 | 5.5296e-07 | -2.8596e-07 | 0.0054136 | 0.0054138 | 0.0054138 | 0.98466 | -0.29347 | 0.9845 | -0.29672 | 1.4873
46 | -0.095931 | -0.02429 | 0.09604 | 0.02436 | 0.00010925 | 6.9744e-05 | 0.14506 | 0.14506 | 0.14506 | 0.98466 | -0.29347 | 0.98589 | -0.26979 | 39.8513
47 | 0.069163 | 0.017556 | -0.069066 | -0.017494 | 9.7117e-05 | 6.1848e-05 | 0.10404 | 0.10404 | 0.10404 | 0.98992 | -0.19242 | 0.9884 | -0.22165 | 28.5832
48 | 0.051123 | 0.012906 | -0.051118 | -0.012902 | 5.5726e-06 | 3.5348e-06 | 0.077313 | 0.077313 | 0.077313 | 0.98438 | -0.29946 | 0.98427 | -0.30173 | 21.2397
49 | -0.055706 | -0.014054 | 0.055743 | 0.014078 | 3.7247e-05 | 2.366e-05 | 0.084239 | 0.084239 | 0.084239 | 0.98438 | -0.29946 | 0.9851 | -0.2855 | 23.1426
50 | -0.058927 | -0.014876 | 0.058944 | 0.014887 | 1.7416e-05 | 1.1072e-05 | 0.089049 | 0.089049 | 0.089049 | 0.9851 | -0.2855 | 0.98542 | -0.27933 | 24.464
51 | -0.065799 | -0.016605 | 0.065869 | 0.016649 | 6.9229e-05 | 4.4068e-05 | 0.0994 | 0.0994 | 0.0994 | 0.98542 | -0.27933 | 0.98655 | -0.25739 | 27.3077
52 | -0.065869 | -0.016649 | 0.065982 | 0.016721 | 0.00011308 | 7.1981e-05 | 0.0994 | 0.0994 | 0.0994 | 0.98655 | -0.25739 | 0.9884 | -0.22165 | 27.3076
53 | 0.027824 | 0.0069769 | -0.027821 | -0.0069748 | 3.302e-06 | 2.0495e-06 | 0.041967 | 0.041967 | 0.041967 | 0.98658 | -0.25742 | 0.98646 | -0.25991 | 11.5294
54 | -0.032544 | -0.0081599 | 0.032549 | 0.0081629 | 4.8566e-06 | 3.0396e-06 | 0.049086 | 0.049086 | 0.049086 | 0.98658 | -0.25742 | 0.98674 | -0.25429 | 13.4853
55 | -0.037055 | -0.0092921 | 0.037068 | 0.0093005 | 1.3449e-05 | 8.4607e-06 | 0.05588 | 0.05588 | 0.05588 | 0.98674 | -0.25429 | 0.98714 | -0.24668 | 15.3518
56 | 0.018528 | 0.0046476 | -0.018519 | -0.0046424 | 8.6826e-06 | 5.1776e-06 | 0.02793 | 0.02793 | 0.02793 | 0.98714 | -0.24668 | 0.98663 | -0.25651 | 7.6732
57 | -0.055596 | -0.013948 | 0.055616 | 0.013961 | 2.0334e-05 | 1.2915e-05 | 0.083811 | 0.083811 | 0.083811 | 0.98714 | -0.24668 | 0.98753 | -0.23901 | 23.0249
58 | -0.060914 | -0.015289 | 0.060917 | 0.015291 | 2.9603e-06 | 1.8826e-06 | 0.091793 | 0.091793 | 0.091793 | 0.98753 | -0.23901 | 0.98758 | -0.23799 | 25.2179
59 | 0.11381 | 0.028974 | -0.11372 | -0.028917 | 8.853e-05 | 5.6556e-05 | 0.17121 | 0.17121 | 0.17121 | 0.99008 | -0.18903 | 0.98924 | -0.20518 | 47.0344
60 | -0.11735 | -0.029863 | 0.11766 | 0.030059 | 0.00030698 | 0.00019613 | 0.17654 | 0.17654 | 0.17654 | 0.99008 | -0.18903 | 0.99291 | -0.13492 | 48.4987
61 | 0.10982 | 0.02794 | -0.10968 | -0.027853 | 0.00013642 | 8.7137e-05 | 0.16534 | 0.16534 | 0.16534 | 0.98924 | -0.20518 | 0.9879 | -0.23099 | 45.4229
62 | -0.20865 | -0.053046 | 0.2089 | 0.053207 | 0.00025171 | 0.00016074 | 0.31295 | 0.31295 | 0.31295 | 0.99291 | -0.13492 | 0.99422 | -0.10991 | 42.9881
63 | 0.090985 | 0.022987 | -0.090907 | -0.022937 | 7.8135e-05 | 4.9861e-05 | 0.13642 | 0.13642 | 0.13642 | 0.99291 | -0.13492 | 0.99198 | -0.15285 | 37.4777
64 | 0.10147 | 0.025795 | -0.10129 | -0.025675 | 0.00018923 | 0.00012083 | 0.15298 | 0.15298 | 0.15298 | 0.9879 | -0.23099 | 0.98589 | -0.26979 | 42.0262
65 | -0.2125 | -0.054109 | 0.2125 | 0.05411 | 7.0847e-07 | 4.5124e-07 | 0.31834 | 0.31834 | 0.31834 | 0.99422 | -0.10991 | 0.99422 | -0.10984 | 29.1524
66 | 0.090907 | 0.022937 | -0.090776 | -0.022854 | 0.00013064 | 8.3371e-05 | 0.13642 | 0.13642 | 0.13642 | 0.99198 | -0.15285 | 0.99042 | -0.18291 | 37.4777
67 | -0.21609 | -0.055009 | 0.21609 | 0.055009 | 3.7815e-07 | 2.409e-07 | 0.32371 | 0.32371 | 0.32371 | 0.99422 | -0.10984 | 0.99422 | -0.1098 | 29.6442
68 | 0.086629 | 0.021815 | -0.086584 | -0.021786 | 4.4634e-05 | 2.8475e-05 | 0.13019 | 0.13019 | 0.13019 | 0.99042 | -0.18291 | 0.98987 | -0.19369 | 35.7661
69 | -0.22285 | -0.056704 | 0.22311 | 0.056868 | 0.00025647 | 0.00016343 | 0.33384 | 0.33384 | 0.33384 | 0.99422 | -0.1098 | 0.99547 | -0.085953 | 30.5711
70 | 0.083612 | 0.021041 | -0.083576 | -0.021018 | 3.5693e-05 | 2.2766e-05 | 0.12572 | 0.12572 | 0.12572 | 0.98987 | -0.19369 | 0.9894 | -0.20263 | 34.5385
71 | -0.079598 | -0.019998 | 0.079657 | 0.020036 | 5.8887e-05 | 3.7547e-05 | 0.11983 | 0.11983 | 0.11983 | 0.98861 | -0.21812 | 0.9894 | -0.20263 | 32.9191
72 | 0.0060643 | 0.0015198 | -0.0060639 | -0.0015197 | 4.1612e-07 | 9.5559e-08 | 0.0091278 | 0.0091278 | 0.0091278 | 0.98861 | -0.21812 | 0.98853 | -0.21956 | 2.5076
73 | 0.012252 | 0.0030708 | -0.012251 | -0.0030704 | 7.2209e-07 | 3.8658e-07 | 0.018258 | 0.018258 | 0.018258 | 0.99854 | -0.027917 | 0.99848 | -0.029155 | 5.0159
74 | -0.23011 | -0.058622 | 0.23029 | 0.058739 | 0.0001837 | 0.00011708 | 0.3443 | 0.3443 | 0.3443 | 0.99547 | -0.085953 | 0.99634 | -0.069421 | 31.5293
75 | -0.23445 | -0.059781 | 0.23446 | 0.05979 | 1.4303e-05 | 9.1173e-06 | 0.35051 | 0.35051 | 0.35051 | 0.99634 | -0.069421 | 0.99641 | -0.068157 | 32.0977
76 | 0.03133 | 0.0078611 | -0.031323 | -0.0078563 | 7.5295e-06 | 4.7081e-06 | 0.047684 | 0.047684 | 0.047684 | 0.97774 | -0.429 | 0.97749 | -0.43404 | 13.1001
77 | 0.025614 | 0.0064257 | -0.025604 | -0.0064191 | 1.0651e-05 | 6.5823e-06 | 0.038995 | 0.038995 | 0.038995 | 0.97749 | -0.43404 | 0.97704 | -0.44277 | 10.7128
78 | 0.0035823 | 0.00089612 | -0.0035811 | -0.00089674 | 1.1987e-06 | -6.1897e-07 | 0.0054138 | 0.0054143 | 0.0054143 | 0.9845 | -0.29672 | 0.98414 | -0.30375 | 1.4875
79 | 0.0035811 | 0.00089674 | -0.0035803 | -0.00089716 | 8.1535e-07 | -4.203e-07 | 0.0054143 | 0.0054147 | 0.0054147 | 0.98414 | -0.30375 | 0.98389 | -0.30853 | 1.4875
80 | 0.002256 | 0.00056527 | -0.002256 | -0.0005654 | 5.5271e-08 | -1.2542e-07 | 0.0034119 | 0.003412 | 0.003412 | 0.98389 | -0.30853 | 0.98387 | -0.30905 | 0.93735
81 | 0.013002 | 0.0032593 | -0.013 | -0.0032582 | 1.9658e-06 | 1.0909e-06 | 0.019808 | 0.019808 | 0.019808 | 0.97679 | -0.44773 | 0.97663 | -0.4509 | 5.4417
82 | -0.017762 | -0.004452 | 0.017764 | 0.0044534 | 2.2771e-06 | 1.3535e-06 | 0.027058 | 0.027058 | 0.027058 | 0.97679 | -0.44773 | 0.97693 | -0.44504 | 7.4334
83 | 0.0070635 | 0.0017703 | -0.0070631 | -0.0017701 | 3.4834e-07 | 1.2258e-07 | 0.010762 | 0.010762 | 0.010762 | 0.97663 | -0.4509 | 0.97658 | -0.45194 | 2.9566
84 | -0.021492 | -0.0053878 | 0.021494 | 0.0053892 | 2.3251e-06 | 1.4156e-06 | 0.032736 | 0.032736 | 0.032736 | 0.97693 | -0.44504 | 0.97704 | -0.44277 | 8.9934
85 | 0.0034917 | 0.00087505 | -0.0034916 | -0.00087509 | 6.3089e-08 | -3.3987e-08 | 0.0053203 | 0.0053203 | 0.0053203 | 0.97658 | -0.45194 | 0.97656 | -0.45231 | 1.4616

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40755 | 0.10373

## res_load
| p_mw | q_mvar
0 | 0.0041509 | 0.0010403
1 | 0.0046628 | 0.0011686
2 | 0.0021644 | 0.00054244
3 | 0.0018559 | 0.00046514
4 | 0.003299 | 0.00082681
5 | 0.0018394 | 0.00046101
6 | 0.011571 | 0.0029
7 | 0.0032139 | 0.00080549
8 | 0.0064082 | 0.001606
9 | 0.0112 | 0.0028069
10 | 0.002196 | 0.00055038
11 | 0.0047232 | 0.0011837
12 | 0.0047823 | 0.0011986
13 | 0.0023772 | 0.00059579
14 | 0.0018385 | 0.00046078
15 | 0.0039193 | 0.00098228
16 | 0.005275 | 0.001322
17 | 0.0087823 | 0.0022011
18 | 0.0081264 | 0.0020367
19 | 0.0052017 | 0.0013037
20 | 0.0035993 | 0.00090206
21 | 0.0024114 | 0.00060437
22 | 0.0019454 | 0.00048758
23 | 0.0033015 | 0.00082743
24 | 0.0027452 | 0.00068802
25 | 0.0033003 | 0.00082712
26 | 0.0028661 | 0.0007183
27 | 0.0041335 | 0.0010359
28 | 0.08586 | 0.021518
29 | 0.0025059 | 0.00062805
30 | 0.0045821 | 0.0011484
31 | 0.010563 | 0.0026472
32 | 0.0031843 | 0.00079806
33 | 0.0068548 | 0.001718
34 | 0.0030842 | 0.00077299
35 | 0.0047202 | 0.001183
36 | 0.0049806 | 0.0012482
37 | 0.0045054 | 0.0011292
38 | 0.0097312 | 0.0024389
39 | 0.0052976 | 0.0013277
40 | 0.0086298 | 0.0021628
41 | 0.0035465 | 0.00088883
42 | 0.0038996 | 0.00097733
43 | 0.0082086 | 0.0020573
44 | 0.0036017 | 0.00090268
45 | 0.0052452 | 0.0013146
46 | 0.0035883 | 0.0008993
47 | 0.0041469 | 0.0010393
48 | 0.0067627 | 0.0016949
49 | 0.0029727 | 0.00074502
50 | 0.0039195 | 0.00098232
51 | 0.0060639 | 0.0015197
52 | 0.0038456 | 0.00096379
53 | 0.012251 | 0.0030704
54 | 0.0041561 | 0.0010416
55 | 0.0076478 | 0.0019167
56 | 0.0037329 | 0.00093554
57 | 0.0057085 | 0.0014307
58 | 0.0013242 | 0.00033189
59 | 0.0058427 | 0.0014643
60 | 0.002256 | 0.0005654
61 | 0.0047591 | 0.0011927
62 | 0.005937 | 0.001488
63 | 0.0037282 | 0.00093437
64 | 0.0035714 | 0.00089508
65 | 0.0041094 | 0.0010299
66 | 0.0034916 | 0.00087509

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1