## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1632-68_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1632-68_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1632-68_0_4_node_21 | 0.4 | n |  | TRUE
3 | bus_LV_1632-68_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1632-68_0_4_node_33 | 0.4 | n |  | TRUE
5 | bus_LV_1632-68_0_4_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_1632-68_0_4_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_1632-68_0_4_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_1632-68_0_4_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_1632-68_0_4_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_1632-68_0_4_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_1632-68_0_4_node_3 | 0.4 | n |  | TRUE
12 | bus_LV_1632-68_0_4_node_4 | 0.4 | n |  | TRUE
13 | bus_LV_1632-68_0_4_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_1632-68_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1632-68_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1632-68_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1632-68_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1632-68_0_4_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1632-68_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1632-68_0_4_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1632-68_0_4_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1632-68_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1632-68_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_1632-68_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1632-68_0_4_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1632-68_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1632-68_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1632-68_0_4_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_1632-68_0_4_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_1632-68_0_4_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_1632-68_0_4_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_1632-68_0_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_1632-68_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1632-68_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_1632-68_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_1632-68_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_MV_224_0_node_65 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1632-68_0_4_load_0 | 0 | 0.0037712 | 0.00094515 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1632-68_0_4_load_33 | 4 | 0.012846 | 0.0032194 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1632-68_0_4_load_38 | 6 | 0.0022289 | 0.00055862 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1632-68_0_4_load_37 | 8 | 0.0022263 | 0.00055797 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1632-68_0_4_load_34 | 9 | 0.00097243 | 0.00024371 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1632-68_0_4_load_35 | 10 | 0.0041761 | 0.0010466 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1632-68_0_4_load_3 | 11 | 0.088517 | 0.022184 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1632-68_0_4_load_4 | 12 | 0.041317 | 0.010355 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1632-68_0_4_load_6 | 14 | 0.092912 | 0.023286 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1632-68_0_4_load_7 | 15 | 0.043496 | 0.010901 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1632-68_0_4_load_8 | 16 | 0.0032668 | 0.00081875 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1632-68_0_4_load_9 | 17 | 0.00076553 | 0.00019186 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1632-68_0_4_load_26 | 18 | 0.068252 | 0.017106 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1632-68_0_4_load_10 | 19 | 0.054844 | 0.013745 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1632-68_0_4_load_18 | 20 | 0.0011737 | 0.00029415 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1632-68_0_4_load_24 | 24 | 0.00043669 | 0.00010944 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1632-68_0_4_load_25 | 25 | 0.055256 | 0.013848 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1632-68_0_4_load_23 | 26 | 0.00038758 | 9.7137e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1632-68_0_4_load_12 | 28 | 0.048493 | 0.012154 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1632-68_0_4_load_29 | 31 | 0.00042151 | 0.00010564 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1632-68_0_4_load_27 | 32 | 0.0047955 | 0.0012019 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1632-68_0_4_load_28 | 33 | 0.0005878 | 0.00014732 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1632-68_0_4_load_31 | 35 | 0.020333 | 0.005096 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1632-68_0_4_load_30 | 36 | 0.0016797 | 0.00042098 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1632-68_0_4_line_0 |  | 0 | 1 | 0.046415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1632-68_0_4_line_1 |  | 0 | 2 | 0.038761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1632-68_0_4_line_2 |  | 1 | 3 | 0.022733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1632-68_0_4_line_3 |  | 2 | 4 | 0.0052861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1632-68_0_4_line_4 |  | 2 | 5 | 0.04418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1632-68_0_4_line_5 |  | 3 | 6 | 0.022518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1632-68_0_4_line_6 |  | 3 | 7 | 0.015867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1632-68_0_4_line_7 |  | 4 | 9 | 0.015325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1632-68_0_4_line_8 |  | 5 | 34 | 0.035248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1632-68_0_4_line_9 |  | 7 | 8 | 0.01458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1632-68_0_4_line_10 |  | 8 | 35 | 0.065757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1632-68_0_4_line_11 |  | 9 | 10 | 0.013313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1632-68_0_4_line_12 |  | 11 | 12 | 0.0031611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1632-68_0_4_line_13 |  | 11 | 13 | 0.012642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1632-68_0_4_line_14 |  | 12 | 14 | 0.013358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_1632-68_0_4_line_15 |  | 13 | 15 | 0.018271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_1632-68_0_4_line_16 |  | 13 | 16 | 0.012044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1632-68_0_4_line_17 |  | 13 | 17 | 0.01817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1632-68_0_4_line_18 |  | 14 | 18 | 0.0098965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1632-68_0_4_line_19 |  | 15 | 19 | 0.0054085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_1632-68_0_4_line_20 |  | 16 | 20 | 0.0016452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1632-68_0_4_line_21 |  | 17 | 21 | 0.0027854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1632-68_0_4_line_22 |  | 18 | 22 | 0.0097632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1632-68_0_4_line_23 |  | 19 | 23 | 0.0098606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1632-68_0_4_line_24 |  | 21 | 24 | 0.0075236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1632-68_0_4_line_25 |  | 22 | 32 | 0.025934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1632-68_0_4_line_26 |  | 23 | 25 | 0.0053214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1632-68_0_4_line_27 |  | 23 | 26 | 0.0071643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1632-68_0_4_line_28 |  | 24 | 30 | 0.01469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1632-68_0_4_line_29 |  | 25 | 27 | 0.011286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1632-68_0_4_line_30 |  | 27 | 29 | 0.011928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1632-68_0_4_line_31 |  | 28 | 29 | 0.0058289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1632-68_0_4_line_32 |  | 30 | 31 | 0.0073479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1632-68_0_4_line_33 |  | 31 | 33 | 0.013088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1632-68_0_4_line_34 |  | 32 | 34 | 0.0022224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1632-68_0_4_line_35 |  | 33 | 36 | 0.010573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1632-68_0_4_trafo_3 | 0.63 MVA 20/0.4 kV | 37 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2722866.8401 | 1213397.965 | 2722845.4469 | 1213439.1559
1 | 2722817.5194 | 1213466.0347 | 2722845.4469 | 1213439.1559
2 | 2722866.8401 | 1213397.965 | 2722847.8048 | 1213385.4521
3 | 2722817.5194 | 1213466.0347 | 2722812.8245 | 1213463.6055
4 | 2722813.6188 | 1213498.6017 | 2722815.9187 | 1213495.4022 | 2722828.6269 | 1213477.5502 | 2722830.1204 | 1213475.5016 | 2722820.4495 | 1213468.7639 | 2722817.5194 | 1213466.0347
5 | 2722847.8048 | 1213385.4521 | 2722832.9717 | 1213402.4263
6 | 2722847.8048 | 1213385.4521 | 2722834.5199 | 1213376.7161
7 | 2722812.8245 | 1213463.6055 | 2722812.6625 | 1213463.5217 | 2722810.9219 | 1213462.4405 | 2722800.044 | 1213455.1535
8 | 2722813.6188 | 1213498.6017 | 2722824.7308 | 1213505.1022 | 2722809.8553 | 1213518.2504 | 2722807.5399 | 1213519.248
9 | 2722834.5199 | 1213376.7161 | 2722825.683 | 1213380.3814 | 2722822.1961 | 1213384.0235
10 | 2722756.4504 | 1213382.7864 | 2722822.1961 | 1213384.0235
11 | 2722788.9835 | 1213447.7441 | 2722800.044 | 1213455.1535
12 | 2722765.6738 | 1213502.9232 | 2722763.2753 | 1213500.8643
13 | 2722753.6824 | 1213492.6297 | 2722763.2753 | 1213500.8643
14 | 2722765.6738 | 1213502.9232 | 2722768.2422 | 1213505.128 | 2722772.9119 | 1213513.9401
15 | 2722753.6824 | 1213492.6297 | 2722743.7027 | 1213497.5614 | 2722736.8852 | 1213499.6794
16 | 2722753.6824 | 1213492.6297 | 2722765.6736 | 1213491.4979
17 | 2722753.6824 | 1213492.6297 | 2722741.1188 | 1213484.298 | 2722738.145 | 1213483.4409
18 | 2722772.9119 | 1213513.9401 | 2722777.5458 | 1213522.6847
19 | 2722731.7202 | 1213501.284 | 2722736.8852 | 1213499.6794
20 | 2722765.6736 | 1213491.4979 | 2722765.6736 | 1213491.4979 | 2722767.3187 | 1213491.5189
21 | 2722735.4686 | 1213482.6694 | 2722738.145 | 1213483.4409
22 | 2722782.1173 | 1213531.3116 | 2722777.5458 | 1213522.6847
23 | 2722722.053 | 1213503.1535 | 2722729.9065 | 1213501.8475 | 2722731.7202 | 1213501.284
24 | 2722735.4686 | 1213482.6694 | 2722730.0847 | 1213477.414
25 | 2722782.1173 | 1213531.3116 | 2722794.2372 | 1213525.401 | 2722797.4736 | 1213523.5885 | 2722805.4992 | 1213520.1279
26 | 2722722.053 | 1213503.1535 | 2722717.2135 | 1213505.3662
27 | 2722722.053 | 1213503.1535 | 2722721.0228 | 1213496.0637
28 | 2722716.4055 | 1213472.6138 | 2722724.78 | 1213474.4208 | 2722729.4871 | 1213476.8307 | 2722730.0847 | 1213477.414
29 | 2722706.9492 | 1213510.0591 | 2722717.2135 | 1213505.3662
30 | 2722706.9492 | 1213510.0591 | 2722713.6683 | 1213519.9272
31 | 2722713.6683 | 1213519.9272 | 2722717.2068 | 1213524.5591
32 | 2722716.4055 | 1213472.6138 | 2722723.1664 | 1213469.736
33 | 2722733.3316 | 1213462.1045 | 2722732.7266 | 1213463.4315 | 2722730.6981 | 1213465.6248 | 2722727.9426 | 1213467.703 | 2722723.1664 | 1213469.736
34 | 2722807.5399 | 1213519.248 | 2722805.4992 | 1213520.1279
35 | 2722734.4982 | 1213451.9369 | 2722735.1223 | 1213455.2078 | 2722734.8912 | 1213458.6835 | 2722733.3316 | 1213462.1045

## bus_geodata
| x | y | coords
0 | 2722845.4469 | 1213439.1559
1 | 2722866.8401 | 1213397.965
2 | 2722817.5194 | 1213466.0347
3 | 2722847.8048 | 1213385.4521
4 | 2722812.8245 | 1213463.6055
5 | 2722813.6188 | 1213498.6017
6 | 2722832.9717 | 1213402.4263
7 | 2722834.5199 | 1213376.7161
8 | 2722822.1961 | 1213384.0235
9 | 2722800.044 | 1213455.1535
10 | 2722788.9835 | 1213447.7441
11 | 2722763.2753 | 1213500.8643
12 | 2722765.6738 | 1213502.9232
13 | 2722753.6824 | 1213492.6297
14 | 2722772.9119 | 1213513.9401
15 | 2722736.8852 | 1213499.6794
16 | 2722765.6736 | 1213491.4979
17 | 2722738.145 | 1213483.4409
18 | 2722777.5458 | 1213522.6847
19 | 2722731.7202 | 1213501.284
20 | 2722767.3187 | 1213491.5189
21 | 2722735.4686 | 1213482.6694
22 | 2722782.1173 | 1213531.3116
23 | 2722722.053 | 1213503.1535
24 | 2722730.0847 | 1213477.414
25 | 2722717.2135 | 1213505.3662
26 | 2722721.0228 | 1213496.0637
27 | 2722706.9492 | 1213510.0591
28 | 2722717.2068 | 1213524.5591
29 | 2722713.6683 | 1213519.9272
30 | 2722716.4055 | 1213472.6138
31 | 2722723.1664 | 1213469.736
32 | 2722805.4992 | 1213520.1279
33 | 2722733.3316 | 1213462.1045
34 | 2722807.5399 | 1213519.248
35 | 2722756.4504 | 1213382.7864
36 | 2722734.4982 | 1213451.9369
37 | 2722753.6824 | 1213492.6297

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99109 | -0.17141 | 0.0037712 | 0.00094515
1 | 0.99003 | -0.19185 | 0 | 0
2 | 0.9921 | -0.15178 | 0 | 0
3 | 0.98951 | -0.20188 | 0 | 0
4 | 0.99201 | -0.15347 | 0.012846 | 0.0032194
5 | 0.99399 | -0.11543 | 0 | 0
6 | 0.98947 | -0.20278 | 0.0022289 | 0.00055862
7 | 0.98918 | -0.20826 | 0 | 0
8 | 0.98888 | -0.21412 | 0.0022263 | 0.00055797
9 | 0.99194 | -0.15487 | 0.00097243 | 0.00024371
10 | 0.99189 | -0.15585 | 0.0041761 | 0.0010466
11 | 1 | 0 | -0.46788 | -0.11746
12 | 0.99963 | -0.0069955 | 0.041317 | 0.010355
13 | 0.99879 | -0.023255 | 0 | 0
14 | 0.99834 | -0.031786 | 0.092912 | 0.023286
15 | 0.9971 | -0.055627 | 0.043496 | 0.010901
16 | 0.99874 | -0.024189 | 0.0032668 | 0.00081875
17 | 0.99872 | -0.024491 | 0.00076553 | 0.00019186
18 | 0.99726 | -0.052509 | 0.068252 | 0.017106
19 | 0.99671 | -0.063167 | 0.054844 | 0.013745
20 | 0.99874 | -0.024223 | 0.0011737 | 0.00029415
21 | 0.99871 | -0.024643 | 0 | 0
22 | 0.9968 | -0.061301 | 0 | 0
23 | 0.99577 | -0.0812 | 0 | 0
24 | 0.99869 | -0.025054 | 0.00043669 | 0.00010944
25 | 0.99527 | -0.09091 | 0.055256 | 0.013848
26 | 0.99577 | -0.081249 | 0.00038758 | 9.7137e-05
27 | 0.99477 | -0.10054 | 0 | 0
28 | 0.99399 | -0.11572 | 0.048493 | 0.012154
29 | 0.99424 | -0.11074 | 0 | 0
30 | 0.99866 | -0.025745 | 0 | 0
31 | 0.99864 | -0.02609 | 0.00042151 | 0.00010564
32 | 0.99558 | -0.084695 | 0.0047955 | 0.0012019
33 | 0.99861 | -0.026609 | 0.0005878 | 0.00014732
34 | 0.99549 | -0.086515 | 0 | 0
35 | 0.98765 | -0.23798 | 0.020333 | 0.005096
36 | 0.9986 | -0.02692 | 0.0016797 | 0.00042098
37 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.024861 | 0.0062567 | -0.024837 | -0.0062417 | 2.4263e-05 | 1.4931e-05 | 0.037336 | 0.037336 | 0.037336 | 0.99109 | -0.17141 | 0.99003 | -0.19185 | 10.2572
1 | -0.028632 | -0.0072018 | 0.028659 | 0.0072185 | 2.6873e-05 | 1.6699e-05 | 0.042998 | 0.042998 | 0.042998 | 0.99109 | -0.17141 | 0.9921 | -0.15178 | 11.8126
2 | 0.024837 | 0.0062417 | -0.024825 | -0.0062344 | 1.1884e-05 | 7.3133e-06 | 0.037336 | 0.037336 | 0.037336 | 0.99003 | -0.19185 | 0.98951 | -0.20188 | 10.2572
3 | 0.017996 | 0.0045106 | -0.017995 | -0.0045098 | 1.4442e-06 | 8.5606e-07 | 0.026992 | 0.026992 | 0.026992 | 0.9921 | -0.15178 | 0.99201 | -0.15347 | 7.4154
4 | -0.046655 | -0.011729 | 0.046737 | 0.01178 | 8.1156e-05 | 5.1368e-05 | 0.06999 | 0.069989 | 0.06999 | 0.9921 | -0.15178 | 0.99399 | -0.11543 | 19.2279
5 | 0.002229 | 0.00055839 | -0.0022289 | -0.00055862 | 9.4874e-08 | -2.2852e-07 | 0.0033519 | 0.003352 | 0.003352 | 0.98951 | -0.20188 | 0.98947 | -0.20278 | 0.92087
6 | 0.022596 | 0.005676 | -0.022589 | -0.0056718 | 6.872e-06 | 4.1943e-06 | 0.033984 | 0.033984 | 0.033984 | 0.98951 | -0.20188 | 0.98918 | -0.20826 | 9.3364
7 | 0.0051491 | 0.0012903 | -0.0051488 | -0.0012903 | 3.4281e-07 | 2.1566e-08 | 0.0077236 | 0.0077236 | 0.0077236 | 0.99201 | -0.15347 | 0.99194 | -0.15487 | 2.1219
8 | -0.046737 | -0.01178 | 0.046801 | 0.011821 | 6.4749e-05 | 4.0982e-05 | 0.069989 | 0.069989 | 0.069989 | 0.99399 | -0.11543 | 0.99549 | -0.086515 | 19.2279
9 | 0.022589 | 0.0056718 | -0.022583 | -0.005668 | 6.3146e-06 | 3.8543e-06 | 0.033984 | 0.033984 | 0.033984 | 0.98918 | -0.20826 | 0.98888 | -0.21412 | 9.3364
10 | 0.020357 | 0.00511 | -0.020333 | -0.005096 | 2.3142e-05 | 1.3968e-05 | 0.030634 | 0.030635 | 0.030635 | 0.98888 | -0.21412 | 0.98765 | -0.23798 | 8.4161
11 | 0.0041763 | 0.0010466 | -0.0041761 | -0.0010466 | 1.9595e-07 | -4.6439e-08 | 0.0062649 | 0.0062649 | 0.0062649 | 0.99194 | -0.15487 | 0.99189 | -0.15585 | 1.7211
12 | 0.25462 | 0.064115 | -0.25453 | -0.06406 | 8.5129e-05 | 5.44e-05 | 0.37898 | 0.37898 | 0.37898 | 1 | 0 | 0.99963 | -0.0069955 | 52.0581
13 | 0.21161 | 0.053344 | -0.21138 | -0.053194 | 0.00023519 | 0.00015019 | 0.31499 | 0.31499 | 0.31499 | 1 | 0 | 0.99879 | -0.023255 | 43.2678
14 | 0.21322 | 0.053705 | -0.21296 | -0.053544 | 0.00025245 | 0.00016122 | 0.31748 | 0.31748 | 0.31748 | 0.99963 | -0.0069955 | 0.99834 | -0.031786 | 43.6099
15 | 0.20304 | 0.051107 | -0.20273 | -0.050906 | 0.00031364 | 0.00020025 | 0.30258 | 0.30258 | 0.30258 | 0.99879 | -0.023255 | 0.9971 | -0.055627 | 41.5627
16 | 0.0044407 | 0.0011128 | -0.0044405 | -0.0011129 | 1.9769e-07 | -3.11e-08 | 0.0066158 | 0.0066159 | 0.0066159 | 0.99879 | -0.023255 | 0.99874 | -0.024189 | 1.8176
17 | 0.0038918 | 0.00097461 | -0.0038915 | -0.0009747 | 2.2905e-07 | -9.1197e-08 | 0.0057978 | 0.0057979 | 0.0057979 | 0.99879 | -0.023255 | 0.99872 | -0.024491 | 1.5928
18 | 0.12005 | 0.030258 | -0.11993 | -0.030182 | 0.0001189 | 7.597e-05 | 0.179 | 0.179 | 0.179 | 0.99834 | -0.031786 | 0.99726 | -0.052509 | 49.1747
19 | 0.15923 | 0.040005 | -0.15918 | -0.039969 | 5.7281e-05 | 3.6519e-05 | 0.23766 | 0.23766 | 0.23766 | 0.9971 | -0.055627 | 0.99671 | -0.063167 | 32.6463
20 | 0.0011737 | 0.00029413 | -0.0011737 | -0.00029415 | 1.8865e-09 | -2.0322e-08 | 0.0017486 | 0.0017486 | 0.0017486 | 0.99874 | -0.024189 | 0.99874 | -0.024223 | 0.48039
21 | 0.003126 | 0.00078284 | -0.003126 | -0.00078286 | 2.2656e-08 | -2.1949e-08 | 0.0046573 | 0.0046573 | 0.0046573 | 0.99872 | -0.024491 | 0.99871 | -0.024643 | 1.2795
22 | 0.051681 | 0.013076 | -0.051659 | -0.013063 | 2.1796e-05 | 1.3822e-05 | 0.077157 | 0.077157 | 0.077157 | 0.99726 | -0.052509 | 0.9968 | -0.061301 | 21.1969
23 | 0.10433 | 0.026223 | -0.10424 | -0.026166 | 8.9741e-05 | 5.7306e-05 | 0.15579 | 0.15579 | 0.15579 | 0.99671 | -0.063167 | 0.99577 | -0.0812 | 42.7984
24 | 0.003126 | 0.00078286 | -0.0031259 | -0.00078292 | 6.1197e-08 | -5.9283e-08 | 0.0046573 | 0.0046573 | 0.0046573 | 0.99871 | -0.024643 | 0.99869 | -0.025054 | 1.2795
25 | 0.051659 | 0.013063 | -0.051601 | -0.013026 | 5.7895e-05 | 3.6715e-05 | 0.077157 | 0.077157 | 0.077157 | 0.9968 | -0.061301 | 0.99558 | -0.084695 | 21.1969
26 | 0.10385 | 0.026069 | -0.10381 | -0.026038 | 4.8071e-05 | 3.0696e-05 | 0.15521 | 0.15521 | 0.15521 | 0.99577 | -0.0812 | 0.99527 | -0.09091 | 42.6393
27 | 0.00038758 | 9.7044e-05 | -0.00038758 | -9.7137e-05 | 9.0116e-10 | -9.2621e-08 | 0.00057914 | 0.00057917 | 0.00057917 | 0.99577 | -0.0812 | 0.99577 | -0.081249 | 0.15911
28 | 0.0026892 | 0.00067347 | -0.0026892 | -0.00067361 | 8.844e-08 | -1.3562e-07 | 0.0040067 | 0.0040068 | 0.0040068 | 0.99869 | -0.025054 | 0.99866 | -0.025745 | 1.1008
29 | 0.048551 | 0.01219 | -0.048528 | -0.012176 | 2.2305e-05 | 1.4128e-05 | 0.072595 | 0.072595 | 0.072595 | 0.99527 | -0.09091 | 0.99477 | -0.10054 | 19.9437
30 | 0.048528 | 0.012176 | -0.048505 | -0.012161 | 2.3573e-05 | 1.4932e-05 | 0.072595 | 0.072595 | 0.072595 | 0.99477 | -0.10054 | 0.99424 | -0.11074 | 19.9438
31 | -0.048493 | -0.012154 | 0.048505 | 0.012161 | 1.1519e-05 | 7.2969e-06 | 0.072595 | 0.072595 | 0.072595 | 0.99399 | -0.11572 | 0.99424 | -0.11074 | 19.9438
32 | 0.0026892 | 0.00067361 | -0.0026891 | -0.00067368 | 4.4237e-08 | -6.7827e-08 | 0.0040068 | 0.0040068 | 0.0040068 | 0.99866 | -0.025745 | 0.99864 | -0.02609 | 1.1008
33 | 0.0022676 | 0.00056804 | -0.0022675 | -0.00056817 | 5.603e-08 | -1.3538e-07 | 0.0033787 | 0.0033788 | 0.0033788 | 0.99864 | -0.02609 | 0.99861 | -0.026609 | 0.92824
34 | 0.046805 | 0.011824 | -0.046801 | -0.011821 | 4.0824e-06 | 2.5838e-06 | 0.069989 | 0.069989 | 0.069989 | 0.99558 | -0.084695 | 0.99549 | -0.086515 | 19.2278
35 | 0.0016797 | 0.00042085 | -0.0016797 | -0.00042098 | 2.4839e-08 | -1.2243e-07 | 0.0025029 | 0.002503 | 0.002503 | 0.99861 | -0.026609 | 0.9986 | -0.02692 | 0.68763

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.5564 | 0.13964

## res_load
| p_mw | q_mvar
0 | 0.0037712 | 0.00094515
1 | 0.012846 | 0.0032194
2 | 0.0022289 | 0.00055862
3 | 0.0022263 | 0.00055797
4 | 0.00097243 | 0.00024371
5 | 0.0041761 | 0.0010466
6 | 0.088517 | 0.022184
7 | 0.041317 | 0.010355
8 | 0.092912 | 0.023286
9 | 0.043496 | 0.010901
10 | 0.0032668 | 0.00081875
11 | 0.00076553 | 0.00019186
12 | 0.068252 | 0.017106
13 | 0.054844 | 0.013745
14 | 0.0011737 | 0.00029415
15 | 0.00043669 | 0.00010944
16 | 0.055256 | 0.013848
17 | 0.00038758 | 9.7137e-05
18 | 0.048493 | 0.012154
19 | 0.00042151 | 0.00010564
20 | 0.0047955 | 0.0012019
21 | 0.0005878 | 0.00014732
22 | 0.020333 | 0.005096
23 | 0.0016797 | 0.00042098

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1