## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1632-69_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1632-69_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1632-69_0_4_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_1632-69_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1632-69_0_4_node_77 | 0.4 | n |  | TRUE
5 | bus_LV_1632-69_0_4_node_90 | 0.4 | n |  | TRUE
6 | bus_LV_1632-69_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1632-69_0_4_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_1632-69_0_4_node_36 | 0.4 | n |  | TRUE
9 | bus_LV_1632-69_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1632-69_0_4_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_1632-69_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1632-69_0_4_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_1632-69_0_4_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_1632-69_0_4_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_1632-69_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1632-69_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1632-69_0_4_node_63 | 0.4 | n |  | TRUE
18 | bus_LV_1632-69_0_4_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1632-69_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1632-69_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1632-69_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1632-69_0_4_node_55 | 0.4 | n |  | TRUE
23 | bus_LV_1632-69_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1632-69_0_4_node_52 | 0.4 | n |  | TRUE
25 | bus_LV_1632-69_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1632-69_0_4_node_45 | 0.4 | n |  | TRUE
27 | bus_LV_1632-69_0_4_node_86 | 0.4 | n |  | TRUE
28 | bus_LV_1632-69_0_4_node_78 | 0.4 | n |  | TRUE
29 | bus_LV_1632-69_0_4_node_72 | 0.4 | n |  | TRUE
30 | bus_LV_1632-69_0_4_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_1632-69_0_4_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_1632-69_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_1632-69_0_4_node_11 | 0.4 | n |  | TRUE
34 | bus_LV_1632-69_0_4_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_1632-69_0_4_node_13 | 0.4 | n |  | TRUE
36 | bus_LV_1632-69_0_4_node_14 | 0.4 | n |  | TRUE
37 | bus_LV_1632-69_0_4_node_83 | 0.4 | n |  | TRUE
38 | bus_LV_1632-69_0_4_node_71 | 0.4 | n |  | TRUE
39 | bus_LV_1632-69_0_4_node_81 | 0.4 | n |  | TRUE
40 | bus_LV_1632-69_0_4_node_70 | 0.4 | n |  | TRUE
41 | bus_LV_1632-69_0_4_node_17 | 0.4 | n |  | TRUE
42 | bus_LV_1632-69_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1632-69_0_4_node_62 | 0.4 | n |  | TRUE
44 | bus_LV_1632-69_0_4_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_1632-69_0_4_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_1632-69_0_4_node_30 | 0.4 | n |  | TRUE
47 | bus_LV_1632-69_0_4_node_21 | 0.4 | n |  | TRUE
48 | bus_LV_1632-69_0_4_node_22 | 0.4 | n |  | TRUE
49 | bus_LV_1632-69_0_4_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_1632-69_0_4_node_24 | 0.4 | n |  | TRUE
51 | bus_LV_1632-69_0_4_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_1632-69_0_4_node_26 | 0.4 | n |  | TRUE
53 | bus_LV_1632-69_0_4_node_27 | 0.4 | n |  | TRUE
54 | bus_LV_1632-69_0_4_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_1632-69_0_4_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_1632-69_0_4_node_80 | 0.4 | n |  | TRUE
57 | bus_LV_1632-69_0_4_node_84 | 0.4 | n |  | TRUE
58 | bus_LV_1632-69_0_4_node_29 | 0.4 | n |  | TRUE
59 | bus_LV_1632-69_0_4_node_33 | 0.4 | n |  | TRUE
60 | bus_LV_1632-69_0_4_node_69 | 0.4 | n |  | TRUE
61 | bus_LV_1632-69_0_4_node_68 | 0.4 | n |  | TRUE
62 | bus_LV_1632-69_0_4_node_73 | 0.4 | n |  | TRUE
63 | bus_LV_1632-69_0_4_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_1632-69_0_4_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_1632-69_0_4_node_42 | 0.4 | n |  | TRUE
66 | bus_LV_1632-69_0_4_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_1632-69_0_4_node_74 | 0.4 | n |  | TRUE
68 | bus_LV_1632-69_0_4_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_1632-69_0_4_node_47 | 0.4 | n |  | TRUE
70 | bus_LV_1632-69_0_4_node_48 | 0.4 | n |  | TRUE
71 | bus_LV_1632-69_0_4_node_49 | 0.4 | n |  | TRUE
72 | bus_LV_1632-69_0_4_node_59 | 0.4 | n |  | TRUE
73 | bus_LV_1632-69_0_4_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_1632-69_0_4_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_1632-69_0_4_node_85 | 0.4 | n |  | TRUE
76 | bus_LV_1632-69_0_4_node_54 | 0.4 | n |  | TRUE
77 | bus_LV_1632-69_0_4_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_1632-69_0_4_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_1632-69_0_4_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_1632-69_0_4_node_66 | 0.4 | n |  | TRUE
81 | bus_LV_1632-69_0_4_node_67 | 0.4 | n |  | TRUE
82 | bus_LV_1632-69_0_4_node_89 | 0.4 | n |  | TRUE
83 | bus_LV_1632-69_0_4_node_87 | 0.4 | n |  | TRUE
84 | bus_LV_1632-69_0_4_node_88 | 0.4 | n |  | TRUE
85 | bus_LV_1632-69_0_4_node_82 | 0.4 | n |  | TRUE
86 | bus_MV_224_0_node_74 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1632-69_0_4_load_0 | 0 | 0.059837 | 0.014996 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1632-69_0_4_load_90 | 5 | 0.0023339 | 0.00058492 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1632-69_0_4_load_38 | 7 | 0.0024236 | 0.00060741 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1632-69_0_4_load_36 | 8 | 0.0059305 | 0.0014863 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1632-69_0_4_load_50 | 10 | 0.0062872 | 0.0015757 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1632-69_0_4_load_34 | 12 | 0.0074251 | 0.0018609 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1632-69_0_4_load_35 | 13 | 0.0020692 | 0.00051859 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1632-69_0_4_load_31 | 14 | 0.0022569 | 0.00056564 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1632-69_0_4_load_63 | 17 | 0.0063774 | 0.0015983 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1632-69_0_4_load_28 | 18 | 0.024248 | 0.006077 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1632-69_0_4_load_12 | 19 | 0.0018184 | 0.00045573 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1632-69_0_4_load_15 | 20 | 0.0044434 | 0.0011136 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1632-69_0_4_load_52 | 24 | 0.0034292 | 0.00085944 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1632-69_0_4_load_45 | 26 | 0.0040753 | 0.0010214 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1632-69_0_4_load_86 | 27 | 0.0073834 | 0.0018505 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1632-69_0_4_load_72 | 29 | 0.0059229 | 0.0014844 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1632-69_0_4_load_37 | 30 | 0.0023887 | 0.00059868 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1632-69_0_4_load_40 | 31 | 0.0026813 | 0.00067201 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1632-69_0_4_load_32 | 32 | 0.003756 | 0.00094135 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1632-69_0_4_load_11 | 33 | 0.020469 | 0.00513 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1632-69_0_4_load_16 | 34 | 0.002454 | 0.00061503 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1632-69_0_4_load_13 | 35 | 0.017772 | 0.0044541 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1632-69_0_4_load_83 | 37 | 0.0071187 | 0.0017841 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1632-69_0_4_load_70 | 40 | 0.015702 | 0.0039354 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1632-69_0_4_load_17 | 41 | 0.0027874 | 0.00069858 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1632-69_0_4_load_39 | 42 | 0.0033194 | 0.00083192 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1632-69_0_4_load_62 | 43 | 0.0050239 | 0.0012591 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1632-69_0_4_load_53 | 44 | 0.0025788 | 0.0006463 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1632-69_0_4_load_43 | 45 | 0.015169 | 0.0038017 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1632-69_0_4_load_30 | 46 | 0.016336 | 0.0040942 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1632-69_0_4_load_21 | 47 | 0.0081349 | 0.0020388 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1632-69_0_4_load_22 | 48 | 0.0038958 | 0.00097638 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1632-69_0_4_load_24 | 50 | 0.0041829 | 0.0010483 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1632-69_0_4_load_25 | 51 | 0.0045727 | 0.001146 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1632-69_0_4_load_26 | 52 | 0.0041703 | 0.0010452 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1632-69_0_4_load_27 | 53 | 0.0045993 | 0.0011527 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1632-69_0_4_load_51 | 54 | 0.0041444 | 0.0010387 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1632-69_0_4_load_60 | 55 | 0.0055065 | 0.0013801 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1632-69_0_4_load_80 | 56 | 0.0064339 | 0.0016125 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1632-69_0_4_load_84 | 57 | 0.00243 | 0.00060903 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1632-69_0_4_load_29 | 58 | 0.030393 | 0.0076171 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1632-69_0_4_load_69 | 60 | 0.0075846 | 0.0019009 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1632-69_0_4_load_68 | 61 | 0.0028949 | 0.00072552 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1632-69_0_4_load_73 | 62 | 0.0024996 | 0.00062647 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1632-69_0_4_load_58 | 63 | 0.0022817 | 0.00057185 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1632-69_0_4_load_41 | 64 | 0.01026 | 0.0025714 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1632-69_0_4_load_42 | 65 | 0.018439 | 0.0046213 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1632-69_0_4_load_44 | 66 | 0.0091891 | 0.002303 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1632-69_0_4_load_74 | 67 | 0.0011416 | 0.00028612 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1632-69_0_4_load_46 | 68 | 0.0039596 | 0.00099237 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1632-69_0_4_load_47 | 69 | 0.0025229 | 0.00063229 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1632-69_0_4_load_48 | 70 | 0.0023425 | 0.00058709 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1632-69_0_4_load_59 | 72 | 0.01062 | 0.0026616 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1632-69_0_4_load_56 | 73 | 0.0052081 | 0.0013053 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1632-69_0_4_load_57 | 74 | 0.0040281 | 0.0010095 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1632-69_0_4_load_85 | 75 | 0.0018376 | 0.00046055 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1632-69_0_4_load_75 | 77 | 0.0040206 | 0.0010077 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1632-69_0_4_load_65 | 78 | 0.003191 | 0.00079973 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1632-69_0_4_load_64 | 79 | 0.0025652 | 0.00064291 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1632-69_0_4_load_66 | 80 | 0.0024549 | 0.00061526 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1632-69_0_4_load_89 | 82 | 0.010786 | 0.0027032 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1632-69_0_4_load_87 | 83 | 0.0037627 | 0.00094303 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1632-69_0_4_load_88 | 84 | 0.0031592 | 0.00079176 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1632-69_0_4_load_82 | 85 | 0.0080616 | 0.0020204 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1632-69_0_4_line_0 |  | 0 | 1 | 0.013592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1632-69_0_4_line_1 |  | 1 | 2 | 0.007958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1632-69_0_4_line_2 |  | 2 | 9 | 0.009715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1632-69_0_4_line_3 |  | 2 | 10 | 0.021566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1632-69_0_4_line_4 |  | 3 | 4 | 0.14982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1632-69_0_4_line_5 |  | 3 | 5 | 0.037962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1632-69_0_4_line_6 |  | 4 | 28 | 0.15016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1632-69_0_4_line_7 |  | 5 | 29 | 0.0020841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1632-69_0_4_line_8 |  | 6 | 7 | 0.0076324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1632-69_0_4_line_9 |  | 6 | 8 | 0.01363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1632-69_0_4_line_10 |  | 7 | 17 | 0.011007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1632-69_0_4_line_11 |  | 8 | 30 | 0.0056104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1632-69_0_4_line_12 |  | 9 | 18 | 0.033511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1632-69_0_4_line_13 |  | 9 | 15 | 0.009153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1632-69_0_4_line_14 |  | 11 | 12 | 0.00997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1632-69_0_4_line_15 |  | 11 | 13 | 0.017043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1632-69_0_4_line_16 |  | 11 | 14 | 0.024883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1632-69_0_4_line_17 |  | 13 | 31 | 0.0050793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_1632-69_0_4_line_18 |  | 14 | 32 | 0.00096845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_1632-69_0_4_line_19 |  | 15 | 16 | 0.005913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1632-69_0_4_line_20 |  | 15 | 17 | 0.0090408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1632-69_0_4_line_21 |  | 16 | 19 | 0.016311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1632-69_0_4_line_22 |  | 16 | 20 | 0.015096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1632-69_0_4_line_23 |  | 19 | 33 | 0.025653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1632-69_0_4_line_24 |  | 20 | 34 | 0.010294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1632-69_0_4_line_25 |  | 21 | 22 | 0.00394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1632-69_0_4_line_26 |  | 21 | 23 | 0.038175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1632-69_0_4_line_27 |  | 21 | 24 | 0.017946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1632-69_0_4_line_28 |  | 22 | 43 | 0.0083104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1632-69_0_4_line_29 |  | 23 | 27 | 0.043135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1632-69_0_4_line_30 |  | 23 | 25 | 0.033964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1632-69_0_4_line_31 |  | 24 | 44 | 0.0058036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1632-69_0_4_line_32 |  | 25 | 26 | 0.046131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1632-69_0_4_line_33 |  | 26 | 45 | 0.024015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1632-69_0_4_line_34 |  | 27 | 46 | 0.029352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1632-69_0_4_line_35 |  | 28 | 82 | 0.038248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1632-69_0_4_line_36 |  | 28 | 83 | 0.02725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1632-69_0_4_line_37 |  | 29 | 38 | 0.028191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1632-69_0_4_line_38 |  | 31 | 42 | 0.013134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1632-69_0_4_line_39 |  | 32 | 59 | 0.016138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1632-69_0_4_line_40 |  | 33 | 35 | 0.023502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1632-69_0_4_line_41 |  | 34 | 41 | 0.0062052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1632-69_0_4_line_42 |  | 35 | 36 | 0.016451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1632-69_0_4_line_43 |  | 36 | 37 | 0.016902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_1632-69_0_4_line_44 |  | 36 | 38 | 0.03048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1632-69_0_4_line_45 |  | 37 | 39 | 0.038546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1632-69_0_4_line_46 |  | 38 | 40 | 0.015571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1632-69_0_4_line_47 |  | 39 | 85 | 0.011419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1632-69_0_4_line_48 |  | 39 | 56 | 0.036493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1632-69_0_4_line_49 |  | 43 | 72 | 0.0012506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1632-69_0_4_line_50 |  | 44 | 76 | 0.01079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1632-69_0_4_line_51 |  | 45 | 64 | 0.020449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1632-69_0_4_line_52 |  | 46 | 58 | 0.0071769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1632-69_0_4_line_53 |  | 47 | 48 | 0.010805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1632-69_0_4_line_54 |  | 47 | 49 | 0.013787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1632-69_0_4_line_55 |  | 48 | 50 | 0.0042758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_1632-69_0_4_line_56 |  | 49 | 51 | 0.013256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1632-69_0_4_line_57 |  | 49 | 52 | 0.010228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1632-69_0_4_line_58 |  | 49 | 53 | 0.0091623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1632-69_0_4_line_59 |  | 50 | 54 | 0.0019483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_1632-69_0_4_line_60 |  | 51 | 55 | 0.02239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1632-69_0_4_line_61 |  | 53 | 56 | 0.024939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1632-69_0_4_line_62 |  | 54 | 57 | 0.011133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1632-69_0_4_line_63 |  | 57 | 75 | 0.00050676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_1632-69_0_4_line_64 |  | 59 | 60 | 0.0014076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_1632-69_0_4_line_65 |  | 59 | 61 | 0.015193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_1632-69_0_4_line_66 |  | 60 | 62 | 0.0096152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1632-69_0_4_line_67 |  | 61 | 63 | 0.0067025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_1632-69_0_4_line_68 |  | 62 | 81 | 0.0076057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1632-69_0_4_line_69 |  | 63 | 74 | 0.013603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_1632-69_0_4_line_70 |  | 64 | 65 | 0.024377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1632-69_0_4_line_71 |  | 65 | 66 | 0.023004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1632-69_0_4_line_72 |  | 66 | 67 | 0.04491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1632-69_0_4_line_73 |  | 68 | 69 | 0.026269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1632-69_0_4_line_74 |  | 68 | 70 | 0.0040668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1632-69_0_4_line_75 |  | 70 | 71 | 0.021754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1632-69_0_4_line_76 |  | 71 | 72 | 0.017733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1632-69_0_4_line_77 |  | 71 | 73 | 0.018032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_1632-69_0_4_line_78 |  | 73 | 74 | 0.0087762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_1632-69_0_4_line_79 |  | 75 | 81 | 0.008441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_1632-69_0_4_line_80 |  | 76 | 77 | 0.0047855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1632-69_0_4_line_81 |  | 78 | 79 | 0.022495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1632-69_0_4_line_82 |  | 79 | 80 | 0.016714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1632-69_0_4_line_83 |  | 80 | 81 | 0.010418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1632-69_0_4_line_84 |  | 83 | 84 | 0.0033049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1632-69_0_4_trafo_39 | 0.63 MVA 20/0.4 kV | 86 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2722640.5757 | 1213411.1065 | 2722652.7934 | 1213417.0624
1 | 2722640.5757 | 1213411.1065 | 2722633.1235 | 1213413.9555
2 | 2722633.1235 | 1213413.9555 | 2722629.3642 | 1213404.9935
3 | 2722633.1235 | 1213413.9555 | 2722641.4388 | 1213433.8538
4 | 2722475.681 | 1213506.6245 | 2722493.1077 | 1213506.8382 | 2722518.1744 | 1213506.8865 | 2722545.3455 | 1213506.589 | 2722577.7238 | 1213510.2461 | 2722601.4962 | 1213511.1577 | 2722605.2964 | 1213511.1136 | 2722607.9899 | 1213510.2016 | 2722611.2772 | 1213507.7562 | 2722616.3163 | 1213501.7886 | 2722620.4696 | 1213498.616
5 | 2722620.4696 | 1213498.616 | 2722591.2974 | 1213474.3237
6 | 2722365.7555 | 1213440.973 | 2722368.3064 | 1213445.8958 | 2722395.3526 | 1213495.7113 | 2722398.0171 | 1213501.0146 | 2722404.622 | 1213505.7426 | 2722415.1507 | 1213505.5141 | 2722446.8262 | 1213497.8919 | 2722453.4541 | 1213497.4277 | 2722457.9222 | 1213498.5314 | 2722472.2545 | 1213505.1196 | 2722475.681 | 1213506.6245
7 | 2722589.6958 | 1213472.9901 | 2722591.2974 | 1213474.3237
8 | 2722631.9228 | 1213434.2686 | 2722628.9243 | 1213427.2499
9 | 2722631.9228 | 1213434.2686 | 2722619.2914 | 1213439.3888
10 | 2722624.6003 | 1213417.1283 | 2722628.9243 | 1213427.2499
11 | 2722614.0919 | 1213441.4964 | 2722619.2914 | 1213439.3888
12 | 2722629.3642 | 1213404.9935 | 2722616.1978 | 1213374.1776
13 | 2722621.0485 | 1213408.8143 | 2722624.6099 | 1213407.0862 | 2722629.3642 | 1213404.9935
14 | 2722574.3528 | 1213296.5903 | 2722571.5997 | 1213287.8381 | 2722571.4005 | 1213287.0685
15 | 2722574.3528 | 1213296.5903 | 2722578.6938 | 1213309.4227 | 2722580.0652 | 1213312.6393
16 | 2722574.3528 | 1213296.5903 | 2722553.8964 | 1213306.2106 | 2722551.7104 | 1213306.8489
17 | 2722580.0652 | 1213312.6393 | 2722582.0574 | 1213317.3116
18 | 2722550.7807 | 1213307.1203 | 2722551.7104 | 1213306.8489
19 | 2722621.0485 | 1213408.8143 | 2722618.7289 | 1213403.3736
20 | 2722621.0485 | 1213408.8143 | 2722624.6003 | 1213417.1283
21 | 2722618.7289 | 1213403.3736 | 2722603.8694 | 1213410.1
22 | 2722618.7289 | 1213403.3736 | 2722612.8128 | 1213389.4855
23 | 2722582.4377 | 1213423.3464 | 2722589.0307 | 1213421.2212 | 2722592.3392 | 1213418.854 | 2722597.5868 | 1213413.8358 | 2722599.4615 | 1213412.0953 | 2722603.8694 | 1213410.1
24 | 2722612.8128 | 1213389.4855 | 2722608.7784 | 1213380.0149
25 | 2722546.5967 | 1213241.4108 | 2722543.2114 | 1213243.4428
26 | 2722546.5967 | 1213241.4108 | 2722548.6126 | 1213238.3499 | 2722557.5416 | 1213241.2912 | 2722563.5047 | 1213242.8705 | 2722566.5541 | 1213243.1334 | 2722568.9655 | 1213242.2712 | 2722570.4718 | 1213241.079 | 2722576.272 | 1213243.5557 | 2722581.0297 | 1213245.366
27 | 2722546.5967 | 1213241.4108 | 2722532.724 | 1213230.0271
28 | 2722543.2114 | 1213243.4428 | 2722536.0809 | 1213247.7111
29 | 2722581.0297 | 1213245.366 | 2722579.0393 | 1213253.0977 | 2722578.0667 | 1213260.4833 | 2722578.0538 | 1213268.8673 | 2722578.9127 | 1213276.6131 | 2722580.6541 | 1213285.7893 | 2722581.3205 | 1213287.8697
30 | 2722610.5948 | 1213248.4316 | 2722603.4717 | 1213245.6164 | 2722595.9991 | 1213243.5389 | 2722592.0971 | 1213242.6136 | 2722587.1704 | 1213241.6338 | 2722582.7369 | 1213240.6863 | 2722581.0297 | 1213245.366
31 | 2722532.724 | 1213230.0271 | 2722528.2375 | 1213226.3456
32 | 2722610.5948 | 1213248.4316 | 2722623.9096 | 1213261.2819 | 2722641.105 | 1213282.9045
33 | 2722641.105 | 1213282.9045 | 2722656.0526 | 1213301.7005
34 | 2722581.3205 | 1213287.8697 | 2722584.01 | 1213296.2663 | 2722591.4188 | 1213315.1109 | 2722591.5289 | 1213315.375
35 | 2722334.6822 | 1213430.7276 | 2722335.1201 | 1213436.7857 | 2722336.0952 | 1213438.8851 | 2722338.5772 | 1213439.392 | 2722355.6024 | 1213439.1855 | 2722362.1111 | 1213439.7195 | 2722365.7555 | 1213440.973
36 | 2722365.7555 | 1213440.973 | 2722363.6525 | 1213434.2247 | 2722360.8282 | 1213425.2265 | 2722354.3378 | 1213416.6562
37 | 2722567.9709 | 1213455.0254 | 2722581.585 | 1213466.2361 | 2722589.6958 | 1213472.9901
38 | 2722582.0574 | 1213317.3116 | 2722587.2088 | 1213329.3934
39 | 2722535.2891 | 1213311.6436 | 2722550.7807 | 1213307.1203
40 | 2722582.4377 | 1213423.3464 | 2722560.0694 | 1213430.5568
41 | 2722606.3466 | 1213374.3061 | 2722608.7784 | 1213380.0149
42 | 2722544.4117 | 1213435.6041 | 2722560.0694 | 1213430.5568
43 | 2722544.4117 | 1213435.6041 | 2722532.6597 | 1213423.4559
44 | 2722567.9709 | 1213455.0254 | 2722544.4117 | 1213435.6041
45 | 2722507.2637 | 1213394.487 | 2722524.1512 | 1213414.6606 | 2722532.6597 | 1213423.4559
46 | 2722567.9709 | 1213455.0254 | 2722572.1635 | 1213451.053 | 2722580.7836 | 1213446.401
47 | 2722507.2637 | 1213394.487 | 2722498.7259 | 1213402.0953
48 | 2722507.2637 | 1213394.487 | 2722492.7992 | 1213375.8311 | 2722489.9456 | 1213371.2245 | 2722486.4681 | 1213364.6161
49 | 2722536.0809 | 1213247.7111 | 2722535.0078 | 1213248.3534
50 | 2722519.8963 | 1213219.5009 | 2722528.2375 | 1213226.3456
51 | 2722670.4494 | 1213315.9853 | 2722660.9577 | 1213308.3689 | 2722656.5975 | 1213302.3858 | 2722656.0526 | 1213301.7005
52 | 2722594.2918 | 1213321.9988 | 2722591.5289 | 1213315.375
53 | 2722492.7436 | 1213325.9091 | 2722482.7351 | 1213329.9804
54 | 2722469.9647 | 1213335.1753 | 2722482.7351 | 1213329.9804
55 | 2722492.7436 | 1213325.9091 | 2722496.7042 | 1213324.2979
56 | 2722469.9647 | 1213335.1753 | 2722463.8554 | 1213323.4111
57 | 2722469.9647 | 1213335.1753 | 2722461.1014 | 1213340.2792
58 | 2722469.9647 | 1213335.1753 | 2722473.0936 | 1213343.7868
59 | 2722496.7042 | 1213324.2979 | 2722498.5089 | 1213323.5638
60 | 2722463.8554 | 1213323.4111 | 2722457.2461 | 1213310.6842 | 2722453.3967 | 1213304.6116 | 2722452.8954 | 1213303.914
61 | 2722486.4681 | 1213364.6161 | 2722483.415 | 1213358.8142 | 2722477.1961 | 1213351.5698 | 2722474.0354 | 1213346.3787 | 2722473.0936 | 1213343.7868
62 | 2722508.9279 | 1213319.6414 | 2722498.5089 | 1213323.5638 | 2722498.5089 | 1213323.5638
63 | 2722509.4021 | 1213319.4628 | 2722508.9279 | 1213319.6414
64 | 2722535.2891 | 1213311.6436 | 2722533.93 | 1213312.0097
65 | 2722535.2891 | 1213311.6436 | 2722530.463 | 1213299.4906 | 2722530.005 | 1213297.4241
66 | 2722533.93 | 1213312.0097 | 2722524.6458 | 1213314.5106
67 | 2722530.005 | 1213297.4241 | 2722528.5549 | 1213290.8804
68 | 2722517.3019 | 1213316.4888 | 2722524.6458 | 1213314.5106
69 | 2722525.1574 | 1213277.7649 | 2722525.1574 | 1213277.7649 | 2722527.511 | 1213284.5185 | 2722528.1335 | 1213288.9791 | 2722528.5549 | 1213290.8804
70 | 2722670.4494 | 1213315.9853 | 2722675.8486 | 1213320.3177 | 2722690.4865 | 1213329.8244
71 | 2722690.4865 | 1213329.8244 | 2722692.293 | 1213330.9976 | 2722710.2402 | 1213341.6091
72 | 2722744.8928 | 1213369.6337 | 2722737.3282 | 1213361.0252 | 2722724.2294 | 1213349.8804 | 2722710.2402 | 1213341.6091
73 | 2722494.7912 | 1213263.7718 | 2722488.8894 | 1213265.8663 | 2722483.3817 | 1213266.1645 | 2722479.8274 | 1213267.9151 | 2722473.694 | 1213276.4735
74 | 2722494.7912 | 1213263.7718 | 2722498.6237 | 1213262.4116
75 | 2722519.7921 | 1213257.4613 | 2722500.647 | 1213261.6935 | 2722498.6237 | 1213262.4116
76 | 2722519.7921 | 1213257.4613 | 2722535.0078 | 1213248.3534
77 | 2722519.7921 | 1213257.4613 | 2722513.8062 | 1213263.2761 | 2722519.3445 | 1213271.2235
78 | 2722519.3445 | 1213271.2235 | 2722520.8109 | 1213273.3278 | 2722525.1574 | 1213277.7649
79 | 2722517.3019 | 1213316.4888 | 2722509.4021 | 1213319.4628
80 | 2722519.8963 | 1213219.5009 | 2722515.7146 | 1213221.8279
81 | 2722493.7043 | 1213303.1501 | 2722488.1286 | 1213300.2882 | 2722473.1116 | 1213294.1391
82 | 2722493.7043 | 1213303.1501 | 2722506.589 | 1213309.7636 | 2722508.4787 | 1213310.9499
83 | 2722517.3019 | 1213316.4888 | 2722508.4787 | 1213310.9499
84 | 2722352.3426 | 1213414.0216 | 2722354.3378 | 1213416.6562

## bus_geodata
| x | y | coords
0 | 2722652.7934 | 1213417.0624
1 | 2722640.5757 | 1213411.1065
2 | 2722633.1235 | 1213413.9555
3 | 2722620.4696 | 1213498.616
4 | 2722475.681 | 1213506.6245
5 | 2722591.2974 | 1213474.3237
6 | 2722631.9228 | 1213434.2686
7 | 2722628.9243 | 1213427.2499
8 | 2722619.2914 | 1213439.3888
9 | 2722629.3642 | 1213404.9935
10 | 2722641.4388 | 1213433.8538
11 | 2722574.3528 | 1213296.5903
12 | 2722571.4005 | 1213287.0685
13 | 2722580.0652 | 1213312.6393
14 | 2722551.7104 | 1213306.8489
15 | 2722621.0485 | 1213408.8143
16 | 2722618.7289 | 1213403.3736
17 | 2722624.6003 | 1213417.1283
18 | 2722616.1978 | 1213374.1776
19 | 2722603.8694 | 1213410.1
20 | 2722612.8128 | 1213389.4855
21 | 2722546.5967 | 1213241.4108
22 | 2722543.2114 | 1213243.4428
23 | 2722581.0297 | 1213245.366
24 | 2722532.724 | 1213230.0271
25 | 2722610.5948 | 1213248.4316
26 | 2722641.105 | 1213282.9045
27 | 2722581.3205 | 1213287.8697
28 | 2722365.7555 | 1213440.973
29 | 2722589.6958 | 1213472.9901
30 | 2722614.0919 | 1213441.4964
31 | 2722582.0574 | 1213317.3116
32 | 2722550.7807 | 1213307.1203
33 | 2722582.4377 | 1213423.3464
34 | 2722608.7784 | 1213380.0149
35 | 2722560.0694 | 1213430.5568
36 | 2722544.4117 | 1213435.6041
37 | 2722532.6597 | 1213423.4559
38 | 2722567.9709 | 1213455.0254
39 | 2722507.2637 | 1213394.487
40 | 2722580.7836 | 1213446.401
41 | 2722606.3466 | 1213374.3061
42 | 2722587.2088 | 1213329.3934
43 | 2722536.0809 | 1213247.7111
44 | 2722528.2375 | 1213226.3456
45 | 2722656.0525 | 1213301.7005
46 | 2722591.5289 | 1213315.375
47 | 2722482.7351 | 1213329.9804
48 | 2722492.7436 | 1213325.9091
49 | 2722469.9647 | 1213335.1753
50 | 2722496.7042 | 1213324.2979
51 | 2722463.8554 | 1213323.4111
52 | 2722461.1014 | 1213340.2792
53 | 2722473.0936 | 1213343.7868
54 | 2722498.5089 | 1213323.5638
55 | 2722452.8954 | 1213303.914
56 | 2722486.4681 | 1213364.6161
57 | 2722508.9279 | 1213319.6414
58 | 2722594.2918 | 1213321.9988
59 | 2722535.2891 | 1213311.6436
60 | 2722533.93 | 1213312.0097
61 | 2722530.005 | 1213297.4241
62 | 2722524.6458 | 1213314.5106
63 | 2722528.5549 | 1213290.8804
64 | 2722670.4494 | 1213315.9853
65 | 2722690.4865 | 1213329.8244
66 | 2722710.2402 | 1213341.6091
67 | 2722744.8928 | 1213369.6337
68 | 2722494.7912 | 1213263.7717
69 | 2722473.694 | 1213276.4735
70 | 2722498.6237 | 1213262.4116
71 | 2722519.7921 | 1213257.4613
72 | 2722535.0078 | 1213248.3534
73 | 2722519.3445 | 1213271.2235
74 | 2722525.1574 | 1213277.7649
75 | 2722509.4021 | 1213319.4628
76 | 2722519.8963 | 1213219.5009
77 | 2722515.7146 | 1213221.8279
78 | 2722473.1116 | 1213294.1391
79 | 2722493.7043 | 1213303.1501
80 | 2722508.4787 | 1213310.9499
81 | 2722517.3019 | 1213316.4888
82 | 2722334.6822 | 1213430.7276
83 | 2722354.3378 | 1213416.6562
84 | 2722352.3426 | 1213414.0216
85 | 2722498.7259 | 1213402.0953
86 | 2722574.3528 | 1213296.5903

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97005 | -0.57808 | 0.059837 | 0.014996
1 | 0.97081 | -0.56302 | 0 | 0
2 | 0.97125 | -0.55422 | 0 | 0
3 | 0.97899 | -0.40251 | 0 | 0
4 | 0.97652 | -0.4509 | 0 | 0
5 | 0.97962 | -0.39028 | 0.0023339 | 0.00058492
6 | 0.97231 | -0.53331 | 0 | 0
7 | 0.97237 | -0.53214 | 0.0024236 | 0.00060741
8 | 0.9722 | -0.5354 | 0.0059305 | 0.0014863
9 | 0.97185 | -0.54236 | 0 | 0
10 | 0.97112 | -0.55673 | 0.0062872 | 0.0015757
11 | 0.99625 | -0.070807 | 0 | 0
12 | 0.99618 | -0.072108 | 0.0074251 | 0.0018609
13 | 0.99805 | -0.036666 | 0.0020692 | 0.00051859
14 | 0.99365 | -0.12006 | 0.0022569 | 0.00056564
15 | 0.97262 | -0.52711 | 0 | 0
16 | 0.97322 | -0.5154 | 0 | 0
17 | 0.97248 | -0.52996 | 0.0063774 | 0.0015983
18 | 0.97109 | -0.55737 | 0.024248 | 0.006077
19 | 0.975 | -0.48029 | 0.0018184 | 0.00045573
20 | 0.97308 | -0.51809 | 0.0044434 | 0.0011136
21 | 0.98523 | -0.2816 | 0 | 0
22 | 0.98568 | -0.27294 | 0 | 0
23 | 0.98125 | -0.35895 | 0 | 0
24 | 0.98507 | -0.28483 | 0.0034292 | 0.00085944
25 | 0.97941 | -0.39485 | 0 | 0
26 | 0.97691 | -0.44383 | 0.0040753 | 0.0010214
27 | 0.97908 | -0.4013 | 0.0073834 | 0.0018505
28 | 0.97405 | -0.49964 | 0 | 0
29 | 0.97966 | -0.38952 | 0.0059229 | 0.0014844
30 | 0.97219 | -0.53565 | 0.0023887 | 0.00059868
31 | 0.99859 | -0.02647 | 0.0026813 | 0.00067201
32 | 0.99355 | -0.12197 | 0.003756 | 0.00094135
33 | 0.97785 | -0.42449 | 0.020469 | 0.00513
34 | 0.97303 | -0.51909 | 0.002454 | 0.00061503
35 | 0.98091 | -0.36493 | 0.017772 | 0.0044541
36 | 0.98152 | -0.35322 | 0 | 0
37 | 0.9823 | -0.33802 | 0.0071187 | 0.0017841
38 | 0.98034 | -0.37623 | 0 | 0
39 | 0.98415 | -0.30222 | 0 | 0
40 | 0.98011 | -0.38067 | 0.015702 | 0.0039354
41 | 0.97301 | -0.51941 | 0.0027874 | 0.00069858
42 | 1 | 0 | -0.47234 | -0.12141
43 | 0.98663 | -0.25471 | 0.0050239 | 0.0012591
44 | 0.98503 | -0.28552 | 0.0025788 | 0.0006463
45 | 0.9757 | -0.46763 | 0.015169 | 0.0038017
46 | 0.97781 | -0.42627 | 0.016336 | 0.0040942
47 | 0.9885 | -0.21856 | 0.0081349 | 0.0020388
48 | 0.98912 | -0.20664 | 0.0038958 | 0.00097638
49 | 0.98773 | -0.23329 | 0 | 0
50 | 0.98937 | -0.20186 | 0.0041829 | 0.0010483
51 | 0.98761 | -0.23568 | 0.0045727 | 0.001146
52 | 0.98769 | -0.23406 | 0.0041703 | 0.0010452
53 | 0.98725 | -0.24251 | 0.0045993 | 0.0011527
54 | 0.98948 | -0.19964 | 0.0041444 | 0.0010387
55 | 0.98749 | -0.23789 | 0.0055065 | 0.0013801
56 | 0.98597 | -0.26714 | 0.0064339 | 0.0016125
57 | 0.99016 | -0.18678 | 0.00243 | 0.00060903
58 | 0.97761 | -0.43025 | 0.030393 | 0.0076171
59 | 0.99189 | -0.15363 | 0 | 0
60 | 0.9918 | -0.15539 | 0.0075846 | 0.0019009
61 | 0.99132 | -0.16449 | 0.0028949 | 0.00072552
62 | 0.99118 | -0.1671 | 0.0024996 | 0.00062647
63 | 0.99108 | -0.1692 | 0.0022817 | 0.00057185
64 | 0.97495 | -0.48225 | 0.01026 | 0.0025714
65 | 0.9743 | -0.49512 | 0.018439 | 0.0046213
66 | 0.97408 | -0.49949 | 0.0091891 | 0.002303
67 | 0.97403 | -0.50043 | 0.0011416 | 0.00028612
68 | 0.98885 | -0.21202 | 0.0039596 | 0.00099237
69 | 0.98879 | -0.2132 | 0.0025229 | 0.00063229
70 | 0.98887 | -0.21155 | 0.0023425 | 0.00058709
71 | 0.98905 | -0.20813 | 0 | 0
72 | 0.98678 | -0.25185 | 0.01062 | 0.0026616
73 | 0.99028 | -0.18456 | 0.0052081 | 0.0013053
74 | 0.99058 | -0.17863 | 0.0040281 | 0.0010095
75 | 0.99019 | -0.18619 | 0.0018376 | 0.00046055
76 | 0.98499 | -0.2863 | 0 | 0
77 | 0.98498 | -0.28664 | 0.0040206 | 0.0010077
78 | 0.99047 | -0.18079 | 0.003191 | 0.00079973
79 | 0.99054 | -0.17952 | 0.0025652 | 0.00064291
80 | 0.99063 | -0.17781 | 0.0024549 | 0.00061526
81 | 0.9907 | -0.17629 | 0 | 0
82 | 0.97366 | -0.50722 | 0.010786 | 0.0027032
83 | 0.97387 | -0.5031 | 0.0037627 | 0.00094303
84 | 0.97386 | -0.5033 | 0.0031592 | 0.00079176
85 | 0.98406 | -0.30388 | 0.0080616 | 0.0020204
86 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.059837 | -0.014996 | 0.05988 | 0.015024 | 4.2942e-05 | 2.7315e-05 | 0.091787 | 0.091787 | 0.091787 | 0.97005 | -0.57808 | 0.97081 | -0.56302 | 25.2163
1 | -0.05988 | -0.015024 | 0.059905 | 0.01504 | 2.5142e-05 | 1.5992e-05 | 0.091787 | 0.091787 | 0.091787 | 0.97081 | -0.56302 | 0.97125 | -0.55422 | 25.2163
2 | -0.066193 | -0.016616 | 0.06623 | 0.01664 | 3.7474e-05 | 2.3863e-05 | 0.10142 | 0.10142 | 0.10142 | 0.97125 | -0.55422 | 0.97185 | -0.54236 | 27.8628
3 | 0.006288 | 0.0015759 | -0.0062872 | -0.0015757 | 7.5055e-07 | 2.1349e-07 | 0.0096336 | 0.0096337 | 0.0096337 | 0.97125 | -0.55422 | 0.97112 | -0.55673 | 2.6466
4 | 0.017795 | 0.0044894 | -0.017754 | -0.0044649 | 4.1136e-05 | 2.4448e-05 | 0.027059 | 0.027059 | 0.027059 | 0.97899 | -0.40251 | 0.97652 | -0.4509 | 7.4339
5 | -0.017795 | -0.0044894 | 0.017806 | 0.0044956 | 1.0423e-05 | 6.1931e-06 | 0.027059 | 0.027058 | 0.027059 | 0.97899 | -0.40251 | 0.97962 | -0.39028 | 7.4337
6 | 0.017754 | 0.0044649 | -0.017713 | -0.0044404 | 4.1232e-05 | 2.4514e-05 | 0.027059 | 0.02706 | 0.02706 | 0.97652 | -0.4509 | 0.97405 | -0.49964 | 7.4341
7 | -0.02014 | -0.0050805 | 0.02014 | 0.0050809 | 7.3196e-07 | 4.4222e-07 | 0.030604 | 0.030604 | 0.030604 | 0.97962 | -0.39028 | 0.97966 | -0.38952 | 8.4076
8 | -0.0083201 | -0.0020853 | 0.0083206 | 0.0020855 | 4.6404e-07 | 2.0232e-07 | 0.012733 | 0.012733 | 0.012733 | 0.97231 | -0.53331 | 0.97237 | -0.53214 | 3.4981
9 | 0.0083201 | 0.0020853 | -0.0083193 | -0.002085 | 8.2868e-07 | 3.6133e-07 | 0.012733 | 0.012733 | 0.012733 | 0.97231 | -0.53331 | 0.9722 | -0.5354 | 3.4981
10 | -0.010744 | -0.0026929 | 0.010745 | 0.0026935 | 1.1158e-06 | 5.7756e-07 | 0.016442 | 0.016442 | 0.016442 | 0.97237 | -0.53214 | 0.97248 | -0.52996 | 4.517
11 | 0.0023888 | 0.00059862 | -0.0023887 | -0.00059868 | 2.8124e-08 | -5.1569e-08 | 0.0036561 | 0.0036562 | 0.0036562 | 0.9722 | -0.5354 | 0.97219 | -0.53565 | 1.0044
12 | 0.024265 | 0.0060877 | -0.024248 | -0.006077 | 1.7348e-05 | 1.0688e-05 | 0.037155 | 0.037155 | 0.037155 | 0.97185 | -0.54236 | 0.97109 | -0.55737 | 10.2074
13 | -0.090495 | -0.022727 | 0.090561 | 0.022769 | 6.5912e-05 | 4.207e-05 | 0.13858 | 0.13858 | 0.13858 | 0.97185 | -0.54236 | 0.97262 | -0.52711 | 38.0701
14 | 0.0074255 | 0.0018611 | -0.0074251 | -0.0018609 | 4.599e-07 | 1.6453e-07 | 0.011091 | 0.011091 | 0.011091 | 0.99625 | -0.070807 | 0.99618 | -0.072108 | 3.047
15 | -0.46433 | -0.11919 | 0.46511 | 0.11968 | 0.00077078 | 0.00049241 | 0.69454 | 0.69454 | 0.69454 | 0.99625 | -0.070807 | 0.99805 | -0.036666 | 47.7022
16 | 0.45691 | 0.11733 | -0.45582 | -0.11663 | 0.0010897 | 0.00069609 | 0.68345 | 0.68345 | 0.68345 | 0.99625 | -0.070807 | 0.99365 | -0.12006 | 46.9405
17 | -0.46717 | -0.1202 | 0.46741 | 0.12035 | 0.00023175 | 0.00014806 | 0.69763 | 0.69763 | 0.69763 | 0.99805 | -0.036666 | 0.99859 | -0.02647 | 47.914
18 | 0.45356 | 0.11607 | -0.45352 | -0.11604 | 4.1992e-05 | 2.6824e-05 | 0.68007 | 0.68007 | 0.68007 | 0.99365 | -0.12006 | 0.99355 | -0.12197 | 46.7084
19 | -0.10769 | -0.027063 | 0.10775 | 0.027101 | 6.0204e-05 | 3.8457e-05 | 0.16478 | 0.16478 | 0.16478 | 0.97262 | -0.52711 | 0.97322 | -0.5154 | 45.2679
20 | 0.017125 | 0.0042932 | -0.017123 | -0.0042918 | 2.3272e-06 | 1.3772e-06 | 0.0262 | 0.0262 | 0.0262 | 0.97262 | -0.52711 | 0.97248 | -0.52996 | 7.1978
21 | -0.11743 | -0.029529 | 0.11763 | 0.029655 | 0.00019727 | 0.00012605 | 0.17959 | 0.17959 | 0.17959 | 0.97322 | -0.5154 | 0.975 | -0.48029 | 49.3366
22 | 0.0096863 | 0.0024278 | -0.009685 | -0.0024272 | 1.2416e-06 | 6.071e-07 | 0.01481 | 0.01481 | 0.01481 | 0.97322 | -0.5154 | 0.97308 | -0.51809 | 4.0687
23 | -0.11945 | -0.030111 | 0.11977 | 0.030315 | 0.00031991 | 0.00020442 | 0.18236 | 0.18236 | 0.18236 | 0.975 | -0.48029 | 0.97785 | -0.42449 | 50.099
24 | 0.0052416 | 0.0013136 | -0.0052414 | -0.0013136 | 2.4801e-07 | 3.0855e-08 | 0.0080154 | 0.0080154 | 0.0080154 | 0.97308 | -0.51809 | 0.97303 | -0.51909 | 2.202
25 | -0.12335 | -0.031277 | 0.12341 | 0.031309 | 5.1354e-05 | 3.2816e-05 | 0.18643 | 0.18643 | 0.18643 | 0.98523 | -0.2816 | 0.98568 | -0.27294 | 51.218
26 | 0.11332 | 0.028762 | -0.1129 | -0.028494 | 0.00041999 | 0.00026831 | 0.17128 | 0.17128 | 0.17128 | 0.98523 | -0.2816 | 0.98125 | -0.35895 | 47.0561
27 | 0.010031 | 0.0025142 | -0.010029 | -0.0025134 | 1.5445e-06 | 7.5998e-07 | 0.015149 | 0.01515 | 0.01515 | 0.98523 | -0.2816 | 0.98507 | -0.28483 | 4.162
28 | -0.12341 | -0.031309 | 0.12351 | 0.031379 | 0.00010832 | 6.9217e-05 | 0.18643 | 0.18643 | 0.18643 | 0.98568 | -0.27294 | 0.98663 | -0.25471 | 51.218
29 | 0.054283 | 0.01367 | -0.054174 | -0.013601 | 0.00010967 | 6.9647e-05 | 0.082341 | 0.082342 | 0.082342 | 0.98125 | -0.35895 | 0.97908 | -0.4013 | 22.6213
30 | 0.058621 | 0.014824 | -0.05852 | -0.01476 | 0.00010076 | 6.4055e-05 | 0.088943 | 0.088943 | 0.088943 | 0.98125 | -0.35895 | 0.97941 | -0.39485 | 24.4349
31 | 0.0065999 | 0.001654 | -0.0065996 | -0.0016539 | 2.1631e-07 | 6.4559e-08 | 0.0099695 | 0.0099695 | 0.0099695 | 0.98507 | -0.28483 | 0.98503 | -0.28552 | 2.7389
32 | 0.05852 | 0.01476 | -0.058383 | -0.014673 | 0.00013685 | 8.7006e-05 | 0.088943 | 0.088943 | 0.088943 | 0.97941 | -0.39485 | 0.97691 | -0.44383 | 24.435
33 | 0.054308 | 0.013651 | -0.054246 | -0.013612 | 6.1645e-05 | 3.9153e-05 | 0.082736 | 0.082736 | 0.082736 | 0.97691 | -0.44383 | 0.9757 | -0.46763 | 22.7296
34 | 0.04679 | 0.01175 | -0.046734 | -0.011715 | 5.5674e-05 | 3.5263e-05 | 0.07112 | 0.07112 | 0.07112 | 0.97908 | -0.4013 | 0.97781 | -0.42627 | 19.5386
35 | 0.01079 | 0.0027053 | -0.010786 | -0.0027032 | 3.8973e-06 | 2.0184e-06 | 0.016484 | 0.016484 | 0.016484 | 0.97405 | -0.49964 | 0.97366 | -0.50722 | 4.5286
36 | 0.0069231 | 0.0017352 | -0.0069219 | -0.0017348 | 1.143e-06 | 3.9242e-07 | 0.010576 | 0.010576 | 0.010576 | 0.97405 | -0.49964 | 0.97387 | -0.5031 | 2.9056
37 | -0.026063 | -0.0065654 | 0.02608 | 0.0065756 | 1.6578e-05 | 1.0254e-05 | 0.0396 | 0.0396 | 0.0396 | 0.97966 | -0.38952 | 0.98034 | -0.37623 | 10.8791
38 | -0.47009 | -0.12102 | 0.47069 | 0.12141 | 0.00060615 | 0.00038725 | 0.70162 | 0.70162 | 0.70162 | 0.99859 | -0.02647 | 1 | 0 | 48.1884
39 | 0.44976 | 0.1151 | -0.44908 | -0.11466 | 0.00068822 | 0.00043963 | 0.67445 | 0.67445 | 0.67445 | 0.99355 | -0.12197 | 0.99189 | -0.15363 | 46.322
40 | -0.14024 | -0.035445 | 0.14064 | 0.035702 | 0.00040175 | 0.00025683 | 0.21351 | 0.21351 | 0.21351 | 0.97785 | -0.42449 | 0.98091 | -0.36493 | 58.6561
41 | 0.0027874 | 0.00069853 | -0.0027874 | -0.00069858 | 4.2281e-08 | -5.0015e-08 | 0.0042626 | 0.0042627 | 0.0042627 | 0.97303 | -0.51909 | 0.97301 | -0.51941 | 1.1711
42 | -0.15841 | -0.040156 | 0.1585 | 0.040212 | 8.9182e-05 | 5.6246e-05 | 0.24047 | 0.24047 | 0.24047 | 0.98091 | -0.36493 | 0.98152 | -0.35322 | 16.5157
43 | -0.20033 | -0.050754 | 0.20048 | 0.050847 | 0.00014635 | 9.281e-05 | 0.30391 | 0.30391 | 0.30391 | 0.98152 | -0.35322 | 0.9823 | -0.33802 | 20.8727
44 | 0.041832 | 0.010542 | -0.041786 | -0.010513 | 4.6001e-05 | 2.9056e-05 | 0.063439 | 0.063439 | 0.063439 | 0.98152 | -0.35322 | 0.98034 | -0.37623 | 17.4284
45 | -0.2076 | -0.052631 | 0.20795 | 0.052858 | 0.00035786 | 0.00022708 | 0.31469 | 0.31469 | 0.31469 | 0.9823 | -0.33802 | 0.98415 | -0.30222 | 21.6133
46 | 0.015706 | 0.0039373 | -0.015702 | -0.0039354 | 3.3185e-06 | 1.9276e-06 | 0.02384 | 0.02384 | 0.02384 | 0.98034 | -0.37623 | 0.98011 | -0.38067 | 6.5494
47 | 0.0080622 | 0.0020207 | -0.0080616 | -0.0020204 | 6.363e-07 | 2.6215e-07 | 0.01219 | 0.01219 | 0.01219 | 0.98415 | -0.30222 | 0.98406 | -0.30388 | 3.3489
48 | -0.21602 | -0.054879 | 0.21638 | 0.055111 | 0.00036555 | 0.0002321 | 0.32688 | 0.32688 | 0.32688 | 0.98415 | -0.30222 | 0.98597 | -0.26714 | 22.4505
49 | -0.12854 | -0.032638 | 0.12856 | 0.032649 | 1.7653e-05 | 1.1282e-05 | 0.19401 | 0.19401 | 0.19401 | 0.98663 | -0.25471 | 0.98678 | -0.25185 | 53.2996
50 | 0.0040209 | 0.0010076 | -0.0040207 | -0.0010077 | 1.4928e-07 | -4.1807e-08 | 0.006074 | 0.006074 | 0.006074 | 0.98503 | -0.28552 | 0.98499 | -0.2863 | 1.6687
51 | 0.039077 | 0.0098106 | -0.03905 | -0.0097934 | 2.724e-05 | 1.7179e-05 | 0.059602 | 0.059602 | 0.059602 | 0.9757 | -0.46763 | 0.97495 | -0.48225 | 16.3742
52 | 0.030398 | 0.0076207 | -0.030393 | -0.0076171 | 5.7595e-06 | 3.5961e-06 | 0.04626 | 0.046261 | 0.046261 | 0.97781 | -0.42627 | 0.97761 | -0.43025 | 12.7089
53 | -0.25034 | -0.063829 | 0.25048 | 0.063921 | 0.00014415 | 9.1701e-05 | 0.37723 | 0.37723 | 0.37723 | 0.9885 | -0.21856 | 0.98912 | -0.20664 | 25.909
54 | 0.24221 | 0.06179 | -0.24203 | -0.061681 | 0.00017218 | 0.00010949 | 0.36499 | 0.36499 | 0.36499 | 0.9885 | -0.21856 | 0.98773 | -0.23329 | 25.068
55 | -0.25438 | -0.064897 | 0.25444 | 0.064935 | 5.883e-05 | 3.7432e-05 | 0.3831 | 0.3831 | 0.3831 | 0.98912 | -0.20664 | 0.98937 | -0.20186 | 26.3115
56 | 0.010081 | 0.0025267 | -0.01008 | -0.0025262 | 1.1465e-06 | 5.6414e-07 | 0.015187 | 0.015187 | 0.015187 | 0.98773 | -0.23329 | 0.98761 | -0.23568 | 4.1723
57 | 0.0041704 | 0.0010451 | -0.0041703 | -0.0010452 | 1.514e-07 | -3.401e-08 | 0.0062827 | 0.0062828 | 0.0062828 | 0.98773 | -0.23329 | 0.98769 | -0.23406 | 1.726
58 | 0.22778 | 0.058109 | -0.22768 | -0.058044 | 0.00010136 | 6.4404e-05 | 0.34352 | 0.34352 | 0.34352 | 0.98773 | -0.23329 | 0.98725 | -0.24251 | 23.5934
59 | -0.25862 | -0.065983 | 0.25865 | 0.066 | 2.7695e-05 | 1.7624e-05 | 0.38939 | 0.38939 | 0.38939 | 0.98937 | -0.20186 | 0.98948 | -0.19964 | 26.7436
60 | 0.0055071 | 0.0013801 | -0.0055065 | -0.0013801 | 5.7806e-07 | 8.349e-08 | 0.0082974 | 0.0082975 | 0.0082975 | 0.98761 | -0.23568 | 0.98749 | -0.23789 | 2.2795
61 | 0.22308 | 0.056892 | -0.22282 | -0.056724 | 0.00026488 | 0.00016825 | 0.33659 | 0.33659 | 0.33659 | 0.98725 | -0.24251 | 0.98597 | -0.26714 | 23.1173
62 | -0.26279 | -0.067039 | 0.26296 | 0.067143 | 0.00016335 | 0.00010397 | 0.39562 | 0.39562 | 0.39562 | 0.98948 | -0.19964 | 0.99016 | -0.18678 | 27.1716
63 | -0.26539 | -0.067752 | 0.2654 | 0.067757 | 7.5736e-06 | 4.8211e-06 | 0.39927 | 0.39927 | 0.39927 | 0.99016 | -0.18678 | 0.99019 | -0.18619 | 27.4224
64 | 0.28596 | 0.073078 | -0.28594 | -0.073063 | 2.4342e-05 | 1.5506e-05 | 0.4295 | 0.4295 | 0.4295 | 0.99189 | -0.15363 | 0.9918 | -0.15539 | 29.4985
65 | 0.16311 | 0.04158 | -0.16303 | -0.041526 | 8.5461e-05 | 5.3911e-05 | 0.24495 | 0.24495 | 0.24495 | 0.99189 | -0.15363 | 0.99132 | -0.16449 | 16.8236
66 | 0.27835 | 0.071162 | -0.2782 | -0.071061 | 0.00015759 | 0.00010036 | 0.41812 | 0.41812 | 0.41812 | 0.9918 | -0.15539 | 0.99118 | -0.1671 | 28.7169
67 | 0.16013 | 0.0408 | -0.1601 | -0.040777 | 3.6376e-05 | 2.2935e-05 | 0.24061 | 0.24061 | 0.24061 | 0.99132 | -0.16449 | 0.99108 | -0.1692 | 16.5252
68 | 0.2757 | 0.070435 | -0.27557 | -0.070357 | 0.00012243 | 7.7962e-05 | 0.41437 | 0.41437 | 0.41437 | 0.99118 | -0.1671 | 0.9907 | -0.17629 | 28.4592
69 | 0.15782 | 0.040206 | -0.15774 | -0.04016 | 7.1742e-05 | 4.5214e-05 | 0.23718 | 0.23718 | 0.23718 | 0.99108 | -0.1692 | 0.99058 | -0.17863 | 16.2899
70 | 0.02879 | 0.007222 | -0.028772 | -0.007211 | 1.7652e-05 | 1.0993e-05 | 0.043943 | 0.043943 | 0.043943 | 0.97495 | -0.48225 | 0.9743 | -0.49512 | 12.0722
71 | 0.010333 | 0.0025897 | -0.010331 | -0.0025886 | 2.1484e-06 | 1.0885e-06 | 0.015781 | 0.015781 | 0.015781 | 0.9743 | -0.49512 | 0.97408 | -0.49949 | 4.3355
72 | 0.0011417 | 0.00028559 | -0.0011416 | -0.00028612 | 5.1221e-08 | -5.2623e-07 | 0.0017439 | 0.0017441 | 0.0017441 | 0.97408 | -0.49949 | 0.97403 | -0.50043 | 0.47914
73 | 0.002523 | 0.00063204 | -0.0025229 | -0.00063229 | 1.4199e-07 | -2.461e-07 | 0.0037965 | 0.0037966 | 0.0037966 | 0.98885 | -0.21202 | 0.98879 | -0.2132 | 1.043
74 | -0.0064826 | -0.0016244 | 0.0064828 | 0.0016245 | 1.4512e-07 | 4.0706e-08 | 0.0097549 | 0.0097549 | 0.0097549 | 0.98885 | -0.21202 | 0.98887 | -0.21155 | 2.6799
75 | -0.0088253 | -0.0022115 | 0.0088267 | 0.0022122 | 1.4387e-06 | 6.4161e-07 | 0.01328 | 0.01328 | 0.01328 | 0.98887 | -0.21155 | 0.98905 | -0.20813 | 3.6483
76 | 0.13947 | 0.035498 | -0.13918 | -0.035311 | 0.00029334 | 0.00018751 | 0.21002 | 0.21002 | 0.21002 | 0.98905 | -0.20813 | 0.98678 | -0.25185 | 57.6992
77 | -0.1483 | -0.03771 | 0.14846 | 0.037818 | 0.00016859 | 0.00010744 | 0.2233 | 0.2233 | 0.2233 | 0.98905 | -0.20813 | 0.99028 | -0.18456 | 30.6737
78 | -0.15367 | -0.039123 | 0.15372 | 0.039151 | 4.3953e-05 | 2.7678e-05 | 0.23113 | 0.23113 | 0.23113 | 0.99028 | -0.18456 | 0.99058 | -0.17863 | 15.8743
79 | -0.26723 | -0.068218 | 0.26736 | 0.068299 | 0.0001279 | 8.1425e-05 | 0.40203 | 0.40203 | 0.40203 | 0.99019 | -0.18619 | 0.9907 | -0.17629 | 27.6121
80 | 0.0040207 | 0.0010077 | -0.0040206 | -0.0010077 | 6.6209e-08 | -1.8538e-08 | 0.006074 | 0.006074 | 0.006074 | 0.98499 | -0.2863 | 0.98498 | -0.28664 | 1.6687
81 | -0.003191 | -0.00079973 | 0.0031912 | 0.00079957 | 1.9385e-07 | -1.6547e-07 | 0.0047939 | 0.0047938 | 0.0047939 | 0.99047 | -0.18079 | 0.99054 | -0.17952 | 1.317
82 | -0.0057564 | -0.0014425 | 0.0057569 | 0.0014426 | 4.6868e-07 | 8.4791e-08 | 0.0086474 | 0.0086473 | 0.0086474 | 0.99054 | -0.17952 | 0.99063 | -0.17781 | 2.3757
83 | -0.0082118 | -0.0020578 | 0.0082124 | 0.0020581 | 5.9438e-07 | 2.4627e-07 | 0.012335 | 0.012335 | 0.012335 | 0.99063 | -0.17781 | 0.9907 | -0.17629 | 3.3887
84 | 0.0031592 | 0.00079174 | -0.0031592 | -0.00079176 | 2.8877e-08 | -2.264e-08 | 0.004827 | 0.0048271 | 0.0048271 | 0.97387 | -0.5031 | 0.97386 | -0.5033 | 1.3261

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.47566 | 0.12224

## res_load
| p_mw | q_mvar
0 | 0.059837 | 0.014996
1 | 0.0023339 | 0.00058492
2 | 0.0024236 | 0.00060741
3 | 0.0059305 | 0.0014863
4 | 0.0062872 | 0.0015757
5 | 0.0074251 | 0.0018609
6 | 0.0020692 | 0.00051859
7 | 0.0022569 | 0.00056564
8 | 0.0063774 | 0.0015983
9 | 0.024248 | 0.006077
10 | 0.0018184 | 0.00045573
11 | 0.0044434 | 0.0011136
12 | 0.0034292 | 0.00085944
13 | 0.0040753 | 0.0010214
14 | 0.0073834 | 0.0018505
15 | 0.0059229 | 0.0014844
16 | 0.0023887 | 0.00059868
17 | 0.0026813 | 0.00067201
18 | 0.003756 | 0.00094135
19 | 0.020469 | 0.00513
20 | 0.002454 | 0.00061503
21 | 0.017772 | 0.0044541
22 | 0.0071187 | 0.0017841
23 | 0.015702 | 0.0039354
24 | 0.0027874 | 0.00069858
25 | 0.0033194 | 0.00083192
26 | 0.0050239 | 0.0012591
27 | 0.0025788 | 0.0006463
28 | 0.015169 | 0.0038017
29 | 0.016336 | 0.0040942
30 | 0.0081349 | 0.0020388
31 | 0.0038958 | 0.00097638
32 | 0.0041829 | 0.0010483
33 | 0.0045727 | 0.001146
34 | 0.0041703 | 0.0010452
35 | 0.0045993 | 0.0011527
36 | 0.0041444 | 0.0010387
37 | 0.0055065 | 0.0013801
38 | 0.0064339 | 0.0016125
39 | 0.00243 | 0.00060903
40 | 0.030393 | 0.0076171
41 | 0.0075846 | 0.0019009
42 | 0.0028949 | 0.00072552
43 | 0.0024996 | 0.00062647
44 | 0.0022817 | 0.00057185
45 | 0.01026 | 0.0025714
46 | 0.018439 | 0.0046213
47 | 0.0091891 | 0.002303
48 | 0.0011416 | 0.00028612
49 | 0.0039596 | 0.00099237
50 | 0.0025229 | 0.00063229
51 | 0.0023425 | 0.00058709
52 | 0.01062 | 0.0026616
53 | 0.0052081 | 0.0013053
54 | 0.0040281 | 0.0010095
55 | 0.0018376 | 0.00046055
56 | 0.0040206 | 0.0010077
57 | 0.003191 | 0.00079973
58 | 0.0025652 | 0.00064291
59 | 0.0024549 | 0.00061526
60 | 0.010786 | 0.0027032
61 | 0.0037627 | 0.00094303
62 | 0.0031592 | 0.00079176
63 | 0.0080616 | 0.0020204

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1