## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1706-6_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1706-6_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1706-6_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1706-6_0_6_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_1706-6_0_6_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1706-6_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1706-6_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1706-6_0_6_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_1706-6_0_6_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1706-6_0_6_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1706-6_0_6_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1706-6_0_6_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1706-6_0_6_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1706-6_0_6_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1706-6_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1706-6_0_6_node_48 | 0.4 | n |  | TRUE
16 | bus_LV_1706-6_0_6_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_1706-6_0_6_node_47 | 0.4 | n |  | TRUE
18 | bus_LV_1706-6_0_6_node_49 | 0.4 | n |  | TRUE
19 | bus_LV_1706-6_0_6_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_1706-6_0_6_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1706-6_0_6_node_71 | 0.4 | n |  | TRUE
22 | bus_LV_1706-6_0_6_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_1706-6_0_6_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1706-6_0_6_node_68 | 0.4 | n |  | TRUE
25 | bus_LV_1706-6_0_6_node_41 | 0.4 | n |  | TRUE
26 | bus_LV_1706-6_0_6_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1706-6_0_6_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_1706-6_0_6_node_45 | 0.4 | n |  | TRUE
29 | bus_LV_1706-6_0_6_node_44 | 0.4 | n |  | TRUE
30 | bus_LV_1706-6_0_6_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1706-6_0_6_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_1706-6_0_6_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1706-6_0_6_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1706-6_0_6_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1706-6_0_6_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_1706-6_0_6_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1706-6_0_6_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_1706-6_0_6_node_60 | 0.4 | n |  | TRUE
39 | bus_LV_1706-6_0_6_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1706-6_0_6_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_1706-6_0_6_node_64 | 0.4 | n |  | TRUE
42 | bus_LV_1706-6_0_6_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_1706-6_0_6_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_1706-6_0_6_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_1706-6_0_6_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_1706-6_0_6_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_1706-6_0_6_node_62 | 0.4 | n |  | TRUE
48 | bus_LV_1706-6_0_6_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_1706-6_0_6_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_1706-6_0_6_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_1706-6_0_6_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_1706-6_0_6_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_1706-6_0_6_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_1706-6_0_6_node_58 | 0.4 | n |  | TRUE
55 | bus_LV_1706-6_0_6_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_1706-6_0_6_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_1706-6_0_6_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_1706-6_0_6_node_81 | 0.4 | n |  | TRUE
59 | bus_LV_1706-6_0_6_node_72 | 0.4 | n |  | TRUE
60 | bus_LV_1706-6_0_6_node_73 | 0.4 | n |  | TRUE
61 | bus_LV_1706-6_0_6_node_74 | 0.4 | n |  | TRUE
62 | bus_LV_1706-6_0_6_node_75 | 0.4 | n |  | TRUE
63 | bus_LV_1706-6_0_6_node_78 | 0.4 | n |  | TRUE
64 | bus_LV_1706-6_0_6_node_76 | 0.4 | n |  | TRUE
65 | bus_LV_1706-6_0_6_node_77 | 0.4 | n |  | TRUE
66 | bus_LV_1706-6_0_6_node_79 | 0.4 | n |  | TRUE
67 | bus_LV_1706-6_0_6_node_80 | 0.4 | n |  | TRUE
68 | bus_LV_1706-6_0_6_node_83 | 0.4 | n |  | TRUE
69 | bus_LV_1706-6_0_6_node_82 | 0.4 | n |  | TRUE
70 | bus_LV_1706-6_0_6_node_84 | 0.4 | n |  | TRUE
71 | bus_LV_1706-6_0_6_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_1706-6_0_6_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_1706-6_0_6_node_54 | 0.4 | n |  | TRUE
74 | bus_LV_1706-6_0_6_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_1706-6_0_6_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_1706-6_0_6_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_1706-6_0_6_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_1706-6_0_6_node_88 | 0.4 | n |  | TRUE
79 | bus_LV_1706-6_0_6_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_1706-6_0_6_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_1706-6_0_6_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_1706-6_0_6_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_1706-6_0_6_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_1706-6_0_6_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_1706-6_0_6_node_89 | 0.4 | n |  | TRUE
86 | bus_LV_1706-6_0_6_node_90 | 0.4 | n |  | TRUE
87 | bus_LV_1706-6_0_6_node_87 | 0.4 | n |  | TRUE
88 | bus_LV_1706-6_0_6_node_91 | 0.4 | n |  | TRUE
89 | bus_LV_1706-6_0_6_node_85 | 0.4 | n |  | TRUE
90 | bus_LV_1706-6_0_6_node_86 | 0.4 | n |  | TRUE
91 | bus_MV_22_0_node_138 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1706-6_0_6_load_0 | 0 | 0.00052199 | 0.00013082 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1706-6_0_6_load_1 | 1 | 0.00028738 | 7.2023e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1706-6_0_6_load_5 | 3 | 0.0014631 | 0.00036668 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1706-6_0_6_load_3 | 4 | 0.00059341 | 0.00014872 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1706-6_0_6_load_4 | 5 | 0.00011311 | 2.8348e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1706-6_0_6_load_10 | 7 | 0.0011661 | 0.00029226 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1706-6_0_6_load_11 | 8 | 0.00081445 | 0.00020412 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1706-6_0_6_load_12 | 9 | 0.0016156 | 0.0004049 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1706-6_0_6_load_13 | 10 | 0.0038168 | 0.00095657 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1706-6_0_6_load_14 | 11 | 0.0038958 | 0.00097637 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1706-6_0_6_load_15 | 12 | 0.0019561 | 0.00049026 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1706-6_0_6_load_7 | 13 | 0.012336 | 0.0030917 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1706-6_0_6_load_8 | 14 | 0.0014176 | 0.00035529 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1706-6_0_6_load_32 | 16 | 0.0082196 | 0.00206 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1706-6_0_6_load_47 | 17 | 0.00066919 | 0.00016771 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1706-6_0_6_load_49 | 18 | 0.0040404 | 0.0010126 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1706-6_0_6_load_30 | 19 | 0.002487 | 0.0006233 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1706-6_0_6_load_16 | 20 | 0.0073952 | 0.0018534 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1706-6_0_6_load_71 | 21 | 0.0022611 | 0.00056669 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1706-6_0_6_load_40 | 22 | 0.015265 | 0.0038257 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1706-6_0_6_load_17 | 23 | 0.0047108 | 0.0011806 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1706-6_0_6_load_68 | 24 | 0.0050174 | 0.0012575 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1706-6_0_6_load_41 | 25 | 0.0081347 | 0.0020387 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1706-6_0_6_load_19 | 27 | 0.0059853 | 0.0015001 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1706-6_0_6_load_45 | 28 | 0.00976 | 0.0024461 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1706-6_0_6_load_44 | 29 | 0.0048815 | 0.0012234 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1706-6_0_6_load_20 | 30 | 0.0012703 | 0.00031836 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1706-6_0_6_load_21 | 31 | 0.0033743 | 0.00084568 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1706-6_0_6_load_22 | 32 | 0.0036832 | 0.0009231 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1706-6_0_6_load_27 | 37 | 0.012613 | 0.003161 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1706-6_0_6_load_60 | 38 | 0.0051361 | 0.0012872 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1706-6_0_6_load_37 | 39 | 0.0015173 | 0.00038026 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1706-6_0_6_load_34 | 40 | 0.0059843 | 0.0014998 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1706-6_0_6_load_43 | 43 | 0.0061219 | 0.0015343 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1706-6_0_6_load_39 | 44 | 0.007826 | 0.0019614 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1706-6_0_6_load_35 | 45 | 0.002841 | 0.00071203 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1706-6_0_6_load_33 | 46 | 0.0022754 | 0.00057027 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1706-6_0_6_load_62 | 47 | 0.0028576 | 0.00071618 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1706-6_0_6_load_28 | 48 | 0.01462 | 0.0036641 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1706-6_0_6_load_29 | 49 | 0.0025469 | 0.0006383 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1706-6_0_6_load_31 | 50 | 0.0082444 | 0.0020663 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1706-6_0_6_load_36 | 51 | 0.0019795 | 0.00049612 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1706-6_0_6_load_38 | 52 | 0.0019771 | 0.00049551 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1706-6_0_6_load_50 | 53 | 0.0031219 | 0.00078241 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1706-6_0_6_load_58 | 54 | 0.010504 | 0.0026325 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1706-6_0_6_load_56 | 56 | 0.0062461 | 0.0015654 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1706-6_0_6_load_46 | 57 | 0.10298 | 0.025809 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1706-6_0_6_load_81 | 58 | 0.0018051 | 0.00045241 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1706-6_0_6_load_72 | 59 | 0.0050866 | 0.0012748 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1706-6_0_6_load_73 | 60 | 0.0077918 | 0.0019528 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1706-6_0_6_load_74 | 61 | 0.060107 | 0.015064 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1706-6_0_6_load_75 | 62 | 0.056112 | 0.014063 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1706-6_0_6_load_78 | 63 | 0.018387 | 0.0046081 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1706-6_0_6_load_76 | 64 | 0.0039132 | 0.00098075 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1706-6_0_6_load_77 | 65 | 0.0067647 | 0.0016954 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1706-6_0_6_load_79 | 66 | 0.0046669 | 0.0011696 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1706-6_0_6_load_80 | 67 | 0.00090366 | 0.00022648 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1706-6_0_6_load_82 | 69 | 0.0025147 | 0.00063025 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1706-6_0_6_load_84 | 70 | 0.00069808 | 0.00017495 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1706-6_0_6_load_52 | 71 | 0.021318 | 0.0053427 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1706-6_0_6_load_53 | 72 | 0.0044554 | 0.0011166 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1706-6_0_6_load_54 | 73 | 0.0078314 | 0.0019627 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1706-6_0_6_load_55 | 74 | 0.0037024 | 0.00092792 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1706-6_0_6_load_57 | 75 | 0.004412 | 0.0011057 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1706-6_0_6_load_69 | 77 | 0.006213 | 0.0015571 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1706-6_0_6_load_88 | 78 | 0.011025 | 0.0027631 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1706-6_0_6_load_61 | 79 | 0.0020433 | 0.0005121 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1706-6_0_6_load_63 | 80 | 0.003058 | 0.00076642 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1706-6_0_6_load_70 | 81 | 0.0038954 | 0.00097628 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1706-6_0_6_load_65 | 82 | 0.0035058 | 0.00087865 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1706-6_0_6_load_66 | 83 | 0.0035045 | 0.00087832 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1706-6_0_6_load_67 | 84 | 0.0069806 | 0.0017495 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1706-6_0_6_load_89 | 85 | 0.0039472 | 0.00098926 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1706-6_0_6_load_90 | 86 | 0.0011926 | 0.0002989 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1706-6_0_6_load_87 | 87 | 0.0014809 | 0.00037116 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1706-6_0_6_load_91 | 88 | 0.001718 | 0.00043058 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1706-6_0_6_load_85 | 89 | 0.0031854 | 0.00079832 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1706-6_0_6_load_86 | 90 | 0.0039998 | 0.0010024 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1706-6_0_6_line_0 |  | 0 | 1 | 0.056551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1706-6_0_6_line_1 |  | 0 | 2 | 0.0043803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1706-6_0_6_line_2 |  | 1 | 3 | 0.10364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1706-6_0_6_line_3 |  | 2 | 4 | 0.016022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1706-6_0_6_line_4 |  | 2 | 5 | 0.025705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1706-6_0_6_line_5 |  | 3 | 6 | 0.090581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1706-6_0_6_line_6 |  | 6 | 7 | 0.042899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1706-6_0_6_line_7 |  | 6 | 8 | 0.024778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_1706-6_0_6_line_8 |  | 6 | 9 | 0.019665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1706-6_0_6_line_9 |  | 7 | 10 | 0.019339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_1706-6_0_6_line_10 |  | 8 | 11 | 0.0016587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_1706-6_0_6_line_11 |  | 9 | 12 | 0.021806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1706-6_0_6_line_12 |  | 10 | 20 | 0.010753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_1706-6_0_6_line_13 |  | 11 | 21 | 0.015114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_1706-6_0_6_line_14 |  | 12 | 22 | 0.04331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_1706-6_0_6_line_15 |  | 13 | 14 | 0.014402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1706-6_0_6_line_16 |  | 13 | 15 | 0.16523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1706-6_0_6_line_17 |  | 14 | 16 | 0.052721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1706-6_0_6_line_18 |  | 15 | 17 | 0.039888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1706-6_0_6_line_19 |  | 16 | 19 | 0.01273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1706-6_0_6_line_20 |  | 17 | 18 | 0.049615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1706-6_0_6_line_21 |  | 19 | 48 | 0.027782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1706-6_0_6_line_22 |  | 20 | 23 | 0.014731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_1706-6_0_6_line_23 |  | 21 | 24 | 0.071336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1706-6_0_6_line_24 |  | 22 | 25 | 0.0063696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_1706-6_0_6_line_25 |  | 23 | 26 | 0.024618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_1706-6_0_6_line_26 |  | 24 | 84 | 0.002736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1706-6_0_6_line_27 |  | 25 | 42 | 0.015215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_1706-6_0_6_line_28 |  | 26 | 27 | 0.022429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_1706-6_0_6_line_29 |  | 27 | 28 | 0.016838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1706-6_0_6_line_30 |  | 28 | 29 | 0.011763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_1706-6_0_6_line_31 |  | 29 | 57 | 0.023397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_1706-6_0_6_line_32 |  | 30 | 31 | 0.0010996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1706-6_0_6_line_33 |  | 30 | 32 | 0.044589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1706-6_0_6_line_34 |  | 31 | 33 | 0.04393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1706-6_0_6_line_35 |  | 32 | 34 | 0.0044833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1706-6_0_6_line_36 |  | 33 | 35 | 0.038496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_1706-6_0_6_line_37 |  | 33 | 36 | 0.020574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_1706-6_0_6_line_38 |  | 34 | 37 | 0.020281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1706-6_0_6_line_39 |  | 35 | 38 | 0.036474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_1706-6_0_6_line_40 |  | 36 | 39 | 0.0079823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_1706-6_0_6_line_41 |  | 36 | 40 | 0.013286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1706-6_0_6_line_42 |  | 37 | 41 | 0.018967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1706-6_0_6_line_43 |  | 38 | 43 | 0.0068992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_1706-6_0_6_line_44 |  | 39 | 44 | 0.028847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_1706-6_0_6_line_45 |  | 40 | 45 | 0.0064391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1706-6_0_6_line_46 |  | 41 | 46 | 0.02736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1706-6_0_6_line_47 |  | 41 | 47 | 0.0099227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1706-6_0_6_line_48 |  | 42 | 43 | 0.010973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_1706-6_0_6_line_49 |  | 44 | 54 | 0.017032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1706-6_0_6_line_50 |  | 45 | 51 | 0.029247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1706-6_0_6_line_51 |  | 46 | 50 | 0.0025279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1706-6_0_6_line_52 |  | 47 | 79 | 0.0018138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1706-6_0_6_line_53 |  | 48 | 49 | 0.0082113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1706-6_0_6_line_54 |  | 49 | 50 | 0.020029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1706-6_0_6_line_55 |  | 51 | 52 | 0.005432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1706-6_0_6_line_56 |  | 52 | 53 | 0.00073855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1706-6_0_6_line_57 |  | 53 | 55 | 0.014816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1706-6_0_6_line_58 |  | 54 | 56 | 0.011752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1706-6_0_6_line_59 |  | 55 | 71 | 0.049537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1706-6_0_6_line_60 |  | 56 | 73 | 0.0023092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1706-6_0_6_line_61 |  | 57 | 58 | 0.089719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_1706-6_0_6_line_62 |  | 58 | 69 | 0.027353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_1706-6_0_6_line_63 |  | 59 | 60 | 0.0088325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1706-6_0_6_line_64 |  | 59 | 61 | 0.023855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1706-6_0_6_line_65 |  | 61 | 62 | 0.0023666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1706-6_0_6_line_66 |  | 62 | 63 | 0.015866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1706-6_0_6_line_67 |  | 63 | 64 | 0.018527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_1706-6_0_6_line_68 |  | 64 | 65 | 0.014743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_1706-6_0_6_line_69 |  | 65 | 66 | 0.019341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_1706-6_0_6_line_70 |  | 66 | 67 | 0.033397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_1706-6_0_6_line_71 |  | 67 | 68 | 0.022337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_1706-6_0_6_line_72 |  | 68 | 70 | 0.079584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1706-6_0_6_line_73 |  | 68 | 69 | 0.04614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_1706-6_0_6_line_74 |  | 72 | 73 | 0.021662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1706-6_0_6_line_75 |  | 72 | 74 | 0.003266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1706-6_0_6_line_76 |  | 74 | 75 | 0.013768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1706-6_0_6_line_77 |  | 75 | 76 | 0.033758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1706-6_0_6_line_78 |  | 76 | 77 | 0.028948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1706-6_0_6_line_79 |  | 77 | 78 | 0.096916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1706-6_0_6_line_80 |  | 78 | 87 | 0.056095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1706-6_0_6_line_81 |  | 79 | 80 | 0.062753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1706-6_0_6_line_82 |  | 80 | 81 | 0.1545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1706-6_0_6_line_83 |  | 82 | 83 | 0.011637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1706-6_0_6_line_84 |  | 83 | 84 | 0.023686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1706-6_0_6_line_85 |  | 85 | 86 | 0.0060722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1706-6_0_6_line_86 |  | 85 | 87 | 0.12839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1706-6_0_6_line_87 |  | 86 | 88 | 0.049055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1706-6_0_6_line_88 |  | 87 | 90 | 0.0079398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1706-6_0_6_line_89 |  | 89 | 90 | 0.020898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1706-6_0_6_trafo_71 | 0.63 MVA 20/0.4 kV | 91 | 21 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2690911.4817 | 1217490.9059 | 2690936.983 | 1217507.1446 | 2690960.446 | 1217519.0666
1 | 2690907.7869 | 1217488.5532 | 2690911.4817 | 1217490.9059
2 | 2691056.3863 | 1217558.2626 | 2690960.446 | 1217519.0666
3 | 2690907.7869 | 1217488.5532 | 2690903.1117 | 1217498.3997 | 2690904.0252 | 1217503.4395
4 | 2690907.7869 | 1217488.5532 | 2690886.1035 | 1217474.7491
5 | 2691145.7106 | 1217553.8093 | 2691136.475 | 1217556.0363 | 2691104.594 | 1217560.652 | 2691082.1724 | 1217562.7997 | 2691065.2813 | 1217561.2405 | 2691056.3863 | 1217558.2626
6 | 2691145.7106 | 1217553.8093 | 2691126.1924 | 1217515.6082
7 | 2691145.7106 | 1217553.8093 | 2691167.1358 | 1217541.3622
8 | 2691145.7106 | 1217553.8093 | 2691154.7134 | 1217571.2923
9 | 2691117.3936 | 1217498.3869 | 2691126.1924 | 1217515.6082
10 | 2691167.1358 | 1217541.3622 | 2691168.57 | 1217540.5289
11 | 2691154.7134 | 1217571.2923 | 2691164.1721 | 1217589.6607 | 2691164.6892 | 1217590.6822
12 | 2691117.3936 | 1217498.3869 | 2691112.5012 | 1217488.8114
13 | 2691168.57 | 1217540.5289 | 2691181.639 | 1217532.9364
14 | 2691164.6892 | 1217590.6822 | 2691180.443 | 1217621.8093 | 2691184.3201 | 1217629.2877
15 | 2691332.3253 | 1217963.0509 | 2691321.1862 | 1217959.173 | 2691318.8637 | 1217957.9872
16 | 2691332.3253 | 1217963.0509 | 2691317.2751 | 1218127.5951
17 | 2691315.8244 | 1217905.3539 | 2691318.8637 | 1217957.9872
18 | 2691317.2751 | 1218127.5951 | 2691354.1957 | 1218142.6918
19 | 2691315.8244 | 1217905.3539 | 2691309.3348 | 1217894.4028
20 | 2691402.497 | 1218147.2261 | 2691380.0875 | 1218149.2172 | 2691368.5943 | 1218148.7295 | 2691354.9345 | 1218142.9939 | 2691354.1957 | 1218142.6918
21 | 2691309.3348 | 1217894.4028 | 2691295.1713 | 1217870.5019
22 | 2691105.7987 | 1217475.6932 | 2691112.5012 | 1217488.8114
23 | 2691181.639 | 1217532.9364 | 2691231.4238 | 1217481.8455
24 | 2691187.2518 | 1217634.9425 | 2691184.3201 | 1217629.2877
25 | 2691094.5978 | 1217453.7706 | 2691105.7987 | 1217475.6932
26 | 2691231.4238 | 1217481.8455 | 2691232.349 | 1217479.2707
27 | 2691194.2547 | 1217648.45 | 2691187.2518 | 1217634.9425
28 | 2691094.5978 | 1217453.7706 | 2691114.3095 | 1217443.0702
29 | 2691114.3095 | 1217443.0702 | 2691125.0368 | 1217437.2469 | 2691125.631 | 1217432.6528
30 | 2691125.631 | 1217432.6528 | 2691125.631 | 1217432.6528 | 2691120.0923 | 1217422.2749
31 | 2691109.0763 | 1217401.6341 | 2691120.0923 | 1217422.2749
32 | 2691230.2627 | 1217769.6782 | 2691230.1217 | 1217768.5877
33 | 2691238.1455 | 1217813.5087 | 2691233.157 | 1217792.0659 | 2691230.2627 | 1217769.6782
34 | 2691224.4894 | 1217725.0206 | 2691230.1217 | 1217768.5877
35 | 2691239.1614 | 1217817.8754 | 2691238.1455 | 1217813.5087
36 | 2691224.4894 | 1217725.0206 | 2691221.0402 | 1217710.3133 | 2691218.7783 | 1217701.8618 | 2691215.4339 | 1217692.7044 | 2691213.5825 | 1217688.1729
37 | 2691224.4894 | 1217725.0206 | 2691233.2255 | 1217723.6645 | 2691242.8348 | 1217716.8514
38 | 2691239.1614 | 1217817.8754 | 2691258.9658 | 1217813.5025
39 | 2691213.5825 | 1217688.1729 | 2691219.2098 | 1217679.1418 | 2691208.129 | 1217655.8056
40 | 2691242.8348 | 1217716.8514 | 2691244.9873 | 1217709.1648
41 | 2691242.8348 | 1217716.8514 | 2691253.7654 | 1217723.8903 | 2691254.05 | 1217723.9093
42 | 2691276.3625 | 1217815.7659 | 2691269.2503 | 1217811.2316 | 2691258.9658 | 1217813.5025
43 | 2691205.1698 | 1217649.5733 | 2691208.129 | 1217655.8056
44 | 2691252.7661 | 1217681.3861 | 2691244.9873 | 1217709.1648
45 | 2691260.4747 | 1217724.3389 | 2691254.05 | 1217723.9093
46 | 2691276.3625 | 1217815.7659 | 2691286.1025 | 1217841.3337
47 | 2691276.3625 | 1217815.7659 | 2691281.6614 | 1217812.3002 | 2691285.2495 | 1217812.1543
48 | 2691194.2547 | 1217648.45 | 2691205.1698 | 1217649.5733 | 2691205.1698 | 1217649.5733
49 | 2691257.3588 | 1217664.9855 | 2691252.7661 | 1217681.3861
50 | 2691289.6568 | 1217726.2902 | 2691260.4747 | 1217724.3389
51 | 2691287.0025 | 1217843.696 | 2691286.1025 | 1217841.3337
52 | 2691287.0619 | 1217812.0806 | 2691285.2495 | 1217812.1543
53 | 2691292.2936 | 1217862.9392 | 2691293.0838 | 1217866.9793 | 2691295.1713 | 1217870.5019
54 | 2691287.0025 | 1217843.696 | 2691290.1411 | 1217851.935 | 2691292.2936 | 1217862.9392
55 | 2691295.0449 | 1217726.9166 | 2691292.5955 | 1217726.4867 | 2691289.6568 | 1217726.2902
56 | 2691295.7723 | 1217727.0443 | 2691295.0449 | 1217726.9166
57 | 2691310.3656 | 1217729.6055 | 2691295.7723 | 1217727.0443
58 | 2691257.3588 | 1217664.9855 | 2691260.5279 | 1217653.6685
59 | 2691310.3656 | 1217729.6055 | 2691314.1196 | 1217726.3942 | 2691316.0884 | 1217710.8804 | 2691310.1306 | 1217682.5364
60 | 2691261.3454 | 1217651.5098 | 2691260.5838 | 1217653.4687 | 2691260.5279 | 1217653.6685
61 | 2691109.0763 | 1217401.6341 | 2691039.0906 | 1217345.4961
62 | 2691039.0906 | 1217345.4961 | 2691034.4987 | 1217336.539 | 2691026.3884 | 1217321.2715
63 | 2691100.7606 | 1217206.2068 | 2691108.9357 | 1217202.8628
64 | 2691108.9357 | 1217202.8628 | 2691115.462 | 1217212.5025 | 2691118.1877 | 1217224.4079 | 2691118.1877 | 1217224.4079
65 | 2691116.0861 | 1217225.4959 | 2691118.1877 | 1217224.4079
66 | 2691101.9962 | 1217232.7902 | 2691116.0861 | 1217225.4959
67 | 2691085.5433 | 1217241.3078 | 2691101.9962 | 1217232.7902
68 | 2691085.5433 | 1217241.3078 | 2691076.9458 | 1217245.7588 | 2691072.3851 | 1217247.9547
69 | 2691054.959 | 1217256.3452 | 2691072.3851 | 1217247.9547
70 | 2691054.959 | 1217256.3452 | 2691024.8681 | 1217270.8338
71 | 2691004.7426 | 1217280.5241 | 2691024.8681 | 1217270.8338
72 | 2691004.7426 | 1217280.5241 | 2690978.1888 | 1217230.5401 | 2690967.5091 | 1217210.1878
73 | 2691004.7426 | 1217280.5241 | 2691026.3884 | 1217321.2715
74 | 2691269.1944 | 1217631.3194 | 2691261.3454 | 1217651.5098
75 | 2691269.1944 | 1217631.3194 | 2691270.3778 | 1217628.2753
76 | 2691270.3778 | 1217628.2753 | 2691275.3663 | 1217615.4431
77 | 2691287.5979 | 1217583.9793 | 2691275.3663 | 1217615.4431
78 | 2691287.5979 | 1217583.9793 | 2691315.5596 | 1217591.4709
79 | 2691315.5596 | 1217591.4709 | 2691400.6005 | 1217544.9875
80 | 2691429.4542 | 1217496.8827 | 2691400.6005 | 1217544.9875
81 | 2691287.0619 | 1217812.0806 | 2691291.7874 | 1217811.8884 | 2691303.4854 | 1217813.4242 | 2691316.5844 | 1217819.6402 | 2691325.2814 | 1217831.2259 | 2691331.1443 | 1217841.9786 | 2691334.9745 | 1217845.1803
82 | 2691334.9745 | 1217845.1803 | 2691489.2883 | 1217837.5907
83 | 2691244.2929 | 1217446.0282 | 2691240.358 | 1217456.9798
84 | 2691232.349 | 1217479.2707 | 2691240.358 | 1217456.9798
85 | 2691375.5555 | 1217380.3589 | 2691377.5685 | 1217374.6301
86 | 2691429.4542 | 1217496.8827 | 2691375.5555 | 1217380.3589
87 | 2691377.5685 | 1217374.6301 | 2691380.8654 | 1217365.2479 | 2691382.5726 | 1217352.9434 | 2691381.2735 | 1217338.6471 | 2691376.4713 | 1217327.2876
88 | 2691429.4542 | 1217496.8827 | 2691437.3677 | 1217496.2374 | 2691437.3677 | 1217496.2374
89 | 2691457.8308 | 1217499.5734 | 2691451.3668 | 1217499.7435 | 2691437.3677 | 1217496.2374

## bus_geodata
| x | y | coords
0 | 2690911.4817 | 1217490.9059
1 | 2690960.446 | 1217519.0666
2 | 2690907.7869 | 1217488.5532
3 | 2691056.3863 | 1217558.2626
4 | 2690904.0252 | 1217503.4395
5 | 2690886.1035 | 1217474.7491
6 | 2691145.7106 | 1217553.8093
7 | 2691126.1924 | 1217515.6082
8 | 2691167.1358 | 1217541.3622
9 | 2691154.7134 | 1217571.2923
10 | 2691117.3936 | 1217498.3869
11 | 2691168.57 | 1217540.5289
12 | 2691164.6892 | 1217590.6822
13 | 2691332.3253 | 1217963.0509
14 | 2691318.8637 | 1217957.9872
15 | 2691317.2751 | 1218127.5951
16 | 2691315.8244 | 1217905.3539
17 | 2691354.1957 | 1218142.6918
18 | 2691402.497 | 1218147.2261
19 | 2691309.3348 | 1217894.4028
20 | 2691112.5012 | 1217488.8114
21 | 2691181.639 | 1217532.9364
22 | 2691184.3201 | 1217629.2877
23 | 2691105.7987 | 1217475.6932
24 | 2691231.4238 | 1217481.8455
25 | 2691187.2518 | 1217634.9425
26 | 2691094.5978 | 1217453.7706
27 | 2691114.3095 | 1217443.0702
28 | 2691125.631 | 1217432.6528
29 | 2691120.0923 | 1217422.2749
30 | 2691230.2627 | 1217769.6782
31 | 2691230.1217 | 1217768.5877
32 | 2691238.1455 | 1217813.5087
33 | 2691224.4894 | 1217725.0206
34 | 2691239.1614 | 1217817.8754
35 | 2691213.5825 | 1217688.1729
36 | 2691242.8348 | 1217716.8514
37 | 2691258.9658 | 1217813.5025
38 | 2691208.129 | 1217655.8056
39 | 2691244.9873 | 1217709.1648
40 | 2691254.05 | 1217723.9093
41 | 2691276.3625 | 1217815.7659
42 | 2691194.2547 | 1217648.45
43 | 2691205.1698 | 1217649.5733
44 | 2691252.7661 | 1217681.3861
45 | 2691260.4747 | 1217724.3389
46 | 2691286.1025 | 1217841.3337
47 | 2691285.2495 | 1217812.1543
48 | 2691295.1713 | 1217870.5019
49 | 2691292.2936 | 1217862.9392
50 | 2691287.0025 | 1217843.696
51 | 2691289.6568 | 1217726.2902
52 | 2691295.0449 | 1217726.9166
53 | 2691295.7723 | 1217727.0443
54 | 2691257.3588 | 1217664.9855
55 | 2691310.3656 | 1217729.6055
56 | 2691260.5279 | 1217653.6685
57 | 2691109.0763 | 1217401.6341
58 | 2691039.0906 | 1217345.4961
59 | 2691108.9357 | 1217202.8628
60 | 2691100.7606 | 1217206.2068
61 | 2691118.1877 | 1217224.4079
62 | 2691116.0861 | 1217225.4959
63 | 2691101.9962 | 1217232.7902
64 | 2691085.5433 | 1217241.3078
65 | 2691072.3851 | 1217247.9547
66 | 2691054.959 | 1217256.3452
67 | 2691024.8681 | 1217270.8338
68 | 2691004.7426 | 1217280.5241
69 | 2691026.3884 | 1217321.2715
70 | 2690967.5091 | 1217210.1878
71 | 2691310.1306 | 1217682.5364
72 | 2691269.1944 | 1217631.3194
73 | 2691261.3454 | 1217651.5098
74 | 2691270.3778 | 1217628.2753
75 | 2691275.3663 | 1217615.4431
76 | 2691287.5979 | 1217583.9793
77 | 2691315.5596 | 1217591.4709
78 | 2691400.6005 | 1217544.9875
79 | 2691287.0618 | 1217812.0806
80 | 2691334.9745 | 1217845.1803
81 | 2691489.2883 | 1217837.5907
82 | 2691244.2929 | 1217446.0282
83 | 2691240.358 | 1217456.9798
84 | 2691232.349 | 1217479.2707
85 | 2691375.5555 | 1217380.3589
86 | 2691377.5685 | 1217374.6301
87 | 2691429.4542 | 1217496.8827
88 | 2691376.4713 | 1217327.2876
89 | 2691457.8308 | 1217499.5734
90 | 2691437.3677 | 1217496.2374
91 | 2691188.3008 | 1217529.0661

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99525 | -0.09003 | 0.00052199 | 0.00013082
1 | 0.99531 | -0.088805 | 0.00028738 | 7.2023e-05
2 | 0.99525 | -0.090085 | 0 | 0
3 | 0.99546 | -0.086032 | 0.0014631 | 0.00036668
4 | 0.99524 | -0.090252 | 0.00059341 | 0.00014872
5 | 0.99525 | -0.090136 | 0.00011311 | 2.8348e-05
6 | 0.9957 | -0.081274 | 0 | 0
7 | 0.99324 | -0.12807 | 0.0011661 | 0.00029226
8 | 0.99826 | -0.032875 | 0.00081445 | 0.00020412
9 | 0.99481 | -0.09819 | 0.0016156 | 0.0004049
10 | 0.99214 | -0.14917 | 0.0038168 | 0.00095657
11 | 0.99843 | -0.029639 | 0.0038958 | 0.00097637
12 | 0.99383 | -0.11686 | 0.0019561 | 0.00049026
13 | 0.9721 | -0.53885 | 0.012336 | 0.0030917
14 | 0.97233 | -0.53432 | 0.0014176 | 0.00035529
15 | 0.97137 | -0.55323 | 0 | 0
16 | 0.97323 | -0.51639 | 0.0082196 | 0.00206
17 | 0.9712 | -0.55671 | 0.00066919 | 0.00016771
18 | 0.97101 | -0.56041 | 0.0040404 | 0.0010126
19 | 0.97355 | -0.51014 | 0.002487 | 0.0006233
20 | 0.99153 | -0.16077 | 0.0073952 | 0.0018534
21 | 1 | 0 | -0.5921 | -0.15179
22 | 0.9919 | -0.15375 | 0.015265 | 0.0038257
23 | 0.99072 | -0.1763 | 0.0047108 | 0.0011806
24 | 0.99877 | -0.023666 | 0.0050174 | 0.0012575
25 | 0.99164 | -0.15884 | 0.0081347 | 0.0020387
26 | 0.98939 | -0.20191 | 0 | 0
27 | 0.98817 | -0.22529 | 0.0059853 | 0.0015001
28 | 0.98728 | -0.24252 | 0.00976 | 0.0024461
29 | 0.98668 | -0.25417 | 0.0048815 | 0.0012234
30 | 0.9837 | -0.31172 | 0.0012703 | 0.00031836
31 | 0.98379 | -0.31001 | 0.0033743 | 0.00084568
32 | 0.98017 | -0.38026 | 0.0036832 | 0.0009231
33 | 0.98745 | -0.23933 | 0 | 0
34 | 0.97983 | -0.38687 | 0 | 0
35 | 0.98892 | -0.211 | 0 | 0
36 | 0.98701 | -0.2479 | 0 | 0
37 | 0.9783 | -0.41687 | 0.012613 | 0.003161
38 | 0.99031 | -0.18423 | 0.0051361 | 0.0012872
39 | 0.98689 | -0.25017 | 0.0015173 | 0.00038026
40 | 0.98655 | -0.25676 | 0.0059843 | 0.0014998
41 | 0.97708 | -0.44064 | 0 | 0
42 | 0.99103 | -0.17057 | 0 | 0
43 | 0.99058 | -0.17905 | 0.0061219 | 0.0015343
44 | 0.98586 | -0.27026 | 0.007826 | 0.0019614
45 | 0.98637 | -0.26036 | 0.002841 | 0.00071203
46 | 0.97564 | -0.46909 | 0.0022754 | 0.00057027
47 | 0.97697 | -0.44279 | 0.0028576 | 0.00071618
48 | 0.97431 | -0.49524 | 0.01462 | 0.0036641
49 | 0.97464 | -0.48864 | 0.0025469 | 0.0006383
50 | 0.97551 | -0.47162 | 0.0082444 | 0.0020663
51 | 0.9856 | -0.27525 | 0.0019795 | 0.00049612
52 | 0.98547 | -0.27783 | 0.0019771 | 0.00049551
53 | 0.98545 | -0.27815 | 0.0031219 | 0.00078241
54 | 0.98476 | -0.29164 | 0.010504 | 0.0026325
55 | 0.98516 | -0.28382 | 0 | 0
56 | 0.98411 | -0.3042 | 0.0062461 | 0.0015654
57 | 0.9855 | -0.27696 | 0.10298 | 0.025809
58 | 0.98268 | -0.33147 | 0.0018051 | 0.00045241
59 | 0.97412 | -0.49904 | 0.0050866 | 0.0012748
60 | 0.97406 | -0.5003 | 0.0077918 | 0.0019528
61 | 0.97441 | -0.4934 | 0.060107 | 0.015064
62 | 0.97457 | -0.49023 | 0.056112 | 0.014063
63 | 0.97647 | -0.45271 | 0.018387 | 0.0046081
64 | 0.97774 | -0.42777 | 0.0039132 | 0.00098075
65 | 0.97816 | -0.41963 | 0.0067647 | 0.0016954
66 | 0.97873 | -0.4085 | 0.0046669 | 0.0011696
67 | 0.97974 | -0.38873 | 0.00090366 | 0.00022648
68 | 0.98042 | -0.37545 | 0 | 0
69 | 0.98183 | -0.34797 | 0.0025147 | 0.00063025
70 | 0.98037 | -0.37646 | 0.00069808 | 0.00017495
71 | 0.98419 | -0.3028 | 0.021318 | 0.0053427
72 | 0.98309 | -0.32411 | 0.0044554 | 0.0011166
73 | 0.984 | -0.30641 | 0.0078314 | 0.0019627
74 | 0.98296 | -0.32652 | 0.0037024 | 0.00092792
75 | 0.98249 | -0.33576 | 0.004412 | 0.0011057
76 | 0.98146 | -0.35576 | 0 | 0
77 | 0.98058 | -0.37294 | 0.006213 | 0.0015571
78 | 0.9782 | -0.41971 | 0.011025 | 0.0027631
79 | 0.97696 | -0.44309 | 0.0020433 | 0.0005121
80 | 0.97655 | -0.45107 | 0.003058 | 0.00076642
81 | 0.976 | -0.46208 | 0.0038954 | 0.00097628
82 | 0.99855 | -0.02795 | 0.0035058 | 0.00087865
83 | 0.99858 | -0.027237 | 0.0035045 | 0.00087832
84 | 0.99873 | -0.024335 | 0.0069806 | 0.0017495
85 | 0.97657 | -0.45168 | 0.0039472 | 0.00098926
86 | 0.97656 | -0.452 | 0.0011926 | 0.0002989
87 | 0.97739 | -0.43559 | 0.0014809 | 0.00037116
88 | 0.97648 | -0.45354 | 0.001718 | 0.00043058
89 | 0.97727 | -0.43785 | 0.0031854 | 0.00079832
90 | 0.97734 | -0.43663 | 0.0039998 | 0.0010024
91 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0012285 | -0.0003073 | 0.0012286 | 0.00030661 | 7.1519e-08 | -6.8915e-07 | 0.0018366 | 0.0018363 | 0.0018366 | 0.99525 | -0.09003 | 0.99531 | -0.088805 | 0.50455
1 | 0.00070653 | 0.00017648 | -0.00070652 | -0.00017653 | 1.8322e-09 | -5.5749e-08 | 0.0010561 | 0.0010561 | 0.0010561 | 0.99525 | -0.09003 | 0.99525 | -0.090085 | 0.29015
2 | -0.001516 | -0.00037863 | 0.0015162 | 0.00037741 | 1.9951e-07 | -1.2195e-06 | 0.0022659 | 0.0022655 | 0.0022659 | 0.99531 | -0.088805 | 0.99546 | -0.086032 | 0.62251
3 | 0.00059341 | 0.00014852 | -0.00059341 | -0.00014872 | 4.7291e-09 | -2.0518e-07 | 0.00088715 | 0.00088723 | 0.00088723 | 0.99525 | -0.090085 | 0.99524 | -0.090252 | 0.24374
4 | 0.00011311 | 2.8014e-05 | -0.00011311 | -2.8348e-05 | 2.7549e-10 | -3.3385e-07 | 0.000169 | 0.00016911 | 0.00016911 | 0.99525 | -0.090085 | 0.99525 | -0.090136 | 0.04646
5 | -0.0029792 | -0.00074409 | 0.0029799 | 0.00074334 | 6.7333e-07 | -7.4695e-07 | 0.0044524 | 0.004452 | 0.0044524 | 0.99546 | -0.086032 | 0.9957 | -0.081274 | 1.2232
6 | 0.31388 | 0.080363 | -0.31317 | -0.079912 | 0.00070976 | 0.00045146 | 0.46968 | 0.46968 | 0.46968 | 0.9957 | -0.081274 | 0.99324 | -0.12807 | 25.8067
7 | -0.56447 | -0.1444 | 0.5658 | 0.14525 | 0.0013257 | 0.00084684 | 0.84461 | 0.84461 | 0.84461 | 0.9957 | -0.081274 | 0.99826 | -0.032875 | 46.4073
8 | 0.24761 | 0.063292 | -0.24741 | -0.063163 | 0.00020243 | 0.00012828 | 0.37048 | 0.37048 | 0.37048 | 0.9957 | -0.081274 | 0.99481 | -0.09819 | 20.3561
9 | 0.31201 | 0.07962 | -0.31169 | -0.079418 | 0.00031759 | 0.00020201 | 0.46793 | 0.46793 | 0.46793 | 0.99324 | -0.12807 | 0.99214 | -0.14917 | 25.7107
10 | -0.56661 | -0.14545 | 0.5667 | 0.14551 | 8.9002e-05 | 5.6853e-05 | 0.84583 | 0.84583 | 0.84583 | 0.99826 | -0.032875 | 0.99843 | -0.029639 | 46.4739
11 | 0.24579 | 0.062759 | -0.24557 | -0.062618 | 0.00022155 | 0.00014038 | 0.36806 | 0.36806 | 0.36806 | 0.99481 | -0.09819 | 0.99383 | -0.11686 | 20.2233
12 | 0.30787 | 0.078461 | -0.3077 | -0.078352 | 0.00017229 | 0.00010957 | 0.46221 | 0.46221 | 0.46221 | 0.99214 | -0.14917 | 0.99153 | -0.16077 | 25.3962
13 | -0.5706 | -0.14648 | 0.57142 | 0.14701 | 0.00082216 | 0.00052519 | 0.85163 | 0.85163 | 0.85163 | 0.99843 | -0.029639 | 1 | 0 | 46.7929
14 | 0.24362 | 0.062128 | -0.24318 | -0.061854 | 0.00043307 | 0.00027437 | 0.36514 | 0.36514 | 0.36514 | 0.99383 | -0.11686 | 0.9919 | -0.15375 | 20.0625
15 | -0.01705 | -0.0042719 | 0.017054 | 0.004274 | 3.6788e-06 | 2.1758e-06 | 0.026099 | 0.026099 | 0.026099 | 0.9721 | -0.53885 | 0.97233 | -0.53432 | 7.17
16 | 0.0047143 | 0.0011802 | -0.0047111 | -0.0011802 | 3.2266e-06 | 1.8104e-08 | 0.0072158 | 0.0072166 | 0.0072166 | 0.9721 | -0.53885 | 0.97137 | -0.55323 | 1.9826
17 | -0.018472 | -0.0046293 | 0.018487 | 0.0046388 | 1.5798e-05 | 9.4563e-06 | 0.028268 | 0.028268 | 0.028268 | 0.97233 | -0.53432 | 0.97323 | -0.51639 | 7.766
18 | 0.0047111 | 0.0011802 | -0.0047103 | -0.0011802 | 7.7901e-07 | 4.8923e-09 | 0.0072166 | 0.0072168 | 0.0072168 | 0.97137 | -0.55323 | 0.9712 | -0.55671 | 1.9826
19 | -0.026707 | -0.0066988 | 0.026715 | 0.0067038 | 7.96e-06 | 4.9362e-06 | 0.040835 | 0.040835 | 0.040835 | 0.97323 | -0.51639 | 0.97355 | -0.51014 | 11.2185
20 | 0.0040411 | 0.0010125 | -0.0040404 | -0.0010126 | 7.1325e-07 | -1.5735e-07 | 0.0061915 | 0.0061917 | 0.0061917 | 0.9712 | -0.55671 | 0.97101 | -0.56041 | 1.701
21 | -0.029202 | -0.0073271 | 0.029223 | 0.00734 | 2.0758e-05 | 1.2939e-05 | 0.044636 | 0.044636 | 0.044636 | 0.97355 | -0.51014 | 0.97431 | -0.49524 | 12.2627
22 | 0.3003 | 0.076498 | -0.30008 | -0.076355 | 0.00022484 | 0.00014295 | 0.45111 | 0.45111 | 0.45111 | 0.99153 | -0.16077 | 0.99072 | -0.1763 | 24.7864
23 | 0.019031 | 0.0047772 | -0.01901 | -0.0047644 | 2.1457e-05 | 1.2798e-05 | 0.028322 | 0.028322 | 0.028322 | 1 | 0 | 0.99877 | -0.023666 | 7.7807
24 | 0.22792 | 0.058028 | -0.22786 | -0.057992 | 5.5954e-05 | 3.54e-05 | 0.34224 | 0.34224 | 0.34224 | 0.9919 | -0.15375 | 0.99164 | -0.15884 | 18.8043
25 | 0.29537 | 0.075175 | -0.295 | -0.074943 | 0.00036405 | 0.00023141 | 0.44404 | 0.44404 | 0.44404 | 0.99072 | -0.1763 | 0.98939 | -0.20191 | 24.3977
26 | 0.013993 | 0.003507 | -0.013992 | -0.0035067 | 4.4588e-07 | 2.4956e-07 | 0.020847 | 0.020847 | 0.020847 | 0.99877 | -0.023666 | 0.99873 | -0.024335 | 5.7271
27 | 0.21973 | 0.055954 | -0.2196 | -0.055875 | 0.00012429 | 7.8566e-05 | 0.33003 | 0.33003 | 0.33003 | 0.99164 | -0.15884 | 0.99103 | -0.17057 | 18.1336
28 | 0.295 | 0.074943 | -0.29467 | -0.074732 | 0.00033167 | 0.00021083 | 0.44404 | 0.44404 | 0.44404 | 0.98939 | -0.20191 | 0.98817 | -0.22529 | 24.3977
29 | 0.28869 | 0.073232 | -0.28845 | -0.07308 | 0.000239 | 0.00015188 | 0.43503 | 0.43503 | 0.43503 | 0.98817 | -0.22529 | 0.98728 | -0.24252 | 23.9025
30 | 0.27869 | 0.070634 | -0.27853 | -0.070535 | 0.00015586 | 9.9001e-05 | 0.42032 | 0.42032 | 0.42032 | 0.98728 | -0.24252 | 0.98668 | -0.25417 | 23.0943
31 | 0.27365 | 0.069312 | -0.27335 | -0.069122 | 0.00029924 | 0.00019002 | 0.41295 | 0.41295 | 0.41295 | 0.98668 | -0.25417 | 0.9855 | -0.27696 | 22.6898
32 | -0.086974 | -0.02206 | 0.086982 | 0.022065 | 7.1479e-06 | 4.5607e-06 | 0.13166 | 0.13166 | 0.13166 | 0.9837 | -0.31172 | 0.98379 | -0.31001 | 36.1698
33 | 0.085704 | 0.021742 | -0.085423 | -0.021562 | 0.00028144 | 0.00017956 | 0.12974 | 0.12974 | 0.12974 | 0.9837 | -0.31172 | 0.98017 | -0.38026 | 35.642
34 | -0.090356 | -0.02291 | 0.090664 | 0.023107 | 0.00030812 | 0.00019664 | 0.13676 | 0.13676 | 0.13676 | 0.98379 | -0.31001 | 0.98745 | -0.23933 | 37.5719
35 | 0.081739 | 0.020639 | -0.081714 | -0.020623 | 2.5911e-05 | 1.6527e-05 | 0.12415 | 0.12415 | 0.12415 | 0.98017 | -0.38026 | 0.97983 | -0.38687 | 34.1059
36 | -0.20765 | -0.052615 | 0.20793 | 0.052794 | 0.00028307 | 0.0001787 | 0.31312 | 0.31312 | 0.31312 | 0.98745 | -0.23933 | 0.98892 | -0.211 | 17.2044
37 | 0.11699 | 0.029508 | -0.11694 | -0.029479 | 4.7993e-05 | 2.94e-05 | 0.17636 | 0.17636 | 0.17636 | 0.98745 | -0.23933 | 0.98701 | -0.2479 | 9.6901
38 | 0.081714 | 0.020623 | -0.081596 | -0.020548 | 0.00011722 | 7.4764e-05 | 0.12415 | 0.12415 | 0.12415 | 0.97983 | -0.38687 | 0.9783 | -0.41687 | 34.1059
39 | -0.20793 | -0.052794 | 0.2082 | 0.052963 | 0.0002682 | 0.00016931 | 0.31312 | 0.31312 | 0.31312 | 0.98892 | -0.211 | 0.99031 | -0.18423 | 17.2044
40 | 0.079648 | 0.020107 | -0.07964 | -0.020102 | 8.6395e-06 | 5.0193e-06 | 0.12013 | 0.12013 | 0.12013 | 0.98701 | -0.2479 | 0.98689 | -0.25017 | 6.6005
41 | 0.037291 | 0.0093719 | -0.037276 | -0.0093619 | 1.5753e-05 | 9.9122e-06 | 0.05623 | 0.05623 | 0.05623 | 0.98701 | -0.2479 | 0.98655 | -0.25676 | 15.4478
42 | 0.068984 | 0.017387 | -0.068905 | -0.017337 | 7.8358e-05 | 4.9911e-05 | 0.10496 | 0.10496 | 0.10496 | 0.9783 | -0.41687 | 0.97708 | -0.44064 | 28.8355
43 | -0.21334 | -0.054251 | 0.21339 | 0.054284 | 5.3263e-05 | 3.3644e-05 | 0.32084 | 0.32084 | 0.32084 | 0.99031 | -0.18423 | 0.99058 | -0.17905 | 17.6284
44 | 0.078122 | 0.019722 | -0.078047 | -0.019674 | 7.5112e-05 | 4.7335e-05 | 0.11784 | 0.11784 | 0.11784 | 0.98689 | -0.25017 | 0.98586 | -0.27026 | 16.1871
45 | 0.031291 | 0.0078621 | -0.031286 | -0.0078588 | 5.3803e-06 | 3.3612e-06 | 0.047204 | 0.047204 | 0.047204 | 0.98655 | -0.25676 | 0.98637 | -0.26036 | 12.9681
46 | 0.057045 | 0.014365 | -0.056968 | -0.014316 | 7.7479e-05 | 4.9244e-05 | 0.086899 | 0.086899 | 0.086899 | 0.97708 | -0.44064 | 0.97564 | -0.46909 | 23.8735
47 | 0.01186 | 0.002972 | -0.011859 | -0.0029713 | 1.2139e-06 | 6.5266e-07 | 0.018062 | 0.018062 | 0.018062 | 0.97708 | -0.44064 | 0.97697 | -0.44279 | 4.9621
48 | 0.2196 | 0.055875 | -0.21951 | -0.055819 | 8.9637e-05 | 5.6661e-05 | 0.33003 | 0.33003 | 0.33003 | 0.99103 | -0.17057 | 0.99058 | -0.17905 | 18.1336
49 | 0.070221 | 0.017713 | -0.070149 | -0.017667 | 7.1803e-05 | 4.5737e-05 | 0.10603 | 0.10603 | 0.10603 | 0.98586 | -0.27026 | 0.98476 | -0.29164 | 29.1292
50 | 0.028445 | 0.0071468 | -0.028425 | -0.0071342 | 2.0202e-05 | 1.2556e-05 | 0.042918 | 0.042918 | 0.042918 | 0.98637 | -0.26036 | 0.9856 | -0.27525 | 11.7907
51 | 0.054692 | 0.013745 | -0.054686 | -0.013741 | 6.5982e-06 | 4.1913e-06 | 0.083429 | 0.083429 | 0.083429 | 0.97564 | -0.46909 | 0.97551 | -0.47162 | 22.92
52 | 0.0090015 | 0.0022551 | -0.0090014 | -0.0022551 | 1.2785e-07 | 5.9109e-08 | 0.01371 | 0.01371 | 0.01371 | 0.97697 | -0.44279 | 0.97696 | -0.44309 | 3.7664
53 | -0.043843 | -0.011004 | 0.043857 | 0.011013 | 1.3808e-05 | 8.7349e-06 | 0.066965 | 0.066965 | 0.066965 | 0.97431 | -0.49524 | 0.97464 | -0.48864 | 18.3969
54 | -0.046403 | -0.011651 | 0.046441 | 0.011675 | 3.7707e-05 | 2.3882e-05 | 0.070853 | 0.070853 | 0.070853 | 0.97464 | -0.48864 | 0.97551 | -0.47162 | 19.4652
55 | 0.026445 | 0.0066381 | -0.026442 | -0.0066361 | 3.2477e-06 | 2.0093e-06 | 0.039929 | 0.039929 | 0.039929 | 0.9856 | -0.27525 | 0.98547 | -0.27783 | 10.9696
56 | 0.024465 | 0.0061406 | -0.024465 | -0.0061403 | 3.7801e-07 | 2.3252e-07 | 0.036944 | 0.036944 | 0.036944 | 0.98547 | -0.27783 | 0.98545 | -0.27815 | 10.1495
57 | 0.021343 | 0.0053579 | -0.021337 | -0.0053544 | 5.7716e-06 | 3.5051e-06 | 0.03223 | 0.03223 | 0.03223 | 0.98545 | -0.27815 | 0.98516 | -0.28382 | 8.8545
58 | 0.059646 | 0.015035 | -0.05961 | -0.015012 | 3.5824e-05 | 2.2778e-05 | 0.090159 | 0.090159 | 0.090159 | 0.98476 | -0.29164 | 0.98411 | -0.3042 | 24.7689
59 | 0.021337 | 0.0053544 | -0.021318 | -0.0053427 | 1.9297e-05 | 1.172e-05 | 0.03223 | 0.03223 | 0.03223 | 0.98516 | -0.28382 | 0.98419 | -0.3028 | 8.8545
60 | 0.053364 | 0.013447 | -0.053358 | -0.013443 | 5.6415e-06 | 3.5812e-06 | 0.080714 | 0.080714 | 0.080714 | 0.98411 | -0.3042 | 0.984 | -0.30641 | 22.1743
61 | 0.17037 | 0.043313 | -0.16993 | -0.043033 | 0.00044606 | 0.00027978 | 0.25747 | 0.25747 | 0.25747 | 0.9855 | -0.27696 | 0.98268 | -0.33147 | 14.1467
62 | 0.16812 | 0.042581 | -0.16799 | -0.042497 | 0.00013312 | 8.3468e-05 | 0.25474 | 0.25474 | 0.25474 | 0.98268 | -0.33147 | 0.98183 | -0.34797 | 13.9965
63 | 0.0077923 | 0.001953 | -0.0077918 | -0.0019528 | 4.6929e-07 | 1.904e-07 | 0.011903 | 0.011903 | 0.011903 | 0.97412 | -0.49904 | 0.97406 | -0.5003 | 3.2701
64 | -0.012879 | -0.0032278 | 0.012882 | 0.0032298 | 3.4622e-06 | 1.9187e-06 | 0.019673 | 0.019673 | 0.019673 | 0.97412 | -0.49904 | 0.97441 | -0.4934 | 5.4047
65 | -0.072989 | -0.018294 | 0.073 | 0.018301 | 1.1026e-05 | 7.027e-06 | 0.11146 | 0.11146 | 0.11146 | 0.97441 | -0.4934 | 0.97457 | -0.49023 | 30.6215
66 | -0.12911 | -0.032364 | 0.12934 | 0.032512 | 0.00023123 | 0.00014779 | 0.19714 | 0.19714 | 0.19714 | 0.97457 | -0.49023 | 0.97647 | -0.45271 | 54.1585
67 | -0.14773 | -0.03712 | 0.14791 | 0.037232 | 0.0001761 | 0.00011224 | 0.22516 | 0.22516 | 0.22516 | 0.97647 | -0.45271 | 0.97774 | -0.42777 | 30.928
68 | -0.15182 | -0.038213 | 0.15188 | 0.03825 | 5.906e-05 | 3.6873e-05 | 0.23111 | 0.23111 | 0.23111 | 0.97774 | -0.42777 | 0.97816 | -0.41963 | 12.6984
69 | -0.15864 | -0.039945 | 0.15873 | 0.039998 | 8.4531e-05 | 5.2885e-05 | 0.2414 | 0.2414 | 0.2414 | 0.97816 | -0.41963 | 0.97873 | -0.4085 | 13.2638
70 | -0.16339 | -0.041168 | 0.16355 | 0.041265 | 0.00015467 | 9.6889e-05 | 0.2485 | 0.2485 | 0.2485 | 0.97873 | -0.4085 | 0.97974 | -0.38873 | 13.6536
71 | -0.16445 | -0.041491 | 0.16456 | 0.041557 | 0.00010459 | 6.5533e-05 | 0.24987 | 0.24987 | 0.24987 | 0.97974 | -0.38873 | 0.98042 | -0.37545 | 13.729
72 | 0.00069811 | 0.00017397 | -0.00069808 | -0.00017495 | 3.3493e-08 | -9.8211e-07 | 0.0010592 | 0.0010595 | 0.0010595 | 0.98042 | -0.37545 | 0.98037 | -0.37646 | 0.29108
73 | -0.16526 | -0.041731 | 0.16547 | 0.041867 | 0.00021789 | 0.00013653 | 0.25093 | 0.25093 | 0.25093 | 0.98042 | -0.37545 | 0.98183 | -0.34797 | 13.7872
74 | -0.045488 | -0.011456 | 0.045527 | 0.01148 | 3.8532e-05 | 2.4385e-05 | 0.068872 | 0.068872 | 0.068872 | 0.98309 | -0.32411 | 0.984 | -0.30641 | 18.9208
75 | 0.041033 | 0.010339 | -0.041028 | -0.010336 | 4.7274e-06 | 2.9841e-06 | 0.062128 | 0.062128 | 0.062128 | 0.98309 | -0.32411 | 0.98296 | -0.32652 | 17.0681
76 | 0.037326 | 0.0094083 | -0.037309 | -0.0093979 | 1.6495e-05 | 1.0382e-05 | 0.056523 | 0.056523 | 0.056523 | 0.98296 | -0.32652 | 0.98249 | -0.33576 | 15.5283
77 | 0.032897 | 0.0082922 | -0.032866 | -0.0082725 | 3.1447e-05 | 1.9699e-05 | 0.049841 | 0.049841 | 0.049841 | 0.98249 | -0.33576 | 0.98146 | -0.35576 | 13.6926
78 | 0.032866 | 0.0082725 | -0.032839 | -0.0082556 | 2.6966e-05 | 1.6893e-05 | 0.049841 | 0.049841 | 0.049841 | 0.98146 | -0.35576 | 0.98058 | -0.37294 | 13.6927
79 | 0.026626 | 0.0066985 | -0.026566 | -0.0066617 | 5.9358e-05 | 3.6769e-05 | 0.040413 | 0.040414 | 0.040414 | 0.98058 | -0.37294 | 0.9782 | -0.41971 | 11.1026
80 | 0.015542 | 0.0038986 | -0.01553 | -0.0038918 | 1.1759e-05 | 6.822e-06 | 0.023643 | 0.023643 | 0.023643 | 0.9782 | -0.41971 | 0.97739 | -0.43559 | 6.4954
81 | 0.0069581 | 0.001743 | -0.0069555 | -0.0017421 | 2.643e-06 | 9.0607e-07 | 0.010598 | 0.010598 | 0.010598 | 0.97696 | -0.44309 | 0.97655 | -0.45107 | 2.9115
82 | 0.0038974 | 0.00097565 | -0.0038954 | -0.00097628 | 2.0433e-06 | -6.2419e-07 | 0.0059383 | 0.005939 | 0.005939 | 0.97655 | -0.45107 | 0.976 | -0.46208 | 1.6316
83 | -0.0035058 | -0.00087865 | 0.003506 | 0.00087857 | 1.1911e-07 | -7.6004e-08 | 0.0052243 | 0.0052243 | 0.0052243 | 0.99855 | -0.02795 | 0.99858 | -0.027237 | 1.4353
84 | -0.0070105 | -0.0017569 | 0.0070115 | 0.0017572 | 9.6931e-07 | 3.1044e-07 | 0.010447 | 0.010446 | 0.010447 | 0.99858 | -0.027237 | 0.99873 | -0.024335 | 2.8699
85 | 0.0029108 | 0.0007289 | -0.0029108 | -0.00072895 | 4.479e-08 | -4.7308e-08 | 0.0044351 | 0.0044351 | 0.0044351 | 0.97657 | -0.45168 | 0.97656 | -0.452 | 1.2184
86 | -0.006858 | -0.0017182 | 0.0068633 | 0.0017199 | 5.2567e-06 | 1.7566e-06 | 0.010449 | 0.010449 | 0.010449 | 0.97657 | -0.45168 | 0.97739 | -0.43559 | 2.8707
87 | 0.0017182 | 0.00043005 | -0.001718 | -0.00043058 | 1.2608e-07 | -5.3301e-07 | 0.0026178 | 0.0026181 | 0.0026181 | 0.97656 | -0.452 | 0.97648 | -0.45354 | 0.71925
88 | 0.0071857 | 0.0018007 | -0.0071853 | -0.0018006 | 3.5633e-07 | 1.2855e-07 | 0.01094 | 0.01094 | 0.01094 | 0.97739 | -0.43559 | 0.97734 | -0.43663 | 3.0054
89 | -0.0031854 | -0.00079832 | 0.0031855 | 0.00079818 | 1.8434e-07 | -1.4388e-07 | 0.0048501 | 0.00485 | 0.0048501 | 0.97727 | -0.43785 | 0.97734 | -0.43663 | 1.3324

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59436 | 0.15235

## res_load
| p_mw | q_mvar
0 | 0.00052199 | 0.00013082
1 | 0.00028738 | 7.2023e-05
2 | 0.0014631 | 0.00036668
3 | 0.00059341 | 0.00014872
4 | 0.00011311 | 2.8348e-05
5 | 0.0011661 | 0.00029226
6 | 0.00081445 | 0.00020412
7 | 0.0016156 | 0.0004049
8 | 0.0038168 | 0.00095657
9 | 0.0038958 | 0.00097637
10 | 0.0019561 | 0.00049026
11 | 0.012336 | 0.0030917
12 | 0.0014176 | 0.00035529
13 | 0.0082196 | 0.00206
14 | 0.00066919 | 0.00016771
15 | 0.0040404 | 0.0010126
16 | 0.002487 | 0.0006233
17 | 0.0073952 | 0.0018534
18 | 0.0022611 | 0.00056669
19 | 0.015265 | 0.0038257
20 | 0.0047108 | 0.0011806
21 | 0.0050174 | 0.0012575
22 | 0.0081347 | 0.0020387
23 | 0.0059853 | 0.0015001
24 | 0.00976 | 0.0024461
25 | 0.0048815 | 0.0012234
26 | 0.0012703 | 0.00031836
27 | 0.0033743 | 0.00084568
28 | 0.0036832 | 0.0009231
29 | 0.012613 | 0.003161
30 | 0.0051361 | 0.0012872
31 | 0.0015173 | 0.00038026
32 | 0.0059843 | 0.0014998
33 | 0.0061219 | 0.0015343
34 | 0.007826 | 0.0019614
35 | 0.002841 | 0.00071203
36 | 0.0022754 | 0.00057027
37 | 0.0028576 | 0.00071618
38 | 0.01462 | 0.0036641
39 | 0.0025469 | 0.0006383
40 | 0.0082444 | 0.0020663
41 | 0.0019795 | 0.00049612
42 | 0.0019771 | 0.00049551
43 | 0.0031219 | 0.00078241
44 | 0.010504 | 0.0026325
45 | 0.0062461 | 0.0015654
46 | 0.10298 | 0.025809
47 | 0.0018051 | 0.00045241
48 | 0.0050866 | 0.0012748
49 | 0.0077918 | 0.0019528
50 | 0.060107 | 0.015064
51 | 0.056112 | 0.014063
52 | 0.018387 | 0.0046081
53 | 0.0039132 | 0.00098075
54 | 0.0067647 | 0.0016954
55 | 0.0046669 | 0.0011696
56 | 0.00090366 | 0.00022648
57 | 0.0025147 | 0.00063025
58 | 0.00069808 | 0.00017495
59 | 0.021318 | 0.0053427
60 | 0.0044554 | 0.0011166
61 | 0.0078314 | 0.0019627
62 | 0.0037024 | 0.00092792
63 | 0.004412 | 0.0011057
64 | 0.006213 | 0.0015571
65 | 0.011025 | 0.0027631
66 | 0.0020433 | 0.0005121
67 | 0.003058 | 0.00076642
68 | 0.0038954 | 0.00097628
69 | 0.0035058 | 0.00087865
70 | 0.0035045 | 0.00087832
71 | 0.0069806 | 0.0017495
72 | 0.0039472 | 0.00098926
73 | 0.0011926 | 0.0002989
74 | 0.0014809 | 0.00037116
75 | 0.001718 | 0.00043058
76 | 0.0031854 | 0.00079832
77 | 0.0039998 | 0.0010024

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1