## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1706-8_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1706-8_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1706-8_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1706-8_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1706-8_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1706-8_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1706-8_0_2_node_37 | 0.4 | n |  | TRUE
7 | bus_LV_1706-8_0_2_node_73 | 0.4 | n |  | TRUE
8 | bus_LV_1706-8_0_2_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1706-8_0_2_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1706-8_0_2_node_21 | 0.4 | n |  | TRUE
11 | bus_LV_1706-8_0_2_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1706-8_0_2_node_74 | 0.4 | n |  | TRUE
13 | bus_LV_1706-8_0_2_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1706-8_0_2_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_1706-8_0_2_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1706-8_0_2_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1706-8_0_2_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1706-8_0_2_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1706-8_0_2_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1706-8_0_2_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1706-8_0_2_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1706-8_0_2_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_1706-8_0_2_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_1706-8_0_2_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1706-8_0_2_node_71 | 0.4 | n |  | TRUE
26 | bus_LV_1706-8_0_2_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1706-8_0_2_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1706-8_0_2_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_1706-8_0_2_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1706-8_0_2_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_1706-8_0_2_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1706-8_0_2_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_1706-8_0_2_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_1706-8_0_2_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_1706-8_0_2_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1706-8_0_2_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1706-8_0_2_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_1706-8_0_2_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1706-8_0_2_node_84 | 0.4 | n |  | TRUE
40 | bus_LV_1706-8_0_2_node_89 | 0.4 | n |  | TRUE
41 | bus_LV_1706-8_0_2_node_83 | 0.4 | n |  | TRUE
42 | bus_LV_1706-8_0_2_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_1706-8_0_2_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_1706-8_0_2_node_75 | 0.4 | n |  | TRUE
45 | bus_LV_1706-8_0_2_node_81 | 0.4 | n |  | TRUE
46 | bus_LV_1706-8_0_2_node_82 | 0.4 | n |  | TRUE
47 | bus_MV_22_0_node_142 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1706-8_0_2_load_0 | 0 | 0.0044097 | 0.0011052 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1706-8_0_2_load_4 | 4 | 0.00040767 | 0.00010217 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1706-8_0_2_load_5 | 5 | 0.0053525 | 0.0013415 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1706-8_0_2_load_37 | 6 | 0.0046422 | 0.0011635 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1706-8_0_2_load_73 | 7 | 0.0010971 | 0.00027496 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1706-8_0_2_load_21 | 10 | 0.00030264 | 7.5848e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1706-8_0_2_load_19 | 11 | 0.0047261 | 0.0011845 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1706-8_0_2_load_74 | 12 | 0.0016623 | 0.00041661 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1706-8_0_2_load_18 | 14 | 0.0032347 | 0.00081069 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1706-8_0_2_load_6 | 15 | 0.0014732 | 0.00036921 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1706-8_0_2_load_7 | 16 | 0.00089945 | 0.00022542 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1706-8_0_2_load_8 | 17 | 0.0027162 | 0.00068075 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1706-8_0_2_load_10 | 19 | 0.0016135 | 0.00040439 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1706-8_0_2_load_11 | 20 | 0.0041018 | 0.001028 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1706-8_0_2_load_12 | 21 | 0.0060391 | 0.0015135 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1706-8_0_2_load_27 | 22 | 0.005181 | 0.0012985 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1706-8_0_2_load_71 | 25 | 0.00128 | 0.0003208 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1706-8_0_2_load_15 | 26 | 0.00086087 | 0.00021575 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1706-8_0_2_load_13 | 27 | 0.0038077 | 0.0009543 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1706-8_0_2_load_30 | 29 | 0.0013753 | 0.00034467 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1706-8_0_2_load_31 | 30 | 0.0039842 | 0.00099854 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1706-8_0_2_load_32 | 31 | 0.00080871 | 0.00020268 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1706-8_0_2_load_36 | 32 | 0.00094745 | 0.00023745 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1706-8_0_2_load_33 | 33 | 0.001293 | 0.00032406 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1706-8_0_2_load_35 | 34 | 0.00041878 | 0.00010496 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1706-8_0_2_load_29 | 35 | 0.017933 | 0.0044944 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1706-8_0_2_load_24 | 36 | 0.014783 | 0.003705 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1706-8_0_2_load_26 | 37 | 0.0054652 | 0.0013697 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1706-8_0_2_load_89 | 40 | 0.00025006 | 6.267e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1706-8_0_2_load_22 | 42 | 0.0025659 | 0.00064308 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1706-8_0_2_load_23 | 43 | 0.010492 | 0.0026295 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1706-8_0_2_load_75 | 44 | 0.00017234 | 4.3191e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1706-8_0_2_load_81 | 45 | 0.00098394 | 0.0002466 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1706-8_0_2_load_82 | 46 | 0.00056859 | 0.0001425 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1706-8_0_2_line_0 |  | 0 | 1 | 0.071759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1706-8_0_2_line_1 |  | 0 | 2 | 0.064374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1706-8_0_2_line_2 |  | 1 | 3 | 0.012966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1706-8_0_2_line_3 |  | 1 | 4 | 0.082401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1706-8_0_2_line_4 |  | 2 | 5 | 0.0081184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1706-8_0_2_line_5 |  | 3 | 6 | 0.021772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1706-8_0_2_line_6 |  | 4 | 7 | 0.012516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1706-8_0_2_line_7 |  | 5 | 8 | 0.013508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1706-8_0_2_line_8 |  | 7 | 12 | 0.039803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1706-8_0_2_line_9 |  | 8 | 13 | 0.010208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1706-8_0_2_line_10 |  | 8 | 14 | 0.0099176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1706-8_0_2_line_11 |  | 9 | 10 | 0.030868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1706-8_0_2_line_12 |  | 9 | 11 | 0.115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1706-8_0_2_line_13 |  | 10 | 39 | 0.38041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1706-8_0_2_line_14 |  | 11 | 37 | 0.16291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1706-8_0_2_line_15 |  | 13 | 35 | 0.01965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1706-8_0_2_line_16 |  | 13 | 27 | 0.068884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1706-8_0_2_line_17 |  | 15 | 16 | 0.018703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1706-8_0_2_line_18 |  | 15 | 17 | 0.016338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1706-8_0_2_line_19 |  | 16 | 18 | 0.066149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1706-8_0_2_line_20 |  | 17 | 19 | 0.0044167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1706-8_0_2_line_21 |  | 18 | 23 | 0.06502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1706-8_0_2_line_22 |  | 18 | 22 | 0.011746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1706-8_0_2_line_23 |  | 19 | 24 | 0.036825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1706-8_0_2_line_24 |  | 20 | 21 | 0.017811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1706-8_0_2_line_25 |  | 20 | 22 | 0.12163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1706-8_0_2_line_26 |  | 21 | 27 | 0.041306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1706-8_0_2_line_27 |  | 23 | 25 | 0.27558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1706-8_0_2_line_28 |  | 24 | 26 | 0.032043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1706-8_0_2_line_29 |  | 26 | 28 | 0.048358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1706-8_0_2_line_30 |  | 28 | 33 | 0.062565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1706-8_0_2_line_31 |  | 29 | 30 | 0.021708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1706-8_0_2_line_32 |  | 29 | 31 | 0.038688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1706-8_0_2_line_33 |  | 29 | 32 | 0.16114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1706-8_0_2_line_34 |  | 31 | 33 | 0.07502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1706-8_0_2_line_35 |  | 32 | 34 | 0.010556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1706-8_0_2_line_36 |  | 35 | 36 | 0.0094348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1706-8_0_2_line_37 |  | 36 | 43 | 0.017995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1706-8_0_2_line_38 |  | 37 | 38 | 0.049044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1706-8_0_2_line_39 |  | 38 | 42 | 0.1495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1706-8_0_2_line_40 |  | 39 | 40 | 0.1562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1706-8_0_2_line_41 |  | 39 | 41 | 0.10291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1706-8_0_2_line_42 |  | 40 | 44 | 0.089853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1706-8_0_2_line_43 |  | 41 | 45 | 0.027159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1706-8_0_2_line_44 |  | 42 | 43 | 0.066292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1706-8_0_2_line_45 |  | 45 | 46 | 0.097869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1706-8_0_2_trafo_22 | 0.63 MVA 20/0.4 kV | 47 | 42 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2691365.6333 | 1218974.4619 | 2691351.7086 | 1218993.05 | 2691336.0787 | 1219012.4571 | 2691320.1342 | 1219029.8769
1 | 2691267.0056 | 1219065.6352 | 2691289.9814 | 1219053.212 | 2691304.27 | 1219044.0358 | 2691318.9569 | 1219031.1631 | 2691320.1342 | 1219029.8769
2 | 2691365.6333 | 1218974.4619 | 2691374.6359 | 1218983.8175
3 | 2691365.6333 | 1218974.4619 | 2691378.77 | 1218952.3259 | 2691389.0818 | 1218928.312 | 2691399.6758 | 1218899.6831
4 | 2691267.0056 | 1219065.6352 | 2691259.7184 | 1219069.2138
5 | 2691374.6359 | 1218983.8175 | 2691382.7583 | 1219004.0174
6 | 2691404.0193 | 1218887.9455 | 2691399.6758 | 1218899.6831
7 | 2691247.6548 | 1219075.2899 | 2691253.8975 | 1219072.0722 | 2691259.7184 | 1219069.2138
8 | 2691404.0193 | 1218887.9455 | 2691410.3357 | 1218870.8763 | 2691417.5936 | 1218850.5298
9 | 2691238.6248 | 1219080.0994 | 2691247.6548 | 1219075.2899
10 | 2691247.6548 | 1219075.2899 | 2691245.1558 | 1219070.9487 | 2691242.5345 | 1219066.7988
11 | 2691470.531 | 1218974.8716 | 2691479.7896 | 1218959.6477 | 2691482.7909 | 1218948.0747 | 2691483.5003 | 1218947.242
12 | 2691470.531 | 1218974.8716 | 2691472.2401 | 1218986.15 | 2691475.6647 | 1219008.7848 | 2691474.8389 | 1219024.9832 | 2691470.1654 | 1219035.2297 | 2691466.9101 | 1219051.4797 | 2691465.0104 | 1219072.3761 | 2691460.3596 | 1219087.3358
13 | 2691483.5003 | 1218947.242 | 2691849.4487 | 1219051.1418
14 | 2691460.3596 | 1219087.3358 | 2691455.7134 | 1219250.1746
15 | 2691238.6248 | 1219080.0994 | 2691247.2659 | 1219097.199 | 2691247.3998 | 1219097.671
16 | 2691238.6248 | 1219080.0994 | 2691231.8397 | 1219084.5319 | 2691223.7042 | 1219090.4114 | 2691217.9888 | 1219096.3613 | 2691213.5774 | 1219102.409 | 2691209.8297 | 1219109.2341 | 2691207.1269 | 1219116.2198 | 2691204.823 | 1219123.9231 | 2691203.0753 | 1219135.4807
17 | 2691073.6447 | 1219338.6837 | 2691080.7947 | 1219336.3052 | 2691091.6511 | 1219333.6882
18 | 2691073.6447 | 1219338.6837 | 2691067.7576 | 1219340.6422 | 2691058.9811 | 1219345.7081
19 | 2691154.1569 | 1219318.4593 | 2691150.9881 | 1219316.2315 | 2691146.2811 | 1219315.8258 | 2691128.4972 | 1219321.8468 | 2691106.9924 | 1219329.9902 | 2691091.6511 | 1219333.6882
20 | 2691058.9811 | 1219345.7081 | 2691055.1559 | 1219347.9161
21 | 2691154.1569 | 1219318.4593 | 2691149.8479 | 1219331.7136 | 2691139.313 | 1219351.0768 | 2691135.8383 | 1219359.9075 | 2691137.5052 | 1219367.0379 | 2691139.6885 | 1219370.1735 | 2691147.8361 | 1219372.3996
22 | 2691154.1569 | 1219318.4593 | 2691163.2563 | 1219311.0314
23 | 2691020.9527 | 1219351.0119 | 2691026.6201 | 1219354.6232 | 2691035.5308 | 1219355.5933 | 2691046.0231 | 1219352.3959 | 2691055.0158 | 1219347.997 | 2691055.1559 | 1219347.9161
24 | 2691199.2256 | 1219176.5981 | 2691197.5133 | 1219194.3263
25 | 2691197.5133 | 1219194.3263 | 2691163.2563 | 1219311.0314
26 | 2691199.2256 | 1219176.5981 | 2691200.1202 | 1219167.3365 | 2691202.3907 | 1219140.0081 | 2691203.0753 | 1219135.4807
27 | 2691147.8361 | 1219372.3996 | 2691325.4235 | 1219583.1251
28 | 2691020.9527 | 1219351.0119 | 2691003.8404 | 1219378.1025
29 | 2690979.0042 | 1219419.5739 | 2690988.8846 | 1219401.7792 | 2691003.8404 | 1219378.1025
30 | 2690979.0042 | 1219419.5739 | 2690984.814 | 1219426.7786 | 2690985.4148 | 1219434.1484 | 2690983.4304 | 1219439.3439 | 2690971.9592 | 1219457.4479 | 2690968.6893 | 1219468.7946 | 2690969.5558 | 1219475.8546
31 | 2691041.392 | 1219575.19 | 2691019.7137 | 1219574.0462 | 2691019.7137 | 1219574.0462
32 | 2690993.7944 | 1219546.1656 | 2691011.9222 | 1219569.891 | 2691019.7137 | 1219574.0462
33 | 2691019.7137 | 1219574.0462 | 2690898.7272 | 1219680.4862
34 | 2690993.7944 | 1219546.1656 | 2690990.4412 | 1219541.7769 | 2690984.4201 | 1219530.5328 | 2690970.3834 | 1219482.5966 | 2690969.5558 | 1219475.8546
35 | 2690894.1395 | 1219689.9931 | 2690898.7272 | 1219680.4862
36 | 2691249.9765 | 1219106.7471 | 2691247.3998 | 1219097.671
37 | 2691255.2718 | 1219123.9354 | 2691253.3149 | 1219118.5063 | 2691249.9765 | 1219106.7471
38 | 2691413.3706 | 1219264.4935 | 2691417.373 | 1219265.311 | 2691431.4398 | 1219267.5951 | 2691442.0192 | 1219264.1884 | 2691451.1956 | 1219254.7783 | 2691455.7134 | 1219250.1746
39 | 2691294.2514 | 1219174.1625 | 2691413.3706 | 1219264.4935
40 | 2691849.4487 | 1219051.1418 | 2691832.6754 | 1219065.849 | 2691829.4618 | 1219079.331 | 2691834.8342 | 1219090.2435 | 2691851.069 | 1219104.5369 | 2691852.3309 | 1219116.22 | 2691850.103 | 1219139.6017 | 2691856.5064 | 1219180.6065 | 2691854.3287 | 1219189.9126
41 | 2691876.1572 | 1218963.1597 | 2691883.0608 | 1218974.6963 | 2691887.1319 | 1218984.3546 | 2691886.0512 | 1219002.2503 | 2691875.5203 | 1219018.21 | 2691849.4487 | 1219051.1418
42 | 2691854.3287 | 1219189.9126 | 2691907.3143 | 1219262.4806
43 | 2691876.1572 | 1218963.1597 | 2691872.4048 | 1218966.2929 | 2691860.7976 | 1218953.6163 | 2691856.8871 | 1218950.3703
44 | 2691255.2718 | 1219123.9354 | 2691263.2163 | 1219145.9769 | 2691280.1109 | 1219166.3163 | 2691292.6876 | 1219174.2255 | 2691294.2514 | 1219174.1625
45 | 2691774.8557 | 1218933.7672 | 2691786.904 | 1218940.9911 | 2691811.6243 | 1218959.2734 | 2691819.6227 | 1218959.3857 | 2691833.2088 | 1218951.0448 | 2691841.3512 | 1218943.7876 | 2691848.0498 | 1218943.0348 | 2691856.8871 | 1218950.3703

## bus_geodata
| x | y | coords
0 | 2691320.1342 | 1219029.8769
1 | 2691365.6333 | 1218974.4619
2 | 2691267.0056 | 1219065.6352
3 | 2691374.6359 | 1218983.8175
4 | 2691399.6758 | 1218899.6831
5 | 2691259.7184 | 1219069.2138
6 | 2691382.7583 | 1219004.0174
7 | 2691404.0193 | 1218887.9455
8 | 2691247.6548 | 1219075.2899
9 | 2691470.531 | 1218974.8716
10 | 2691483.5003 | 1218947.242
11 | 2691460.3596 | 1219087.3358
12 | 2691417.5936 | 1218850.5298
13 | 2691238.6248 | 1219080.0994
14 | 2691242.5345 | 1219066.7988
15 | 2691073.6447 | 1219338.6837
16 | 2691091.6511 | 1219333.6882
17 | 2691058.9811 | 1219345.7081
18 | 2691154.1569 | 1219318.4593
19 | 2691055.1559 | 1219347.9161
20 | 2691197.5133 | 1219194.3263
21 | 2691199.2256 | 1219176.5981
22 | 2691163.2563 | 1219311.0314
23 | 2691147.8361 | 1219372.3996
24 | 2691020.9527 | 1219351.0119
25 | 2691325.4235 | 1219583.1251
26 | 2691003.8404 | 1219378.1025
27 | 2691203.0753 | 1219135.4807
28 | 2690979.0042 | 1219419.5739
29 | 2691019.7137 | 1219574.0462
30 | 2691041.392 | 1219575.19
31 | 2690993.7944 | 1219546.1656
32 | 2690898.7272 | 1219680.4862
33 | 2690969.5558 | 1219475.8546
34 | 2690894.1395 | 1219689.9931
35 | 2691247.3998 | 1219097.671
36 | 2691249.9765 | 1219106.7471
37 | 2691455.7134 | 1219250.1746
38 | 2691413.3706 | 1219264.4935
39 | 2691849.4487 | 1219051.1418
40 | 2691854.3287 | 1219189.9126
41 | 2691876.1572 | 1218963.1597
42 | 2691294.2514 | 1219174.1625
43 | 2691255.2718 | 1219123.9354
44 | 2691907.3143 | 1219262.4806
45 | 2691856.8871 | 1218950.3703
46 | 2691774.8557 | 1218933.7672
47 | 2691238.6248 | 1219080.0994

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98946 | -0.2025 | 0.0044097 | 0.0011052
1 | 0.98894 | -0.21249 | 0 | 0
2 | 0.99018 | -0.18849 | 0 | 0
3 | 0.98889 | -0.21356 | 0 | 0
4 | 0.9887 | -0.21714 | 0.00040767 | 0.00010217
5 | 0.99027 | -0.18673 | 0.0053525 | 0.0013415
6 | 0.98879 | -0.21536 | 0.0046422 | 0.0011635
7 | 0.98867 | -0.21776 | 0.0010971 | 0.00027496
8 | 0.99049 | -0.18251 | 0 | 0
9 | 0.99648 | -0.068151 | 0 | 0
10 | 0.99641 | -0.069401 | 0.00030264 | 7.5848e-05
11 | 0.99671 | -0.063491 | 0.0047261 | 0.0011845
12 | 0.98861 | -0.21894 | 0.0016623 | 0.00041661
13 | 0.99068 | -0.17873 | 0 | 0
14 | 0.99046 | -0.18308 | 0.0032347 | 0.00081069
15 | 0.98262 | -0.33539 | 0.0014732 | 0.00036921
16 | 0.98288 | -0.33015 | 0.00089945 | 0.00022542
17 | 0.9824 | -0.33953 | 0.0027162 | 0.00068075
18 | 0.98389 | -0.31059 | 0 | 0
19 | 0.98236 | -0.34043 | 0.0016135 | 0.00040439
20 | 0.98664 | -0.25688 | 0.0041018 | 0.001028
21 | 0.98709 | -0.24828 | 0.0060391 | 0.0015135
22 | 0.98408 | -0.30685 | 0.005181 | 0.0012985
23 | 0.98381 | -0.3121 | 0 | 0
24 | 0.98203 | -0.34688 | 0 | 0
25 | 0.98348 | -0.31848 | 0.00128 | 0.0003208
26 | 0.98174 | -0.35251 | 0.00086087 | 0.00021575
27 | 0.98834 | -0.2239 | 0.0038077 | 0.0009543
28 | 0.98135 | -0.36024 | 0 | 0
29 | 0.98007 | -0.38523 | 0.0013753 | 0.00034467
30 | 0.97999 | -0.3868 | 0.0039842 | 0.00099854
31 | 0.98031 | -0.38051 | 0.00080871 | 0.00020268
32 | 0.97987 | -0.38924 | 0.00094745 | 0.00023745
33 | 0.98084 | -0.37025 | 0.001293 | 0.00032406
34 | 0.97987 | -0.38932 | 0.00041878 | 0.00010496
35 | 0.99172 | -0.15863 | 0.017933 | 0.0044944
36 | 0.99238 | -0.146 | 0.014783 | 0.003705
37 | 0.99775 | -0.043391 | 0.0054652 | 0.0013697
38 | 0.99831 | -0.032657 | 0 | 0
39 | 0.99573 | -0.082747 | 0 | 0
40 | 0.99567 | -0.083922 | 0.00025006 | 6.267e-05
41 | 0.99558 | -0.085567 | 0 | 0
42 | 1 | 0 | -0.11602 | -0.029047
43 | 0.99387 | -0.11727 | 0.010492 | 0.0026295
44 | 0.99565 | -0.084197 | 0.00017234 | 4.3191e-05
45 | 0.99555 | -0.08631 | 0.00098394 | 0.0002466
46 | 0.99549 | -0.087292 | 0.00056859 | 0.0001425
47 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0078146 | 0.0019575 | -0.0078108 | -0.001956 | 3.7164e-06 | 1.4573e-06 | 0.011752 | 0.011752 | 0.011752 | 0.98946 | -0.2025 | 0.98894 | -0.21249 | 3.2286
1 | -0.012224 | -0.0030626 | 0.012232 | 0.003067 | 8.158e-06 | 4.3937e-06 | 0.018383 | 0.018383 | 0.018383 | 0.98946 | -0.2025 | 0.99018 | -0.18849 | 5.0504
2 | 0.0046429 | 0.0011634 | -0.0046426 | -0.0011634 | 2.3729e-07 | -1.4488e-08 | 0.0069859 | 0.0069859 | 0.0069859 | 0.98894 | -0.21249 | 0.98889 | -0.21356 | 1.9192
3 | 0.003168 | 0.00079258 | -0.0031673 | -0.00079319 | 7.0201e-07 | -6.0773e-07 | 0.0047662 | 0.0047666 | 0.0047666 | 0.98894 | -0.21249 | 0.9887 | -0.21714 | 1.3095
4 | -0.012232 | -0.003067 | 0.012233 | 0.0030676 | 1.0288e-06 | 5.54e-07 | 0.018383 | 0.018383 | 0.018383 | 0.99018 | -0.18849 | 0.99027 | -0.18673 | 5.0503
5 | 0.0046426 | 0.0011634 | -0.0046422 | -0.0011635 | 3.9845e-07 | -2.428e-08 | 0.0069859 | 0.006986 | 0.006986 | 0.98889 | -0.21356 | 0.98879 | -0.21536 | 1.9192
6 | 0.0027596 | 0.00069101 | -0.0027595 | -0.00069112 | 8.0949e-08 | -1.0869e-07 | 0.004153 | 0.0041531 | 0.0041531 | 0.9887 | -0.21714 | 0.98867 | -0.21776 | 1.141
7 | -0.017586 | -0.004409 | 0.017589 | 0.0044111 | 3.5374e-06 | 2.0901e-06 | 0.026426 | 0.026426 | 0.026426 | 0.99027 | -0.18673 | 0.99049 | -0.18251 | 7.2599
8 | 0.0016624 | 0.00041616 | -0.0016623 | -0.00041661 | 9.3432e-08 | -4.5059e-07 | 0.0025019 | 0.002502 | 0.002502 | 0.98867 | -0.21776 | 0.98861 | -0.21894 | 0.68737
9 | -0.020824 | -0.0052217 | 0.020828 | 0.005224 | 3.7468e-06 | 2.2665e-06 | 0.031285 | 0.031285 | 0.031285 | 0.99049 | -0.18251 | 0.99068 | -0.17873 | 8.5949
10 | 0.0032348 | 0.00081062 | -0.0032347 | -0.00081069 | 8.7831e-08 | -7.1432e-08 | 0.0048596 | 0.0048597 | 0.0048597 | 0.99049 | -0.18251 | 0.99046 | -0.18308 | 1.3351
11 | 0.0022793 | 0.00056037 | -0.0022791 | -0.00056069 | 1.338e-07 | -3.1646e-07 | 0.0033998 | 0.0033999 | 0.0033999 | 0.99648 | -0.068151 | 0.99641 | -0.069401 | 0.93404
12 | -0.0022793 | -0.00056037 | 0.0022798 | 0.00055919 | 4.9839e-07 | -1.1795e-06 | 0.0033998 | 0.0033993 | 0.0033998 | 0.99648 | -0.068151 | 0.99671 | -0.063491 | 0.934
13 | 0.0019765 | 0.00048484 | -0.0019752 | -0.000489 | 1.2405e-06 | -4.1577e-06 | 0.002948 | 0.0029497 | 0.0029497 | 0.99641 | -0.069401 | 0.99573 | -0.082747 | 0.81035
14 | -0.0070059 | -0.0017437 | 0.0070125 | 0.0017458 | 6.6769e-06 | 2.1479e-06 | 0.010455 | 0.010454 | 0.010455 | 0.99671 | -0.063491 | 0.99775 | -0.043391 | 2.8722
15 | -0.057858 | -0.014579 | 0.057913 | 0.014614 | 5.5684e-05 | 3.5384e-05 | 0.086931 | 0.086931 | 0.086931 | 0.99068 | -0.17873 | 0.99172 | -0.15863 | 23.8821
16 | 0.03703 | 0.0093546 | -0.03695 | -0.0093043 | 7.9986e-05 | 5.0306e-05 | 0.055645 | 0.055646 | 0.055646 | 0.99068 | -0.17873 | 0.98834 | -0.2239 | 15.2873
17 | -0.015513 | -0.0038902 | 0.015517 | 0.0038924 | 3.8709e-06 | 2.2404e-06 | 0.023493 | 0.023493 | 0.023493 | 0.98262 | -0.33539 | 0.98288 | -0.33015 | 6.4542
18 | 0.01404 | 0.003521 | -0.014037 | -0.0035194 | 2.7698e-06 | 1.5658e-06 | 0.021262 | 0.021262 | 0.021262 | 0.98262 | -0.33539 | 0.9824 | -0.33953 | 5.8413
19 | -0.016417 | -0.0041178 | 0.016432 | 0.0041268 | 1.5324e-05 | 8.9681e-06 | 0.024855 | 0.024855 | 0.024855 | 0.98288 | -0.33015 | 0.98389 | -0.31059 | 6.8282
20 | 0.011321 | 0.0028387 | -0.011321 | -0.0028384 | 4.8704e-07 | 2.5579e-07 | 0.017148 | 0.017148 | 0.017148 | 0.9824 | -0.33953 | 0.98236 | -0.34043 | 4.7111
21 | 0.0012805 | 0.00031679 | -0.0012804 | -0.00031755 | 9.132e-08 | -7.6724e-07 | 0.0019351 | 0.0019354 | 0.0019354 | 0.98389 | -0.31059 | 0.98381 | -0.3121 | 0.53171
22 | -0.017712 | -0.0044436 | 0.017716 | 0.0044455 | 3.1613e-06 | 1.874e-06 | 0.02679 | 0.02679 | 0.02679 | 0.98389 | -0.31059 | 0.98408 | -0.30685 | 7.3598
23 | 0.0097071 | 0.002434 | -0.0097041 | -0.0024326 | 2.9858e-06 | 1.4448e-06 | 0.014704 | 0.014704 | 0.014704 | 0.98236 | -0.34043 | 0.98203 | -0.34688 | 4.0396
24 | -0.027053 | -0.0068054 | 0.027064 | 0.0068123 | 1.1123e-05 | 6.8913e-06 | 0.040809 | 0.040809 | 0.040809 | 0.98664 | -0.25688 | 0.98709 | -0.24828 | 11.2114
25 | 0.022951 | 0.0057774 | -0.022897 | -0.005744 | 5.4678e-05 | 3.3444e-05 | 0.034623 | 0.034624 | 0.034624 | 0.98664 | -0.25688 | 0.98408 | -0.30685 | 9.512
26 | -0.033103 | -0.0083259 | 0.033142 | 0.00835 | 3.859e-05 | 2.4169e-05 | 0.049913 | 0.049913 | 0.049913 | 0.98709 | -0.24828 | 0.98834 | -0.2239 | 13.7124
27 | 0.0012804 | 0.00031755 | -0.00128 | -0.0003208 | 3.8735e-07 | -3.2502e-06 | 0.0019354 | 0.0019367 | 0.0019367 | 0.98381 | -0.3121 | 0.98348 | -0.31848 | 0.53205
28 | 0.0097041 | 0.0024326 | -0.0097015 | -0.0024313 | 2.5981e-06 | 1.2575e-06 | 0.014704 | 0.014704 | 0.014704 | 0.98203 | -0.34688 | 0.98174 | -0.35251 | 4.0397
29 | 0.0088406 | 0.0022156 | -0.0088374 | -0.0022141 | 3.2561e-06 | 1.4727e-06 | 0.0134 | 0.0134 | 0.0134 | 0.98174 | -0.35251 | 0.98135 | -0.36024 | 3.6813
30 | 0.0088374 | 0.0022141 | -0.0088332 | -0.0022122 | 4.2128e-06 | 1.9061e-06 | 0.0134 | 0.0134 | 0.0134 | 0.98135 | -0.36024 | 0.98084 | -0.37025 | 3.6814
31 | 0.0039845 | 0.00099846 | -0.0039842 | -0.00099854 | 2.9793e-07 | -8.2867e-08 | 0.0060495 | 0.0060496 | 0.0060496 | 0.98007 | -0.38523 | 0.97999 | -0.3868 | 1.662
32 | -0.0067263 | -0.0016835 | 0.0067278 | 0.001684 | 1.5128e-06 | 4.8054e-07 | 0.010212 | 0.010211 | 0.010212 | 0.98007 | -0.38523 | 0.98031 | -0.38051 | 2.8054
33 | 0.0013665 | 0.00034041 | -0.0013662 | -0.00034228 | 2.6002e-07 | -1.8638e-06 | 0.002074 | 0.0020747 | 0.0020747 | 0.98007 | -0.38523 | 0.97987 | -0.38924 | 0.56997
34 | -0.0075365 | -0.0018867 | 0.0075402 | 0.0018881 | 3.681e-06 | 1.4095e-06 | 0.011439 | 0.011439 | 0.011439 | 0.98031 | -0.38051 | 0.98084 | -0.37025 | 3.1425
35 | 0.00041878 | 0.00010482 | -0.00041878 | -0.00010496 | 1.6009e-09 | -1.3194e-07 | 0.00063591 | 0.00063595 | 0.00063595 | 0.97987 | -0.38924 | 0.97987 | -0.38932 | 0.17471
36 | -0.075846 | -0.019108 | 0.075892 | 0.019138 | 4.585e-05 | 2.9222e-05 | 0.11384 | 0.11384 | 0.11384 | 0.99172 | -0.15863 | 0.99238 | -0.146 | 31.2742
37 | -0.090675 | -0.022843 | 0.0908 | 0.022922 | 0.00012482 | 7.9652e-05 | 0.136 | 0.136 | 0.136 | 0.99238 | -0.146 | 0.99387 | -0.11727 | 37.3638
38 | -0.012478 | -0.0031155 | 0.012484 | 0.003119 | 6.366e-06 | 3.4333e-06 | 0.018605 | 0.018605 | 0.018605 | 0.99775 | -0.043391 | 0.99831 | -0.032657 | 5.1112
39 | -0.012484 | -0.003119 | 0.012503 | 0.0031294 | 1.9404e-05 | 1.046e-05 | 0.018605 | 0.018604 | 0.018605 | 0.99831 | -0.032657 | 1 | 0 | 5.1111
40 | 0.00042242 | 0.00010268 | -0.00042239 | -0.00010469 | 2.3285e-08 | -2.0167e-06 | 0.00063015 | 0.00063085 | 0.00063085 | 0.99573 | -0.082747 | 0.99567 | -0.083922 | 0.17331
41 | 0.0015528 | 0.00038632 | -0.0015526 | -0.00038753 | 2.0768e-07 | -1.2055e-06 | 0.0023195 | 0.00232 | 0.00232 | 0.99573 | -0.082747 | 0.99558 | -0.085567 | 0.63736
42 | 0.00017234 | 4.2024e-05 | -0.00017234 | -4.3191e-05 | 2.2316e-09 | -1.1672e-06 | 0.00025715 | 0.00025756 | 0.00025756 | 0.99567 | -0.083922 | 0.99565 | -0.084197 | 0.070757
43 | 0.0015526 | 0.00038753 | -0.0015526 | -0.00038785 | 5.482e-08 | -3.1806e-07 | 0.00232 | 0.0023201 | 0.0023201 | 0.99558 | -0.085567 | 0.99555 | -0.08631 | 0.6374
44 | 0.10186 | 0.025917 | -0.10129 | -0.025552 | 0.00057219 | 0.00036534 | 0.15171 | 0.15171 | 0.15171 | 1 | 0 | 0.99387 | -0.11727 | 41.6793
45 | 0.00056862 | 0.00014125 | -0.00056859 | -0.0001425 | 2.6496e-08 | -1.2555e-06 | 0.00084945 | 0.0008499 | 0.0008499 | 0.99555 | -0.08631 | 0.99549 | -0.087292 | 0.23349

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.11858 | 0.02969

## res_load
| p_mw | q_mvar
0 | 0.0044097 | 0.0011052
1 | 0.00040767 | 0.00010217
2 | 0.0053525 | 0.0013415
3 | 0.0046422 | 0.0011635
4 | 0.0010971 | 0.00027496
5 | 0.00030264 | 7.5848e-05
6 | 0.0047261 | 0.0011845
7 | 0.0016623 | 0.00041661
8 | 0.0032347 | 0.00081069
9 | 0.0014732 | 0.00036921
10 | 0.00089945 | 0.00022542
11 | 0.0027162 | 0.00068075
12 | 0.0016135 | 0.00040439
13 | 0.0041018 | 0.001028
14 | 0.0060391 | 0.0015135
15 | 0.005181 | 0.0012985
16 | 0.00128 | 0.0003208
17 | 0.00086087 | 0.00021575
18 | 0.0038077 | 0.0009543
19 | 0.0013753 | 0.00034467
20 | 0.0039842 | 0.00099854
21 | 0.00080871 | 0.00020268
22 | 0.00094745 | 0.00023745
23 | 0.001293 | 0.00032406
24 | 0.00041878 | 0.00010496
25 | 0.017933 | 0.0044944
26 | 0.014783 | 0.003705
27 | 0.0054652 | 0.0013697
28 | 0.00025006 | 6.267e-05
29 | 0.0025659 | 0.00064308
30 | 0.010492 | 0.0026295
31 | 0.00017234 | 4.3191e-05
32 | 0.00098394 | 0.0002466
33 | 0.00056859 | 0.0001425

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1