## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1706-8_1_2_node_38 | 0.4 | n |  | TRUE
1 | bus_LV_1706-8_1_2_node_39 | 0.4 | n |  | TRUE
2 | bus_LV_1706-8_1_2_node_40 | 0.4 | n |  | TRUE
3 | bus_LV_1706-8_1_2_node_41 | 0.4 | n |  | TRUE
4 | bus_LV_1706-8_1_2_node_42 | 0.4 | n |  | TRUE
5 | bus_LV_1706-8_1_2_node_60 | 0.4 | n |  | TRUE
6 | bus_LV_1706-8_1_2_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_1706-8_1_2_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_1706-8_1_2_node_45 | 0.4 | n |  | TRUE
9 | bus_LV_1706-8_1_2_node_46 | 0.4 | n |  | TRUE
10 | bus_LV_1706-8_1_2_node_47 | 0.4 | n |  | TRUE
11 | bus_LV_1706-8_1_2_node_57 | 0.4 | n |  | TRUE
12 | bus_LV_1706-8_1_2_node_52 | 0.4 | n |  | TRUE
13 | bus_LV_1706-8_1_2_node_48 | 0.4 | n |  | TRUE
14 | bus_LV_1706-8_1_2_node_49 | 0.4 | n |  | TRUE
15 | bus_LV_1706-8_1_2_node_50 | 0.4 | n |  | TRUE
16 | bus_LV_1706-8_1_2_node_51 | 0.4 | n |  | TRUE
17 | bus_LV_1706-8_1_2_node_56 | 0.4 | n |  | TRUE
18 | bus_LV_1706-8_1_2_node_53 | 0.4 | n |  | TRUE
19 | bus_LV_1706-8_1_2_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_1706-8_1_2_node_55 | 0.4 | n |  | TRUE
21 | bus_LV_1706-8_1_2_node_58 | 0.4 | n |  | TRUE
22 | bus_LV_1706-8_1_2_node_59 | 0.4 | n |  | TRUE
23 | bus_LV_1706-8_1_2_node_62 | 0.4 | n |  | TRUE
24 | bus_LV_1706-8_1_2_node_61 | 0.4 | n |  | TRUE
25 | bus_LV_1706-8_1_2_node_67 | 0.4 | n |  | TRUE
26 | bus_LV_1706-8_1_2_node_88 | 0.4 | n |  | TRUE
27 | bus_LV_1706-8_1_2_node_64 | 0.4 | n |  | TRUE
28 | bus_LV_1706-8_1_2_node_63 | 0.4 | n |  | TRUE
29 | bus_LV_1706-8_1_2_node_65 | 0.4 | n |  | TRUE
30 | bus_LV_1706-8_1_2_node_66 | 0.4 | n |  | TRUE
31 | bus_LV_1706-8_1_2_node_90 | 0.4 | n |  | TRUE
32 | bus_LV_1706-8_1_2_node_68 | 0.4 | n |  | TRUE
33 | bus_LV_1706-8_1_2_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_1706-8_1_2_node_70 | 0.4 | n |  | TRUE
35 | bus_LV_1706-8_1_2_node_77 | 0.4 | n |  | TRUE
36 | bus_LV_1706-8_1_2_node_87 | 0.4 | n |  | TRUE
37 | bus_LV_1706-8_1_2_node_80 | 0.4 | n |  | TRUE
38 | bus_LV_1706-8_1_2_node_78 | 0.4 | n |  | TRUE
39 | bus_LV_1706-8_1_2_node_79 | 0.4 | n |  | TRUE
40 | bus_LV_1706-8_1_2_node_85 | 0.4 | n |  | TRUE
41 | bus_LV_1706-8_1_2_node_86 | 0.4 | n |  | TRUE
42 | bus_MV_22_0_node_146 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1706-8_1_2_load_38 | 0 | 0.0015801 | 0.000396 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1706-8_1_2_load_39 | 1 | 0.001584 | 0.00039699 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1706-8_1_2_load_42 | 4 | 0.0089445 | 0.0022417 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1706-8_1_2_load_60 | 5 | 0.0024319 | 0.0006095 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1706-8_1_2_load_43 | 6 | 0.0014783 | 0.00037051 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1706-8_1_2_load_44 | 7 | 0.0017802 | 0.00044616 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1706-8_1_2_load_45 | 8 | 0.00064908 | 0.00016267 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1706-8_1_2_load_46 | 9 | 0.0077669 | 0.0019466 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1706-8_1_2_load_47 | 10 | 0.0024143 | 0.00060507 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1706-8_1_2_load_52 | 12 | 0.00092002 | 0.00023058 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1706-8_1_2_load_48 | 13 | 0.0015187 | 0.00038062 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1706-8_1_2_load_49 | 14 | 0.0022131 | 0.00055465 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1706-8_1_2_load_50 | 15 | 0.0039083 | 0.00097952 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1706-8_1_2_load_56 | 17 | 0.00038045 | 9.535e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1706-8_1_2_load_53 | 18 | 0.0063473 | 0.0015908 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1706-8_1_2_load_54 | 19 | 0.00067669 | 0.0001696 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1706-8_1_2_load_58 | 21 | 0.0062995 | 0.0015788 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1706-8_1_2_load_59 | 22 | 0.0025946 | 0.00065027 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1706-8_1_2_load_61 | 24 | 0.0026456 | 0.00066305 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1706-8_1_2_load_67 | 25 | 0.0018102 | 0.00045367 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1706-8_1_2_load_88 | 26 | 0.0023185 | 0.00058107 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1706-8_1_2_load_63 | 28 | 0.00084231 | 0.0002111 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1706-8_1_2_load_65 | 29 | 0.0021208 | 0.00053153 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1706-8_1_2_load_66 | 30 | 0.00096294 | 0.00024134 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1706-8_1_2_load_90 | 31 | 0.0003652 | 9.1529e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1706-8_1_2_load_68 | 32 | 0.0011409 | 0.00028594 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1706-8_1_2_load_69 | 33 | 0.0054683 | 0.0013705 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1706-8_1_2_load_70 | 34 | 0.0063722 | 0.001597 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1706-8_1_2_load_77 | 35 | 0.00073438 | 0.00018405 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1706-8_1_2_load_80 | 37 | 0.0015679 | 0.00039296 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1706-8_1_2_load_78 | 38 | 0.00023658 | 5.9292e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1706-8_1_2_load_85 | 40 | 0.0014981 | 0.00037545 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1706-8_1_2_load_86 | 41 | 0.00051937 | 0.00013017 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1706-8_1_2_line_0 |  | 0 | 1 | 0.0097116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1706-8_1_2_line_1 |  | 0 | 2 | 0.050151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1706-8_1_2_line_2 |  | 1 | 3 | 0.048286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1706-8_1_2_line_3 |  | 2 | 4 | 0.025798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1706-8_1_2_line_4 |  | 3 | 5 | 0.019354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1706-8_1_2_line_5 |  | 5 | 11 | 0.023243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1706-8_1_2_line_6 |  | 6 | 7 | 0.019964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1706-8_1_2_line_7 |  | 6 | 8 | 0.020173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1706-8_1_2_line_8 |  | 7 | 9 | 0.01292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1706-8_1_2_line_9 |  | 8 | 10 | 0.01657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1706-8_1_2_line_10 |  | 9 | 11 | 0.035565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1706-8_1_2_line_11 |  | 10 | 12 | 0.013243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1706-8_1_2_line_12 |  | 11 | 24 | 0.040036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1706-8_1_2_line_13 |  | 12 | 15 | 0.033945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1706-8_1_2_line_14 |  | 13 | 14 | 0.088893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1706-8_1_2_line_15 |  | 13 | 15 | 0.076261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1706-8_1_2_line_16 |  | 14 | 16 | 0.059686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1706-8_1_2_line_17 |  | 16 | 17 | 0.012707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1706-8_1_2_line_18 |  | 16 | 18 | 0.019398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1706-8_1_2_line_19 |  | 17 | 23 | 0.04688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1706-8_1_2_line_20 |  | 18 | 19 | 0.011317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1706-8_1_2_line_21 |  | 19 | 20 | 0.02105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1706-8_1_2_line_22 |  | 20 | 21 | 0.078851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1706-8_1_2_line_23 |  | 20 | 22 | 0.013923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1706-8_1_2_line_24 |  | 21 | 25 | 0.11663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1706-8_1_2_line_25 |  | 22 | 26 | 0.039821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1706-8_1_2_line_26 |  | 23 | 28 | 0.089265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1706-8_1_2_line_27 |  | 24 | 27 | 0.068755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1706-8_1_2_line_28 |  | 26 | 34 | 0.0083702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1706-8_1_2_line_29 |  | 27 | 29 | 0.007491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1706-8_1_2_line_30 |  | 27 | 30 | 0.036398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1706-8_1_2_line_31 |  | 29 | 31 | 0.22689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1706-8_1_2_line_32 |  | 31 | 37 | 0.23257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1706-8_1_2_line_33 |  | 32 | 33 | 0.0073173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1706-8_1_2_line_34 |  | 33 | 34 | 0.021729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1706-8_1_2_line_35 |  | 35 | 36 | 0.23596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1706-8_1_2_line_36 |  | 35 | 37 | 0.44251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1706-8_1_2_line_37 |  | 36 | 40 | 0.026081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1706-8_1_2_line_38 |  | 37 | 39 | 0.12741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1706-8_1_2_line_39 |  | 38 | 39 | 0.044761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1706-8_1_2_line_40 |  | 40 | 41 | 0.028011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1706-8_1_2_trafo_52 | 0.63 MVA 20/0.4 kV | 42 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2691406.0335 | 1218628.0897 | 2691397.52 | 1218623.4168
1 | 2691450.6431 | 1218610.2269 | 2691426.2099 | 1218621.0372 | 2691415.3402 | 1218629.4317 | 2691408.802 | 1218629.6093 | 2691406.0335 | 1218628.0897
2 | 2691363.9761 | 1218588.7605 | 2691373.1839 | 1218597.6411 | 2691396.7359 | 1218622.9864 | 2691397.52 | 1218623.4168
3 | 2691450.6431 | 1218610.2269 | 2691450.0096 | 1218615.3985 | 2691447.5665 | 1218627.1913 | 2691442.7518 | 1218634.2556
4 | 2691363.9761 | 1218588.7605 | 2691365.4305 | 1218570.6481 | 2691365.6198 | 1218569.4798
5 | 2691369.3377 | 1218546.5359 | 2691365.6198 | 1218569.4798
6 | 2691381.7251 | 1218479.2204 | 2691379.2 | 1218494.4737 | 2691378.3618 | 1218498.8985
7 | 2691381.7251 | 1218479.2204 | 2691383.4668 | 1218468.6992 | 2691384.762 | 1218459.2794
8 | 2691378.3618 | 1218498.8985 | 2691375.9572 | 1218511.5923
9 | 2691384.762 | 1218459.2794 | 2691385.5004 | 1218453.9091 | 2691386.1343 | 1218442.7779 | 2691386.1343 | 1218442.7779
10 | 2691369.3377 | 1218546.5359 | 2691375.9572 | 1218511.5923
11 | 2691385.804 | 1218429.5446 | 2691385.9342 | 1218430.5887 | 2691386.1343 | 1218442.7779
12 | 2691369.3377 | 1218546.5359 | 2691382.1272 | 1218547.5883 | 2691401.0767 | 1218545.4108 | 2691409.1345 | 1218546.4877
13 | 2691385.804 | 1218429.5446 | 2691384.6364 | 1218420.1838 | 2691382.7264 | 1218412.0823 | 2691378.2384 | 1218396.529
14 | 2691349.4076 | 1218325.9527 | 2691315.6764 | 1218249.6765 | 2691313.9396 | 1218244.4673
15 | 2691349.4076 | 1218325.9527 | 2691359.6373 | 1218349.0851 | 2691377.7603 | 1218394.8722 | 2691378.2384 | 1218396.529
16 | 2691305.54 | 1218185.9553 | 2691304.8985 | 1218206.0147 | 2691308.7529 | 1218228.9117 | 2691313.9396 | 1218244.4673
17 | 2691305.54 | 1218185.9553 | 2691307.2248 | 1218173.3604
18 | 2691305.54 | 1218185.9553 | 2691317.8081 | 1218187.889 | 2691324.7817 | 1218187.6385
19 | 2691317.2751 | 1218127.5951 | 2691308.0351 | 1218167.3029 | 2691307.2248 | 1218173.3604
20 | 2691324.7817 | 1218187.6385 | 2691325.6162 | 1218187.6085 | 2691334.1922 | 1218182.2918 | 2691334.5676 | 1218182.1799
21 | 2691354.2976 | 1218184.5126 | 2691347.246 | 1218180.5129 | 2691340.6134 | 1218180.3778 | 2691334.5676 | 1218182.1799
22 | 2691354.2976 | 1218184.5126 | 2691362.4213 | 1218188.3954 | 2691381.6359 | 1218192.2704 | 2691393.1899 | 1218201.654 | 2691403.037 | 1218209.4771 | 2691416.4814 | 1218213.4082 | 2691424.8836 | 1218215.9488
23 | 2691354.2976 | 1218184.5126 | 2691355.1527 | 1218191.1191 | 2691354.0089 | 1218196.4052 | 2691352.9673 | 1218197.9381
24 | 2691479.4235 | 1218290.249 | 2691477.7471 | 1218284.2414 | 2691477.5611 | 1218276.5777 | 2691485.0793 | 1218265.0186 | 2691487.8971 | 1218256.5227 | 2691486.7963 | 1218248.6226 | 2691480.882 | 1218239.7813 | 2691469.161 | 1218231.3956 | 2691452.5087 | 1218224.3018 | 2691424.8836 | 1218215.9488
25 | 2691348.8342 | 1218234.9403 | 2691345.4598 | 1218225.6943 | 2691344.5748 | 1218214.1061 | 2691347.5782 | 1218205.8687 | 2691352.9673 | 1218197.9381
26 | 2691402.497 | 1218147.2261 | 2691380.0875 | 1218149.2172 | 2691368.5943 | 1218148.7295 | 2691354.9345 | 1218142.9939 | 2691317.2751 | 1218127.5951
27 | 2691473.0888 | 1218569.6991 | 2691461.9842 | 1218566.2041 | 2691442.3493 | 1218555.6733 | 2691425.836 | 1218548.4816 | 2691414.8938 | 1218547.2574 | 2691409.1345 | 1218546.4877
28 | 2691351.7037 | 1218242.8032 | 2691348.8342 | 1218234.9403
29 | 2691473.0888 | 1218569.6991 | 2691480.4027 | 1218571.4126
30 | 2691486.8599 | 1218535.9985 | 2691473.0888 | 1218569.6991
31 | 2691480.4027 | 1218571.4126 | 2691657.8297 | 1218712.8251
32 | 2691657.8297 | 1218712.8251 | 2691793.5826 | 1218523.985
33 | 2691362.1639 | 1218269.8711 | 2691360.0806 | 1218265.757 | 2691359.153 | 1218263.2151
34 | 2691351.7037 | 1218242.8032 | 2691359.153 | 1218263.2151
35 | 2692319.1622 | 1218950.8318 | 2692123.6614 | 1218818.7035
36 | 2691793.5826 | 1218523.985 | 2692123.6614 | 1218818.7035
37 | 2692319.1622 | 1218950.8318 | 2692344.9923 | 1218947.2237
38 | 2691877.4407 | 1218428.8453 | 2691871.4813 | 1218437.2481 | 2691850.5383 | 1218464.2994 | 2691837.2413 | 1218481.384 | 2691818.4362 | 1218495.3371 | 2691805.7553 | 1218508.4174 | 2691793.5826 | 1218523.985
39 | 2691877.4407 | 1218428.8453 | 2691881.495 | 1218397.3084 | 2691880.7544 | 1218384.3646
40 | 2692344.9923 | 1218947.2237 | 2692364.871 | 1218944.4469 | 2692372.7811 | 1218943.7622

## bus_geodata
| x | y | coords
0 | 2691406.0335 | 1218628.0897
1 | 2691397.52 | 1218623.4168
2 | 2691450.6431 | 1218610.2269
3 | 2691363.9761 | 1218588.7605
4 | 2691442.7518 | 1218634.2556
5 | 2691365.6198 | 1218569.4798
6 | 2691381.7251 | 1218479.2204
7 | 2691378.3618 | 1218498.8985
8 | 2691384.762 | 1218459.2794
9 | 2691375.9572 | 1218511.5923
10 | 2691386.1343 | 1218442.7779
11 | 2691369.3377 | 1218546.5359
12 | 2691385.804 | 1218429.5446
13 | 2691349.4076 | 1218325.9527
14 | 2691313.9396 | 1218244.4673
15 | 2691378.2384 | 1218396.529
16 | 2691305.54 | 1218185.9553
17 | 2691307.2248 | 1218173.3604
18 | 2691324.7817 | 1218187.6385
19 | 2691334.5676 | 1218182.1799
20 | 2691354.2976 | 1218184.5126
21 | 2691424.8836 | 1218215.9488
22 | 2691352.9673 | 1218197.9381
23 | 2691317.2751 | 1218127.5951
24 | 2691409.1345 | 1218546.4877
25 | 2691479.4235 | 1218290.249
26 | 2691348.8342 | 1218234.9403
27 | 2691473.0888 | 1218569.6991
28 | 2691402.497 | 1218147.2261
29 | 2691480.4027 | 1218571.4126
30 | 2691486.8599 | 1218535.9985
31 | 2691657.8297 | 1218712.8251
32 | 2691362.1639 | 1218269.8711
33 | 2691359.153 | 1218263.2151
34 | 2691351.7037 | 1218242.8032
35 | 2692123.6614 | 1218818.7035
36 | 2692319.1622 | 1218950.8318
37 | 2691793.5826 | 1218523.985
38 | 2691880.7544 | 1218384.3646
39 | 2691877.4407 | 1218428.8453
40 | 2692344.9923 | 1218947.2237
41 | 2692372.7811 | 1218943.7622
42 | 2691369.3377 | 1218546.5359

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99532 | -0.090069 | 0.0015801 | 0.000396
1 | 0.99542 | -0.08827 | 0.001584 | 0.00039699
2 | 0.99491 | -0.097965 | 0 | 0
3 | 0.99595 | -0.077988 | 0 | 0
4 | 0.9947 | -0.10203 | 0.0089445 | 0.0022417
5 | 0.99616 | -0.073869 | 0.0024319 | 0.0006095
6 | 0.9983 | -0.032555 | 0.0014783 | 0.00037051
7 | 0.99767 | -0.044712 | 0.0017802 | 0.00044616
8 | 0.99897 | -0.019765 | 0.00064908 | 0.00016267
9 | 0.99729 | -0.052184 | 0.0077669 | 0.0019466
10 | 0.99953 | -0.0090847 | 0.0024143 | 0.00060507
11 | 0.99647 | -0.067933 | 0 | 0
12 | 1 | 0 | -0.083327 | -0.020634
13 | 0.99604 | -0.075613 | 0.0015187 | 0.00038062
14 | 0.99307 | -0.13276 | 0.0022131 | 0.00055465
15 | 0.9987 | -0.024831 | 0.0039083 | 0.00097952
16 | 0.9912 | -0.16898 | 0 | 0
17 | 0.99119 | -0.16925 | 0.00038045 | 9.535e-05
18 | 0.99061 | -0.18035 | 0.0063473 | 0.0015908
19 | 0.99034 | -0.18572 | 0.00067669 | 0.0001696
20 | 0.98983 | -0.19545 | 0 | 0
21 | 0.98925 | -0.20684 | 0.0062995 | 0.0015788
22 | 0.98961 | -0.19989 | 0.0025946 | 0.00065027
23 | 0.99115 | -0.16996 | 0 | 0
24 | 0.99608 | -0.075456 | 0.0026456 | 0.00066305
25 | 0.98905 | -0.21061 | 0.0018102 | 0.00045367
26 | 0.98905 | -0.21074 | 0.0023185 | 0.00058107
27 | 0.99558 | -0.085187 | 0 | 0
28 | 0.99108 | -0.17129 | 0.00084231 | 0.0002111
29 | 0.99553 | -0.086121 | 0.0021208 | 0.00053153
30 | 0.99555 | -0.085804 | 0.00096294 | 0.00024134
31 | 0.99451 | -0.10594 | 0.0003652 | 9.1529e-05
32 | 0.98881 | -0.21538 | 0.0011409 | 0.00028594
33 | 0.98882 | -0.21524 | 0.0054683 | 0.0013705
34 | 0.98895 | -0.21268 | 0.0063722 | 0.001597
35 | 0.99244 | -0.14643 | 0.00073438 | 0.00018405
36 | 0.992 | -0.15488 | 0 | 0
37 | 0.99355 | -0.12478 | 0.0015679 | 0.00039296
38 | 0.99351 | -0.1255 | 0.00023658 | 5.9292e-05
39 | 0.99352 | -0.12532 | 0 | 0
40 | 0.99195 | -0.15582 | 0.0014981 | 0.00037545
41 | 0.99194 | -0.15607 | 0.00051937 | 0.00013017
42 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.01053 | -0.00264 | 0.010531 | 0.0026404 | 9.0251e-07 | 4.5138e-07 | 0.015742 | 0.015742 | 0.015742 | 0.99532 | -0.090069 | 0.99542 | -0.08827 | 4.3248
1 | 0.0089496 | 0.002244 | -0.0089462 | -0.0022425 | 3.3669e-06 | 1.5033e-06 | 0.01338 | 0.01338 | 0.01338 | 0.99532 | -0.090069 | 0.99491 | -0.097965 | 3.6759
2 | -0.012115 | -0.0030374 | 0.01212 | 0.0030406 | 5.9386e-06 | 3.1727e-06 | 0.01811 | 0.01811 | 0.01811 | 0.99542 | -0.08827 | 0.99595 | -0.077988 | 4.9753
3 | 0.0089462 | 0.0022425 | -0.0089445 | -0.0022417 | 1.732e-06 | 7.7354e-07 | 0.01338 | 0.01338 | 0.01338 | 0.99491 | -0.097965 | 0.9947 | -0.10203 | 3.6759
4 | -0.01212 | -0.0030406 | 0.012123 | 0.0030419 | 2.3803e-06 | 1.2715e-06 | 0.01811 | 0.01811 | 0.01811 | 0.99595 | -0.077988 | 0.99616 | -0.073869 | 4.9752
5 | -0.014555 | -0.0036514 | 0.014559 | 0.0036537 | 4.1204e-06 | 2.3344e-06 | 0.021742 | 0.021742 | 0.021742 | 0.99616 | -0.073869 | 0.99647 | -0.067933 | 5.9732
6 | 0.034828 | 0.0087408 | -0.034808 | -0.0087281 | 2.0179e-05 | 1.2654e-05 | 0.051917 | 0.051917 | 0.051917 | 0.9983 | -0.032555 | 0.99767 | -0.044712 | 14.2629
7 | -0.036306 | -0.0091113 | 0.036329 | 0.0091252 | 2.2158e-05 | 1.3917e-05 | 0.054121 | 0.05412 | 0.054121 | 0.9983 | -0.032555 | 0.99897 | -0.019765 | 14.8683
8 | 0.033028 | 0.008282 | -0.033016 | -0.0082746 | 1.1757e-05 | 7.3559e-06 | 0.049262 | 0.049262 | 0.049262 | 0.99767 | -0.044712 | 0.99729 | -0.052184 | 13.5335
9 | -0.036978 | -0.0092879 | 0.036997 | 0.0092997 | 1.8856e-05 | 1.1851e-05 | 0.055087 | 0.055087 | 0.055087 | 0.99897 | -0.019765 | 0.99953 | -0.0090847 | 15.1339
10 | 0.025249 | 0.006328 | -0.02523 | -0.0063164 | 1.8929e-05 | 1.1651e-05 | 0.037673 | 0.037673 | 0.037673 | 0.99729 | -0.052184 | 0.99647 | -0.067933 | 10.3498
11 | -0.039411 | -0.0099048 | 0.039428 | 0.0099156 | 1.7101e-05 | 1.0771e-05 | 0.058681 | 0.058681 | 0.058681 | 0.99953 | -0.0090847 | 1 | 0 | 16.1212
12 | 0.010671 | 0.0026627 | -0.010667 | -0.0026608 | 3.8105e-06 | 1.9174e-06 | 0.015931 | 0.015931 | 0.015931 | 0.99647 | -0.067933 | 0.99608 | -0.075456 | 4.3767
13 | 0.04225 | 0.010719 | -0.042199 | -0.010687 | 5.0385e-05 | 3.1801e-05 | 0.062914 | 0.062914 | 0.062914 | 1 | 0 | 0.9987 | -0.024831 | 17.2841
14 | 0.036679 | 0.0092681 | -0.036579 | -0.0092051 | 0.00010019 | 6.2967e-05 | 0.054822 | 0.054823 | 0.054823 | 0.99604 | -0.075613 | 0.99307 | -0.13276 | 15.0612
15 | -0.038198 | -0.0096487 | 0.038291 | 0.0097074 | 9.3211e-05 | 5.866e-05 | 0.057091 | 0.057091 | 0.057091 | 0.99604 | -0.075613 | 0.9987 | -0.024831 | 15.6844
16 | 0.034366 | 0.0086505 | -0.034306 | -0.0086132 | 5.9379e-05 | 3.7232e-05 | 0.051507 | 0.051507 | 0.051507 | 0.99307 | -0.13276 | 0.9912 | -0.16898 | 14.1503
17 | 0.0012229 | 0.0003046 | -0.0012228 | -0.00030475 | 1.6048e-08 | -1.5351e-07 | 0.0018351 | 0.0018352 | 0.0018352 | 0.9912 | -0.16898 | 0.99119 | -0.16925 | 0.50417
18 | 0.033083 | 0.0083086 | -0.033065 | -0.0082974 | 1.7947e-05 | 1.1236e-05 | 0.049672 | 0.049672 | 0.049672 | 0.9912 | -0.16898 | 0.99061 | -0.18035 | 13.6461
19 | 0.00084239 | 0.0002094 | -0.00084236 | -0.00020999 | 2.8094e-08 | -5.8624e-07 | 0.001264 | 0.0012642 | 0.0012642 | 0.99119 | -0.16925 | 0.99115 | -0.16996 | 0.34732
20 | 0.026718 | 0.0067066 | -0.026711 | -0.0067024 | 6.8371e-06 | 4.2301e-06 | 0.040138 | 0.040138 | 0.040138 | 0.99061 | -0.18035 | 0.99034 | -0.18572 | 11.0268
21 | 0.026035 | 0.0065328 | -0.026023 | -0.0065253 | 1.2081e-05 | 7.461e-06 | 0.039121 | 0.039121 | 0.039121 | 0.99034 | -0.18572 | 0.98983 | -0.19545 | 10.7475
22 | 0.0081144 | 0.002033 | -0.00811 | -0.0020312 | 4.3999e-06 | 1.803e-06 | 0.012198 | 0.012198 | 0.012198 | 0.98983 | -0.19545 | 0.98925 | -0.20684 | 3.3512
23 | 0.017908 | 0.0044924 | -0.017904 | -0.0044901 | 3.7846e-06 | 2.2432e-06 | 0.026923 | 0.026923 | 0.026923 | 0.98983 | -0.19545 | 0.98961 | -0.19989 | 7.3964
24 | 0.0018105 | 0.00045238 | -0.0018102 | -0.00045367 | 3.2432e-07 | -1.2895e-06 | 0.0027229 | 0.0027234 | 0.0027234 | 0.98925 | -0.20684 | 0.98905 | -0.21061 | 0.74818
25 | 0.01531 | 0.0038399 | -0.015302 | -0.0038353 | 7.9143e-06 | 4.5538e-06 | 0.023022 | 0.023022 | 0.023022 | 0.98961 | -0.19989 | 0.98905 | -0.21074 | 6.3247
26 | 0.00084236 | 0.00020999 | -0.00084231 | -0.0002111 | 5.352e-08 | -1.1161e-06 | 0.0012642 | 0.0012647 | 0.0012647 | 0.99115 | -0.16996 | 0.99108 | -0.17129 | 0.34743
27 | 0.0080218 | 0.0019977 | -0.0080181 | -0.0019963 | 3.6999e-06 | 1.4734e-06 | 0.011979 | 0.011979 | 0.011979 | 0.99608 | -0.075456 | 0.99558 | -0.085187 | 3.291
28 | 0.012983 | 0.0032542 | -0.012982 | -0.0032536 | 1.1977e-06 | 6.5909e-07 | 0.019534 | 0.019534 | 0.019534 | 0.98905 | -0.21074 | 0.98895 | -0.21268 | 5.3664
29 | 0.0070551 | 0.0017554 | -0.0070548 | -0.0017553 | 3.1209e-07 | 1.0233e-07 | 0.01054 | 0.01054 | 0.01054 | 0.99558 | -0.085187 | 0.99553 | -0.086121 | 2.8957
30 | 0.00096297 | 0.00024088 | -0.00096294 | -0.00024134 | 2.8272e-08 | -4.5519e-07 | 0.0014391 | 0.0014393 | 0.0014393 | 0.99558 | -0.085187 | 0.99555 | -0.085804 | 0.39541
31 | 0.004934 | 0.0012237 | -0.0049293 | -0.0012237 | 4.6224e-06 | 1.1304e-08 | 0.0073703 | 0.0073713 | 0.0073713 | 0.99553 | -0.086121 | 0.99451 | -0.10594 | 2.0251
32 | 0.0045641 | 0.0011322 | -0.0045601 | -0.0011326 | 4.063e-06 | -4.1455e-07 | 0.0068249 | 0.0068259 | 0.0068259 | 0.99451 | -0.10594 | 0.99355 | -0.12478 | 1.8753
33 | -0.0011409 | -0.00028593 | 0.0011409 | 0.00028585 | 8.0883e-09 | -8.8685e-08 | 0.0017169 | 0.0017169 | 0.0017169 | 0.98881 | -0.21538 | 0.98882 | -0.21524 | 0.47167
34 | -0.0066092 | -0.0016563 | 0.00661 | 0.0016566 | 8.0601e-07 | 2.3709e-07 | 0.0099458 | 0.0099457 | 0.0099458 | 0.98882 | -0.21524 | 0.98895 | -0.21268 | 2.7324
35 | 0.0020183 | 0.00050245 | -0.0020175 | -0.00050498 | 8.1e-07 | -2.5293e-06 | 0.003025 | 0.0030261 | 0.0030261 | 0.99244 | -0.14643 | 0.992 | -0.15488 | 0.83134
36 | -0.0027527 | -0.0006865 | 0.0027555 | 0.00068259 | 2.8237e-06 | -3.9171e-06 | 0.0041261 | 0.0041241 | 0.0041261 | 0.99244 | -0.14643 | 0.99355 | -0.12478 | 1.1335
37 | 0.0020175 | 0.00050498 | -0.0020174 | -0.00050526 | 8.9565e-08 | -2.7937e-07 | 0.0030261 | 0.0030262 | 0.0030262 | 0.992 | -0.15488 | 0.99195 | -0.15582 | 0.83138
38 | 0.00023659 | 5.7068e-05 | -0.00023658 | -5.8714e-05 | 5.9823e-09 | -1.6462e-06 | 0.00035356 | 0.00035413 | 0.00035413 | 0.99355 | -0.12478 | 0.99352 | -0.12532 | 0.097288
39 | -0.00023658 | -5.9292e-05 | 0.00023658 | 5.8714e-05 | 2.1062e-09 | -5.783e-07 | 0.00035433 | 0.00035413 | 0.00035433 | 0.99351 | -0.1255 | 0.99352 | -0.12532 | 0.097344
40 | 0.00051938 | 0.00012981 | -0.00051937 | -0.00013017 | 6.3753e-09 | -3.5751e-07 | 0.00077899 | 0.00077912 | 0.00077912 | 0.99195 | -0.15582 | 0.99194 | -0.15607 | 0.21404

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.084247 | 0.020865

## res_load
| p_mw | q_mvar
0 | 0.0015801 | 0.000396
1 | 0.001584 | 0.00039699
2 | 0.0089445 | 0.0022417
3 | 0.0024319 | 0.0006095
4 | 0.0014783 | 0.00037051
5 | 0.0017802 | 0.00044616
6 | 0.00064908 | 0.00016267
7 | 0.0077669 | 0.0019466
8 | 0.0024143 | 0.00060507
9 | 0.00092002 | 0.00023058
10 | 0.0015187 | 0.00038062
11 | 0.0022131 | 0.00055465
12 | 0.0039083 | 0.00097952
13 | 0.00038045 | 9.535e-05
14 | 0.0063473 | 0.0015908
15 | 0.00067669 | 0.0001696
16 | 0.0062995 | 0.0015788
17 | 0.0025946 | 0.00065027
18 | 0.0026456 | 0.00066305
19 | 0.0018102 | 0.00045367
20 | 0.0023185 | 0.00058107
21 | 0.00084231 | 0.0002111
22 | 0.0021208 | 0.00053153
23 | 0.00096294 | 0.00024134
24 | 0.0003652 | 9.1529e-05
25 | 0.0011409 | 0.00028594
26 | 0.0054683 | 0.0013705
27 | 0.0063722 | 0.001597
28 | 0.00073438 | 0.00018405
29 | 0.0015679 | 0.00039296
30 | 0.00023658 | 5.9292e-05
31 | 0.0014981 | 0.00037545
32 | 0.00051937 | 0.00013017

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1